## COVER
OWNER: |  |  | ALBA PROJECT – PP AND PEL PLANTS |  |  |  | OWNER IDENTIFICATION CODE
32-L-32-000-2-00-80601
CONTRACTOR IDENTIFICATION CODE
|  |  | PP PLANT (NEW) LINE LIST |  |  |  | 4274-XH-LL-10000001
CONTRACTOR: |  |  |  | Rev 00 |  |  | Revision |  | Page
[7 empty] | 8 |  | 1 / 100
REPSOL POLIMEROS SA, SINES PORTUGAL
PP PLANT (NEW) LINE LIST
#VALUE!
[6 empty] | #VALUE! |  | #VALUE! |  | #VALUE!
08 |  | 2024-12-19 | ISSUED FOR CONSTRUCTION - SITE REVISION |  | W. Donofrio |  | F. Carra |  | M.Pecile
07 |  | 2024-03-15 | Issue for Construction |  | M. Bonati |  | A. Bertoni |  | M.Bonati
06 |  | 2024-02-14 | Issue for Construction |  | I. Kara |  | M. Bonati |  | M.Bonati
05 |  | 2023-09-05 | Issue for Construction |  | E. Salvaggio |  | G. Paganoni |  | G. Paganoni
04 |  | 2023-04-17 | Issue for Construction with HOLDs |  | E. Salvaggio |  | G. Paganoni |  | G. Paganoni
03 |  | 2022-12-02 | Issue for Construction with HOLDs |  | E. Salvaggio |  | G. Paganoni |  | G. Paganoni
02 |  | 2022-08-05 | Issue for Design |  | E. Salvaggio |  | G. Paganoni |  | G. Paganoni
00 |  | 2022-02-11 | Issue for Design |  | E. Salvaggio |  | G. Paganoni |  | G. Paganoni
REV. |  | DATE | STATUS - REVISION MEMO |  | WRITTEN BY |  | CHECKED BY |  | APPROVED BY
CONFIDENTIALITY – This document and the information herein contained are the confidential proprietary information of ALBA project. Any disclosure to third parties, use, or reproduction without proper authorization is strictly prohibited.

## NOTES
OWNER: |  |  | ALBA PROJECT – PP AND PEL PLANTS |  |  |  | OWNER IDENTIFICATION CODE
32-L-32-000-2-00-80601
CONTRACTOR IDENTIFICATION CODE
|  |  | PP PLANT (NEW) LINE LIST |  |  |  | 4274-XH-LL-10000001
CONTRACTOR: | [6 empty] | Revision | Page
[7 empty] | 8 | 2 / 100
|  |  | REPSOL POLIMEROS SA, SINES PORTUGAL | 1-STREAMS 54,56,229,333,335,336,343,357,733 ARE JACKETED BY STREAM 111 (LPS JACKET)
| COLUMN HEADER |  |  |  | DETAIL NOTES LEGEND
| 0 - | REVISION NUMBER, indicates lines subjetc to revision |  |  | 1 - | STREAMS 54, 56, 229, 333, 335, 336, 343, 357, 733 ARE JACKETED BY STREAM 111 (LPS JACKET)
| 1 - | PLANT, defined as: 19 - LLDPE Plant , 32 - PP Plant (New), 45 - Polyolefins PP/LLDPE Commons |  |  | 2 - | DELETED
| 2 - | SIZE indicates the size in INCHES |  |  | 3 - | DESIGN TEMPERATURE AND PRESSURE TO BE CONFIRMED BY EXTRUDER VENDOR
| 3 - | FLUID CODE as per P&ID Legend sheet |  |  | 4 - | DELETED
| 4 - | LINE NUMBER indicates the line number |  |  | 5 - | 1.5D-BENDS
| 5 - | PIPING CLASS Identifies the line class used for construction of the piping |  |  | 6 - | 5D-BENDS
| 6 - | INSULATION CODE identifies the insulation type according to P&ID Legend (Doc. 45-A-45-000-1-01-00001 sh.76 / 4274-VZ-DM-100000B0) and Insulation |  |  | 7 - | HAZARD GRADE REFERRED TO TRIGONOX 101 & LUPEROX 101
|  | general specifications |  |  | 8 - | DELETED
| 7 - | INSULATION THICKNESS indicates the thickness of the insulation in "mm" |  |  | 9 - | SPIROTALLIC GASKET (AISI 316L, FILLER GRAPHITE)
| 8 - | LINE ROUTING / FROM indicates the equipment, or the component, or the line where the line starts |  |  | 10 - | DELETED
| 9 - | LINE ROUTING / TO indicates the equipment, or the component, or the line where the line ends |  |  | 11 - | DELETED
| 10 - | DESIGN PRESSURE in Barg |  |  | 12 - | DELETED
| 11 - | DESIGN TEMPERATURE in Degrees Centigrade (℃) |  |  | 13 - | INTERNAL SURFACE OF PIPE TO BE MECHANICALLY POLISHED TO A FINAL ROUGHNESS < OR = TO 125 RMS.
| 12 - | OPERATION PRESSURE in Barg |  |  | 15 - | DELETED
| 13 - | OPERATION TEMPERATURE in Degrees Centigrade (℃) |  |  | 16 - | PROVIDE 5D BENDS FOR PIPING UP TO 2 INCHES
| 14 - | DENSITY, to be completed for liquid phase only. For vapor phase indicate the following "<50Kg/m³". For mixed phase indicate liquid density and vapor density |  |  | 17 - | INTERNAL SURFACE AND NOZZLES TO BE MECHANICALLY POLISHED TO A FINAL ROUGHNESS < OR = TO 63 RMS AND ELECTROPOLISHED
|  | (Company will fill after documetation handover) |  |  | 18 - | DELETED
| 15 - | TEST PRESSURE MINIMUM, is the minimum required test pressure to comply with applicable design code and PED. |  |  | 20 - | DELETED
|  | See also the Project specification piping pressure test (Doc. 45-L-45-000-2-00-80006 / 4274-XH-SG-00000004) |  |  | 22 - | DELETED
| 16 - | TEST PRESSURE MAX is the maximum allowable test pressure that the line can withstand at test conditions |  |  | 23 - | THREADED CONNECTIONS ARE ADMITTED IF SEAL WELDED
|  | See also the Project specification piping pressure test (Doc. 45-L-45-000-2-00-80006 / 4274-XH-SG-00000004) |  |  | 24 - | DELETED
| 17 - | TEST MEDIUM: H - Hydrostatic, S - Steam, N - Service test, P - Pneumatic, IO - Hydraulic test with Oil, V - Visual test |  |  | 25 - | FOR HYDROSTATIC VENTS,DRAINS, SHORT PIPE CONNECTION WITH TOP SCREW NPT TO BE PROVIDED FOR VALVE FOR RELATED ACTIVITY.
| 18 - | LINE CONTENT, specifies the fluid description as per P&ID Legend (Doc. 45-A-45-000-1-01-00001sh.76 / 4274-VZ-DM-100000B0) |  |  |  | AFTER TEST,DRAIN, REMOVE VALVE & PUT CAP SCREW & PROVIDE CIRCUMFERENTIAL SEAL WELD
| 19 - | FLUID STATE, indicates the phase of fluid: L - Liquid, V - Vapor, G - Gas, SL - Slurry, LG - Liquid + Gas, GS - Gas + Solid, S - Solid |  |  | 26 - | 3PLE ECCENTRIC METAL SEATED BUTTERFLY VALVES CAN BE USED.
| 20 - | STRESS ANALYSIS REQUIRED indicates if stress calculations are required (Yes/No) as per project specification |  |  | 28 - | OPERATING AND DESIGN CONDITIONS AS CONFIRMED WITH VENDOR.
|  | (Deleted) |  |  | 29 - | CONNECTED TO TEAL SERVICE. BALL VALVE O-RING EMERGENCY STEM SEAL MATERIAL : KALREZ SPECTRUM 6375 OR KALREZ SPECTRUM 7075, KALREZ 4079.
| 21 - | STRESS ANALYSIS TEMP. [To be completed by PROCS dept. for extreme temporary OPE cases not covered by Des conditions] |  |  | 31 - | DELETED
|  | (Deleted) |  |  | 32 - | DELETED
| 22 - | VAPOR PRESSURE AT MAX TEMP. indicated with "<1.5" or ">1.5" bar(a). The max temperature corresponds to the highest temperature among design and |  |  | 36 - | HYDROGEN SERVICE. DOUBLE VALVE TO BE PROVIDED FOR INSTRUMENTS AND VENTS GOING TO ATM.
|  | other design conditions (from REPSOL note) |  |  | 37 - | DESIGN CONDITIONS TO BE CONFIRMED BY VENDOR.
| 23 - | MIN OPE. TEMP. indicates the lowest temperature expected to occur during operation, including start-up and shutdown. |  |  | 38 - | PIPING MECHANICALLY POLISHED TO FINAL ROUGHNESS 125 RMS. PROVIDE PROTECTION AGAINST CORROSION BY ENI RUSTIA RUST PROTECTION (OR EQUIVALENT) AND
| 24 - | P&ID, indicates the sheet number as per Company doc: |  |  |  | PROTECTIVE COVERS AROUND THE FLANGES FOR LINE PRESERVAT.
|  | When in PLANT column 32 is indicated following P&ID code prefix applies: 32-A-32-000-1-01-00001 |  |  | 39 - | LINE SHALL BE PROVIDED WITH INTERMEDIATE DISMOUNTING FLANGES TO ALLOW EASY DISASSEMBLY FOR INSPECTION AND CLEANING. FLANGES TO BE LOCATED IN
|  | When in PLANT column 45 is indicated following P&ID code prefix applies: 45-A-45-000-1-01-00001 | Issue for Construction - Working Copy |  |  | ACCESSIBLE POSITION.
| 25 - | PED FLUID GROUP according to 2014/68/EU PED |  |  | 40 - | DELETED
| 26 - | PED CATEGORY according to 2014/68/EU PED |  |  | 41 - | DELETED
| 27 - | CONFORMITY ASSESSMENT MODULE according to 2014/68/EU PED |  |  | 42 - | DESIGN PRESSURE: HOLD
| 28 - | CE MARKING according to 2014/68/EU PED |  |  | 43 - | DESIGN TEMPERATURE TO BE CONFIRMED.
| 29 - | PAINT SYSTEM provides the paint system. According to General Painting specification (Doc 45-A-45-000-1-00-20160 / 4274-VW-SG-00000001) |  |  | 44 - | DELETED
| 30 - | APPLICABILITY, AS PER DEC. LAW 131/2019-D/2017 |  |  | 45 - | DELETED
| 31 - | SYSTEM AS PER DEC. LAW 131/2019-D/2017 |  |  | 46 - | LINE CARRYNG T2 TO REACTORS, XXS PIPE SCHEDULE REQUIRED (7.47 MM THICKNESS)
| 32 - | REGISTER NUMBER, AS PER DEC. LAW 131/2019-D/2017 |  |  | 47 - | OPERATING CONDITIONS TO BE CONFIRMED
| 33 - | WELD CLASS indicates the applicable welding class according to specification piping welding (doc. 4274-XH-SW-00000001) |  |  | 48 - | DELETED
| 34 - | PULSATING LINE indicates whether the line is subject to pressure pulsations (Y - PULSATING, N - NON PULSATING) |  |  | 49 - | DELETED
| 35 - | HAZARD FLUID indicates the hazardous code of fluid according to Dangerous properties of substances (19-A-19-000-1-00-40011 / 4274-SZ-SG-20000002 and |  |  | 51 - | STEAM SERVICE
|  | 32-A-32-000-1-00-40014 / 4274-SZ-SG-10000008) |  |  | 52 - | SEVERE CYCLIC SERVICE
| 36 - | WELD HEAT TREATMENT defines the requirements for welding heat treatment, according to specification piping welding (doc. 45-L-45-000-2-00-80021 / |  |  | 53 - | DELETED
|  | 4274-XH-SW-00000001). When "Y" is shown PWHT is required. |  |  | 54 - | CYCLIC SERVICE (0 TO 37.9 BARG). 550 CYCLES PER YEAR ESTIMATED
| 37 - | STREAM No. indicates the stream number according to Tecnimont stream list |  |  | 55 - | SOLID GRAVITY LINES
| 38 - | REMARKS indicate the referenceto the detailed notes listed under "Detail Notes Legend". |  |  | 56 - | SOLID/GAS CONVEYING
| 39 - | SUPPLY BY VENDOR indicates the Line List data as per Vendors Packages (under responsibility by relevant Vendors) |  |  | 57 - | 10D BENDS
[5 empty] | 58 - | 4D BEND USED ONLY FOR FIRST ELBOW ON PBT DISCHARGE. OTHER ELBOWS TO BE 10D BENDS AS PER PIPING CLASS.
[5 empty] | 62 - | DELETED
| HOLDS: |  |  |  | 63 - | TWO PHASE FLOW.
| a) | Deleted |  |  | 64 - | DURING A RARE ACCIDENTAL DEPRESSURIZATION, THE TEMPERATURE MAY REACH -79 °C AT ATMOSPHERIC PRESSURE.
| b) | Deleted |  |  | 65 - | LINES ARE SUBJECT TO VACUUM AT HIGH ELEVATIONS.
[5 empty] | 66 - | DELETED
[5 empty] | 67 - | ELECTRICAL TRACING TO BE LIMITED TO 80 °C MAXIMUM.
| GENERAL REMARKS: |  |  |  | 68 - | DUE TO OPERABILITY CONCERNS, PERSONNEL PROTECTION MAY CONSIST OF LABELLING AS A HOT SURFACE BUT SHALL NOT CONSIST OF THICK INSULATION WHICH WILL
| 1) | This revision of Line List is based on Stream list revision 12 (Internal information for Contractor only) |  |  |  | HINDER HEAT DISSIPATION FROM THE PROCESS LINES
| 2) | Deleted |  |  | 69 - | PRESSURE WILL CYCLE FROM 4.81 BARG TO 24.1 BARG AND FROM 24.1 BARG TO 4.81 BARG EVERY 2 TO 3 MINUTES.
| 3) | For lines with ATM discharge, only a Visual Test is required |  |  | 70 - | PRESSURE WILL CYCLE FROM 0 BARG TO 17.6 BARG AND FROM 17.6 BARG TO 0 BARG EVERY 2 TO 3 MINUTES.
[5 empty] | 71 - | PRESSURE WILL CYCLE FROM 0 BARG TO 7.55 BARG AND FROM 7.55 BARG TO 0 BARG EVERY 2 TO 3 MINUTES.
[5 empty] | 72 - | E-2114 HEATER WILL BE OPERATED FOR APPROXIMATELY 60 TIMES/YEAR FOR THE REGENERATION OF PURIFICATION BEDS. THE TEMPERATURE WILL CYCLE FROM 0 TO 330°C
AND THE PRESSURE WILL CYCLE FROM 0 TO 5 BARG
[5 empty] | 73 - | AS MUCH AS POSSIBLE FREE OF ANY INTERNAL WELD BEAD PROTRUSION. 0.5 MM ADMITTED FOR INACCESSIBLE WELDINGS.
[5 empty] | 74 - | LINES SUBJECTED TO HYDROGEN SERVICE.
[5 empty] | 75 - | USE A MINIMUM OF NINE DIAMETER BENDS TO FACILITATE CONVEYING OF SOLIDS. DO NOT POCKET.
CONFIDENTIALITY – This document and the information herein contained are the confidential proprietary information of ALBA project. Any disclosure to third parties, use, or reproduction without proper authorization is strictly prohibited.

## DATA
[7 empty] | ALBA PROJECT – PP AND PEL PLANTS | [26 empty] | OWNER IDENTIFICATION CODE
32-L-32-000-2-00-80601
CONTRACTOR IDENTIFICATION CODE
[7 empty] | PP PLANT (NEW) LINE LIST | [26 empty] | 4274-XH-LL-10000001
[34 empty] | Revision |  |  |  | Page
[34 empty] | 8 |  |  |  | 3 / 90
REPSOL POLIMEROS SA, SINES PORTUGAL
PIPELINE | REV | PLANT | SIZE (in) | FLUID CODE | LINE NUMBER | PIPING CLASS | INSULAT. CODE | INSUL THK. (Iin) | LINE ROUTING |  | DESIGN CONDIT. |  | OPERATION CONDIT. |  |  | TEST |  |  | SERVICE |  | STRESS ANALYSIS |  | VAPOR PRESSURE AT MAX TEMP. Bar(a) | MIN. TEMPERATURE (℃) | P&ID (REPSOL CODE) | 2014/68/EU PED |  |  |  | PAINT SYS | DEC. LAW 131/2019-D/2017 |  |  | WELD CLASS | PULSATING LINE (P/N) | HAZARD FLUID | WELD HEAT TREATMENT (Y/N) | STREAM No. | REMARKS
LINE | [8 empty] | FROM | TO | PRESS (barg) | TEMP. (℃) | PRESS (barg) | TEMP. (℃) | DENSITY (Kg/m³) | Pmin (barg) | Pmax (barg) | MEDIUM | LINE CONTENT | FLUID STATE | REQUIRED | TEMP. (℃) |  |  |  | FLUID GROUP | CATEGORY | CONFORMITY ASSESSMENT MODULE | CE MARKING |  | APPLICABILITY | SYSTEM | REGISTER NUMBER
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38
BDL40037 |  | 32 | 8" | BDL | 40037 | B32S1 | SB | 100 | PR40026 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40038 | 08 | 32 | 1/2" | BDL | 40038 | B32S1 | N | 0 | VZ40006 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40038 |  | 32 | 3/4" | BDL | 40038 | B32S1 | N | 0 | VZ40006 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40039 |  | 32 | 1/2" | BDL | 40039 | B32S1 | N | 0 | P40034 | BDL40042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40040 |  | 32 | 1/2" | BDL | 40040 | B32S1 | N | 0 | P40036 | BDL40043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40041 |  | 32 | 1/2" | BDL | 40041 | B32S1 | N | 0 | P40035 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40041 |  | 32 | 3/4" | BDL | 40041 | B32S1 | N | 0 | P40035 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40042 |  | 32 | 1" | BDL | 40042 | B32S1 | N | 0 | P40033 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40043 |  | 32 | 3/4" | BDL | 40043 | B32S1 | N | 0 | P40036 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40044 |  | 32 | 1/2" | BDL | 40044 | B32S1 | N | 0 | P40034 | BDL40039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40044 |  | 32 | 3/4" | BDL | 40044 | B32S1 | N | 0 | P40034 | BDL40039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40045 |  | 32 | 3/4" | BDL | 40045 | B32S1 | N | 0 | P40025 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40045 |  | 32 | 1" | BDL | 40045 | B32S1 | N | 0 | P40025 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40046 |  | 32 | 4" | BDL | 40046 | B32S1 | N | 0 | ET40007 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL42005 |  | 32 | 1" | BDL | 42005 | B32S1 | N | 0 | CO42017 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.32 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43015 |  | 32 | 1" | BDL | 43015 | B32S1 | N | 0 | PR43028 | BDL31026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43016 |  | 32 | 3/4" | BDL | 43016 | B32S1 | N | 0 | BDL24082 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FW68B50 |  | 45 | 3/4" | FW | 68B50 | B-7 | N | 0 | FW68B0J | FW68R07 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B51 | 08 | 45 | 8" | FW | 68B51 | PEB-69 | N | 0 | FW68A03 | FW68B0K | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B57 | 08 | 45 | 6" | FW | 68B57 | PEB-69 | N | 0 | FW68B0R | FW68A17 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B61 | 08 | 45 | 16" | FW | 68B61 | PEB-69 | N | 0 | FW68A17 | FW68B0V | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | TP-FW-02 |  | - | N | 000 | - | 73 | 76
FW68B65 | 08 | 45 | 6" | FW | 68B65 | PEB-69 | N | 0 | FW68A17 | FW68B0W | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B67 | 08 | 45 | 6" | FW | 68B67 | PEB-69 | N | 0 | FW68A17 | FW68B0X | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B72 | 08 | 45 | 6" | FW | 68B72 | PEB-69 | N | 0 | FW68B69 | FW68B0S | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B75 |  | 45 | 1-1/2" | FW | 68B75 | B-7 | N | 0 | FW68B15 | 45-HR-6817 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B77 |  | 45 | 1-1/2" | FW | 68B77 | B-7 | N | 0 | FW68B15 | 45-HR-6819 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B80 |  | 45 | 1-1/2" | FW | 68B80 | B-7 | N | 0 | FW68B36 | 45-HR-6814 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-01 |  | E | N | 000 | N | 75
FW68B81 |  | 45 | 1-1/2" | FW | 68B81 | B-7 | N | 0 | FW68B36 | 45-HR-6815 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-01 |  | E | N | 000 | N | 75
FW68B83 |  | 45 | 1-1/2" | FW | 68B83 | B-7 | N | 0 | FW68B40 | 45-HR-6821 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-02 |  | E | N | 000 | N | 75
FW68B84 |  | 45 | 1-1/2" | FW | 68B84 | B-7 | N | 0 | FW68B40 | 45-HR-6822 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-02 |  | E | N | 000 | N | 75
FW68B85 |  | 45 | 1-1/2" | FW | 68B85 | B-7 | N | 0 | FW68B40 | 45-HR-6823 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-02 |  | E | N | 000 | N | 75
FW68B92 |  | 45 | 10" | FW | 68B92 | UGB-1PE | N | 0 | FW68A55 | FW68A56 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B93 | 08 | 45 | 10" | FW | 68B93 | UGB-1PE | N | 0 | FW68A53 | FW68A54 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B94 |  | 45 | 6" | FW | 68B94 | UGB-1PE | N | 0 | FW15476 | 45-HY-6824 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B96 |  | 45 | 6" | FW | 68B96 | UGB-1PE | N | 0 | FW68B12 | 45-HY-6823 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B98 |  | 45 | 6" | FW | 68B98 | UGB-1PE | N | 0 | FW68B17 | 45-HY-6811 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68C01 |  | 32 | 3/4" | FW | 68C01 | B-7 | N | 0 | FW68A68 | FW68C04 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
BDL72046 |  | 32 | 1" | BDL | 72046 | B32S1 | N | 0 | BDL72050 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72047 |  | 32 | 3" | BDL | 72047 | B32S1 | N | 0 | PR72041 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72048 |  | 32 | 1" | BDL | 72048 | B32S1 | N | 0 | BDL72049 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72049 |  | 32 | 3/4" | BDL | 72049 | B32S1 | N | 0 | PR72025 | BDL72048 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72049 |  | 32 | 1" | BDL | 72049 | B32S1 | N | 0 | PR72025 | BDL72048 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72050 |  | 32 | 3/4" | BDL | 72050 | B32S1 | N | 0 | PR72002 | BDL72046 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72050 |  | 32 | 1" | BDL | 72050 | B32S1 | N | 0 | PR72002 | BDL72046 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72051 |  | 32 | 1" | BDL | 72051 | B32S1 | N | 0 | PR72024 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72052 |  | 32 | 1" | BDL | 72052 | B32S1 | N | 0 | PR72052 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72052 |  | 32 | 4" | BDL | 72052 | B32S1 | N | 0 | PR72052 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72063 | 08 | 32 | 1/2" | BDL | 72063 | B32S1 | N | 0 | PR72074 | BDL72064 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72064 | 08 | 32 | 1" | BDL | 72064 | B32S1 | P | 50 | 32-LI-7252 | BDL72060 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72067 | 08 | 32 | 4" | BDL | 72067 | B32S1 | N | 0 | TP-006 (N720166) | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72068 | 08 | 32 | 1" | BDL | 72068 | B32S1 | N | 0 | PR72063 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72069 | 08 | 32 | 3" | BDL | 72069 | B32S1 | N | 0 | PR72064 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72070 | 08 | 32 | 1" | BDL | 72070 | B32S1 | N | 0 | PR72066 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72070 | 08 | 32 | 4" | BDL | 72070 | B32S1 | N | 0 | PR72066 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72071 | 08 | 32 | 1" | BDL | 72071 | B32S1 | N | 0 | PR72065 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
DO12007 |  | 32 | 1/2" | DO | 12007 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12007 |  | 32 | 1" | DO | 12007 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12009 |  | 32 | 3/4" | DO | 12009 | 1CS2 | N | 0 | 32-S-1200A | N12018 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12010 |  | 32 | 1" | DO | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-S-1200B | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12011 |  | 32 | 1" | DO | 12011 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12012 |  | 32 | 3/4" | DO | 12012 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12012 |  | 32 | 8" | DO | 12012 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12013 |  | 32 | 1/2" | DO | 12013 | 1CS2 | N | 0 | 32-S-1200B | N12020 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12017 |  | 32 | 1/4" | DO | 12017 | 3FS3 | N | 0 | 32-P-1200A | DO12019 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12017 |  | 32 | 1/2" | DO | 12017 | 3FS3 | N | 0 | 32-P-1200A | DO12019 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
FW68I32 | 08 | 32 | 1-1/2" | FW | 68I32 | B-13 | N | 0 | FW68I41 | FW68I41 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I34 | 08 | 32 | 1" | FW | 68I34 | B-13 | N | 0 | FW68I22 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I37 | 08 | 32 | 1-1/2" | FW | 68I37 | B-13 | N | 0 | FW68I38 | FW68I38 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I40 | 08 | 32 | 1-1/2" | FW | 68I40 | B-13 | N | 0 | FW68I39 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I41 | 08 | 32 | 1-1/2" | FW | 68I41 | B-13 | N | 0 | FW68I32 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I42 | 08 | 32 | 1-1/2" | FW | 68I42 | B-13 | N | 0 | FW68I21 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68K14 | 08 | 32 | 3/4" | FW | 68K14 | B-13 | N | 0 | XV6803A | FW68K13 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68K15 | 08 | 32 | 3/4" | FW | 68K15 | B-13 | N | 0 | XV6809A | FW68K13 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68K03 |  | 32 | 1/2" | FW | 68K03 | B-7 | N | 0 | XV6804A | XV6804A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K03 |  | 32 | 6" | FW | 68K03 | B-7 | N | 0 | XV6804A | XV6804A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
ET22009 |  | 32 | 1" | ET | 22009 | 3FS4 | N | 0 | ET22008 | ET22007 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 041 | N | 322 | 36,10,5
ET22010 |  | 32 | 1" | ET | 22010 | 1FS4 | N | 0 | ET71035 | ET22007 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
ET22011 |  | 32 | 1" | ET | 22011 | 1FS4 | N | 0 | ET22010 | PR23012 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | Art 4.3 | NA | N | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
ET40005 |  | 32 | 1-1/2" | ET | 40005 | C3S1 | N | 0 | ET71039 | PR40029 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | C | N | 041 | N | 323 | ,10
ET40007 |  | 32 | 3" | ET | 40007 | C3S1 | N | 0 | ET71039 | BDL40046 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
IA32002 | 08 | 32 | 1/2" | IA | 32002 | B-13 | N | 0 | IA62075 | TP-07B (32-PCV-3283) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62001 | 08 | 32 | 3" | IA | 62001 | B-13 | N | 0 | IA62004 | IA62075 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62002 | 08 | 32 | 1" | IA | 62002 | C3S1 | N | 0 | TP-2 (IA620102) | 32-D-6200 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA62003 | 08 | 32 | 3/4" | IA | 62003 | C3S1 | N | 0 | 32-D-6200 | IA62004 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA62003 | 08 | 32 | 2" | IA | 62003 | C3S1 | N | 0 | 32-D-6200 | IA62004 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA62004 | 08 | 32 | 3" | IA | 62004 | B-13 | N | 0 | IA62003 | IA62904 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62005 | 08 | 32 | 1" | IA | 62005 | B-13 | N | 0 | IA01001 | TP-1 (IA-620105-TUBING) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62008 | 08 | 32 | 1" | IA | 62008 | C3S1 | N | 0 | 32-D-6200 | VA62001 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA6200B | 08 | 32 | 3/4" | IA | 6200B | B-13 | N | 0 | IA620A0 | IA810109 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200C | 08 | 32 | 3/4" | IA | 6200C | B-13 | N | 0 | IA620A0 | IA810115 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200G | 08 | 32 | 1" | IA | 6200G | B-13 | N | 0 | IA02002 | 32-IAM-047 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
HCM24063 |  | 32 | 1" | HCM | 24063 | 3FS4 | HB | 30 | 32-T-2401 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 122.48 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 27 | N | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24063 |  | 32 | 2" | HCM | 24063 | 3FS4 | HB | 40 | 32-T-2401 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 122.48 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 27 | Y | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24063 |  | 32 | 8" | HCM | 24063 | 3FS4 | HB | 40 | 32-T-2401 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 122.48 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 27 | Y | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24064 |  | 32 | 3/4" | HCM | 24064 | 3FS4 | CF | 25 | 32-E-2404 | HCM24055 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24064 |  | 32 | 1-1/2" | HCM | 24064 | 3FS4 | CF | 25 | 32-E-2404 | HCM24055 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24064 |  | 32 | 4" | HCM | 24064 | 3FS4 | CF | 25 | 32-E-2404 | HCM24055 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24065 |  | 32 | 1/2" | HCM | 24065 | 3FS4 | HB | 30 | HCM24098 | HCM24063 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24065 |  | 32 | 1-1/2" | HCM | 24065 | 3FS4 | HB | 30 | HCM24098 | HCM24063 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24066 |  | 32 | 3/4" | HCM | 24066 | C42S1 | N | 0 | 32-T-2401 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24066 |  | 32 | 1-1/2" | HCM | 24066 | C42S1 | N | 0 | 32-T-2401 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24066 |  | 32 | 3" | HCM | 24066 | C42S1 | N | 0 | 32-T-2401 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24069 |  | 32 | 1" | HCM | 24069 | D20S1 | HB | 30 | 32-P-2400A | 32-S-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24069 |  | 32 | 6" | HCM | 24069 | D20S1 | HB | 30 | 32-P-2400A | 32-S-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24070 |  | 32 | 3/4" | HCM | 24070 | D20S1 | HB | 30 | HCM24057 | BDL24070 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24070 |  | 32 | 3" | HCM | 24070 | D20S1 | HB | 30 | HCM24057 | BDL24070 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24072 |  | 32 | 4" | HCM | 24072 | D20S1 | P | 50 | 32-S-2400 | HCM24073 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24073 |  | 32 | 1" | HCM | 24073 | D20S1 | P | 50 | HCM24072 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24073 |  | 32 | 10" | HCM | 24073 | D20S1 | P | 100 | HCM24072 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
BDL24073 |  | 32 | 2" | BDL | 24073 | B32S1 | N | 0 | BDL21008 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24074 |  | 32 | 3/4" | BDL | 24074 | B32S1 | N | 0 | BDL24071 | BDL24001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24074 |  | 32 | 1" | BDL | 24074 | B32S1 | N | 0 | BDL24071 | BDL24001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24075 |  | 32 | 1/2" | BDL | 24075 | B32S1 | N | 0 | VZ24004 | BDL24069 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24076 |  | 32 | 1" | BDL | 24076 | B32S1 | N | 0 | HCM24064 | BDL24068 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24077 |  | 32 | 1/2" | BDL | 24077 | B32S1 | N | 0 | HCM24064 | BDL24076 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24078 |  | 32 | 3/4" | BDL | 24078 | B32S1 | N | 0 | HCM24098 | BDL24069 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24078 |  | 32 | 1" | BDL | 24078 | B32S1 | N | 0 | HCM24098 | BDL24069 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24079 |  | 32 | 6" | BDL | 24079 | B32S1 | N | 0 | BDL23016 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24080 |  | 32 | 3" | BDL | 24080 | B32S1 | N | 0 | HCM24052 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24080 |  | 32 | 6" | BDL | 24080 | B32S1 | N | 0 | HCM24052 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24081 |  | 32 | 1/2" | BDL | 24081 | B32S1 | N | 0 | HCM24079 | BDL31026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24081 |  | 32 | 3/4" | BDL | 24081 | B32S1 | N | 0 | HCM24079 | BDL31026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24082 |  | 32 | 1" | BDL | 24082 | B32S1 | N | 0 | HCM24078 | BDL43016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24083 |  | 32 | 1" | BDL | 24083 | B32S1 | N | 0 | PR22014 | BDL23055 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24084 |  | 32 | 1" | BDL | 24084 | B32S1 | N | 0 | BDL24061 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24085 |  | 32 | 1/2" | BDL | 24085 | B32S1 | N | 0 | VZ24009 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24085 |  | 32 | 1" | BDL | 24085 | B32S1 | N | 0 | VZ24009 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CWR64015 |  | 32 | 20" | CWR | 64015 | UGB-1PE | N | 0 | CWR64001 | CWR01010 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-03 |  | E | N | 000 | N | 16
N51007 |  | 32 | 1/2" | N | 51007 | B-1 | N | 0 | N67062 | PW51014 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 000 | N | 140
N52026 |  | 32 | 1/2" | N | 52026 | 1CS2 | N | 0 | N52025 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N52027 |  | 32 | 1/2" | N | 52027 | 1CS2 | N | 0 | N52025 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N52028 |  | 32 | 1/2" | N | 52028 | 1CS2 | N | 0 | N52025 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
JWR64046 |  | 32 | 4" | JWR | 64046 | B-1 | N | 0 | JWR51001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64047 |  | 32 | 3" | JWR | 64047 | B-1 | N | 0 | JWR32003 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71001 | 08 | 32 | 2" | JWR | 71001 | B-1 | N | 0 | TP-13, JWR710101 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71001 | 08 | 32 | 4" | JWR | 71001 | B-1 | N | 0 | TP-13, JWR710101 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71002 |  | 32 | 2" | JWR | 71002 | C3S1 | N | 0 | 32-E-7102 | JWR71003 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR71003 |  | 32 | 2" | JWR | 71003 | B-1 | N | 0 | JWR71002 | JWR71001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.48 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71006 |  | 32 | 1-1/2" | JWR | 71006 | C3S1 | N | 0 | JWR71002 | VA71005 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR72001 |  | 32 | 6" | JWR | 72001 | B-1 | N | 0 | JWR72005 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.51 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR72002 |  | 32 | 4" | JWR | 72002 | B-1 | N | 0 | JWR72004 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.51 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR72003 | 08 | 32 | 2" | JWR | 72003 | B-1 | N | 0 | TP-008 (JWR720142) | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR72004 |  | 32 | 3/4" | JWR | 72004 | D20S1 | N | 0 | 32-E-7203 | JWR72002 | 33.7/33.7 | 245.0/-45.0 | 5.0 | 40.0 |  | 52.54 | 150.8 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 141 | N | 1031
JWR72005 |  | 32 | 6" | JWR | 72005 | C42S1 | N | 0 | 32-E-7200 | JWR72001 | 33.7/33.7 | 150.0/-45.0 | 3.0 | 46.0 |  | 50.56 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 46 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-U-022-02 |  | M | N | 141 | N | 1033
JWR72007 |  | 32 | 1-1/2" | JWR | 72007 | D20S1 | N | 0 | JWR72004 | VA72002 | 33.7/33.7 | 245.0/-45.0 | 5.0 | 40.0 |  | 52.54 | 153.15 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 141 | N | 1031
JWR73001 |  | 32 | 1/2" | JWR | 73001 | B-1 | N | 0 | JW73001 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.55 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWS23003 |  | 32 | 8" | JWS | 23003 | B-1 | N | 0 | JWS64047 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
N80010 |  | 32 | 3/4" | N | 80010 | 1CS2 | N | 0 | N89010 | TP-030 (32-S-8001A) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
PR33006 |  | 32 | 4" | PR | 33006 | C42S1 | HB | 30 | 32-D-3300 | BDL33007 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33007 |  | 32 | 4" | PR | 33007 | C42S1 | HA | 30 | 32-E-3301 | 32-D-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33008 |  | 32 | 8" | PR | 33008 | C42S1 | N | 0 | PR24033 | 32-D-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33010 |  | 32 | 3/4" | PR | 33010 | C42S1 | N | 0 | 32-P-3300A | 32-D-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33012 |  | 32 | 1" | PR | 33012 | C42S1 | N | 0 | PR33013 | 32-E-3301 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33012 |  | 32 | 3" | PR | 33012 | C42S1 | N | 0 | PR33013 | 32-E-3301 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33014 |  | 32 | 3/4" | PR | 33014 | C42S1 | N | 0 | PR72002 | PR33013 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33014 |  | 32 | 1-1/2" | PR | 33014 | C42S1 | N | 0 | PR72002 | PR33013 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33015 |  | 32 | 1/2" | PR | 33015 | C42S1 | N | 0 | 32-D-3300 | PR33016 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33016 |  | 32 | 3/4" | PR | 33016 | D20S1 | N | 0 | PR33015 | 32-P-3300A | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
LS02001 |  | 32 | 1-1/2" | LS | 02001 | B-5 | HB | 70 | LS63177 | LS66002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS02003 |  | 32 | 3/4" | LS | 02003 | B-5 | HB | 60 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
BDL43016 |  | 32 | 1" | BDL | 43016 | B32S1 | N | 0 | BDL24082 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43018 |  | 32 | 1" | BDL | 43018 | B32S1 | N | 0 | PR43049 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43018 |  | 32 | 6" | BDL | 43018 | B32S1 | N | 0 | PR43049 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CWR89049 | 08 | 32 | 3/4" | CWR | 89049 | B-1 | N | 0 | CWR89037 | VA89022 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR91001 | 08 | 32 | 1-1/2" | CWR | 91001 | B-1 | N | 0 | 32-E-9004 | CWR64001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR91001 | 08 | 32 | 3" | CWR | 91001 | B-1 | N | 0 | 32-E-9004 | CWR64001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
FW68C02 |  | 32 | 1/2" | FW | 68C02 | B-7 | N | 0 | FW68C01 | 32-XV-6801A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C03 |  | 32 | 1/2" | FW | 68C03 | B-7 | N | 0 | FW68C01 | 32-XV-6802A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C04 |  | 32 | 6" | FW | 68C04 | B-7 | N | 0 | FW68C01 | 32-XV-6810A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C09 | 08 | 32 | 4" | FW | 68C09 | B-13 | N | 0 | 32-XV-6810A | FW68Q01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68C10 | 08 | 32 | 4" | FW | 68C10 | B-13 | N | 0 | 32-XV-6808A | FW68O14 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
HOR89003 | 08 | 32 | 4" | HOR | 89003 | C-2 | HA | 90 | TP-N42502 (32-CPN-A408) | TP-N60204 (32-P-8908C/D) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL RETURN | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 209
BDL72072 | 08 | 32 | 1" | BDL | 72072 | B32S1 | HA | 30 | PR72060 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 20 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72072 | 08 | 32 | 3" | BDL | 72072 | B32S1 | HA | 30 | PR72060 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 20 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72076 |  | 32 | 1/2" | BDL | 72076 | B32S1 | N | 0 | PR72053 | BDL72040 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL73040 |  | 32 | 2" | BDL | 73040 | B4S1 | N | 0 | BU73087 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73041 |  | 32 | 1" | BDL | 73041 | B4S1 | N | 0 | BU73087 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73042 |  | 32 | 3/4" | BDL | 73042 | B4S1 | N | 0 | BU73087 | BDL73041 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73042 |  | 32 | 1" | BDL | 73042 | B4S1 | N | 0 | BU73087 | BDL73041 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73043 |  | 32 | 1" | BDL | 73043 | B4S1 | N | 0 | BU73053 | BDL73044 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73044 |  | 32 | 1" | BDL | 73044 | B4S1 | N | 0 | 32-P-7300 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73044 |  | 32 | 1-1/2" | BDL | 73044 | B4S1 | N | 0 | 32-P-7300 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73045 |  | 32 | 1" | BDL | 73045 | B4S1 | N | 0 | BU73051 | BDL73044 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73046 |  | 32 | 1/2" | BDL | 73046 | B4S1 | N | 0 | BU73047 | BDL73044 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
FW68K04 |  | 32 | 1/2" | FW | 68K04 | B-7 | N | 0 | XV6806A | XV6806A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K04 |  | 32 | 6" | FW | 68K04 | B-7 | N | 0 | XV6806A | XV6806A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K05 | 08 | 32 | 6" | FW | 68K05 | B-13 | N | 0 | XV6806A | FW68N09 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68K06 | 08 | 32 | 3" | FW | 68K06 | B-13 | N | 0 | XV6804A | FW68M25 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68K06 | 08 | 32 | 6" | FW | 68K06 | B-13 | N | 0 | XV6804A | FW68M25 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68K08 |  | 32 | 12" | FW | 68K08 | B-7 | N | 0 | FW68A22 | FW68K09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K09 |  | 32 | 3/4" | FW | 68K09 | B-7 | N | 0 | FW68K11 | FW68K01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K09 |  | 32 | 12" | FW | 68K09 | B-7 | N | 0 | FW68K11 | FW68K01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K11 |  | 32 | 12" | FW | 68K11 | B-7 | N | 0 | FW68A19 | FW68K09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K13 | 08 | 32 | 3/4" | FW | 68K13 | B-13 | N | 0 | FW68K01 | WATER ALARM GONG | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68L02 | 08 | 32 | 4" | FW | 68L02 | B-13 | N | 0 | FW68K12 | FW68L10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L05 | 08 | 32 | 3" | FW | 68L05 | B-13 | N | 0 | FW68K12 | FW68L20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L05 | 08 | 32 | 6" | FW | 68L05 | B-13 | N | 0 | FW68K12 | FW68L20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L07 | 08 | 32 | 2" | FW | 68L07 | B-13 | N | 0 | MSN-002 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L16 | 08 | 32 | 1" | FW | 68L16 | B-13 | N | 0 | MSN-001 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L16 | 08 | 32 | 3" | FW | 68L16 | B-13 | N | 0 | MSN-001 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L20 | 08 | 32 | 1-1/2" | FW | 68L20 | B-13 | N | 0 | FW68L05 | MSN-006 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L23 | 08 | 32 | 1" | FW | 68L23 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68L23 | 08 | 32 | 2" | FW | 68L23 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
IA01001 | 08 | 32 | 3" | IA | 01001 | B-13 | N | 0 | IA300003 OSBL LINE | IA62092 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.2 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA02002 | 08 | 32 | 1" | IA | 02002 | B-13 | N | 0 | IA62077 | IA02008 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
CHWR14002 |  | 32 | 1-1/2" | CHWR | 14002 | B-1 | CF | 25 | CHWS14012 | CHWR61016 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR14003 |  | 32 | 1-1/2" | CHWR | 14003 | B-1 | CF | 25 | CHWS14015 | CHWR61016 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
IA6200I | 08 | 32 | 1" | IA | 6200I | B-13 | N | 0 | IA02002 | 32-IAM-048 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200J | 08 | 32 | 1" | IA | 6200J | B-13 | N | 0 | IA6200K | 32-IAM-046 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200K | 08 | 32 | 1" | IA | 6200K | B-13 | N | 0 | IA62077 | 32-IAM-043 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200L | 08 | 32 | 1" | IA | 6200L | B-13 | N | 0 | IA62077 | 32-IAM-051 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200P | 08 | 32 | 1" | IA | 6200P | B-13 | N | 0 | IA62001 | 32-IAM-036 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200Q | 08 | 32 | 1" | IA | 6200Q | B-13 | N | 0 | IA62078 | 32-IAM-003 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200S | 08 | 32 | 1" | IA | 6200S | B-13 | N | 0 | IA62078 | 32-IAM-002 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200Y | 08 | 32 | 1/2" | IA | 6200Y | B-13 | N | 0 | IA62001 | 32-IAT-002 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA6200Z | 08 | 32 | 3/4" | IA | 6200Z | B-13 | N | 0 | IA62077 | 32-IAT-139 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA62010 | 08 | 32 | 1" | IA | 62010 | B-13 | N | 0 | IA62003 | 32-IAM-127 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-02 |  | - | N | 000 | - | 200
IA62011 | 08 | 32 | 1" | IA | 62011 | B-13 | N | 0 | IA62001 | 32-IAM-040 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62013 | 08 | 32 | 1" | IA | 62013 | B-13 | N | 0 | IA62074 | 32-IAM-041 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62014 | 08 | 32 | 1" | IA | 62014 | B-13 | N | 0 | IA62074 | 32-IAM-039 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62015 | 08 | 32 | 1" | IA | 62015 | B-13 | N | 0 | IA62001 | 32-IAM-050 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
CHWS61003 |  | 32 | 1" | CHWS | 61003 | B-1 | CF | 25 | CHWS61028 | CHWS14008 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
LS50049 |  | 32 | 3/4" | LS | 50049 | 3CS6 | HB | 60 | 32-S-5001 | LS50002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 11.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | M | N | 000 | N | 103
LS51001 |  | 32 | 3/4" | LS | 51001 | B-5 | HB | 60 | 32-D-5102 | LC51004 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS51003 |  | 32 | 3/4" | LS | 51003 | B-5 | HB | 60 | 32-D-5101 | LC51007 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS51004 |  | 32 | 1/2" | LS | 51004 | B-5 | HB | 60 | 32-D-5104 | LC51006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-U-060-01 |  | E | N | 000 | N | 90
LS52005 |  | 32 | 3/4" | LS | 52005 | B-5 | HB | 30 | LS50036 | 32-H-5201 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-052-03 |  | E | N | 000 | N | 92
LS52006 |  | 32 | 3/4" | LS | 52006 | B-5 | HB | 30 | 32-D-5200 | LC52003 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS52007 |  | 32 | 1/2" | LS | 52007 | B-5 | HB | 30 | 32-PK-8001 | LC52001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-052-03 |  | E | N | 000 | N | 92
LS52008 |  | 32 | 1" | LS | 52008 | B-5 | HB | 70 | 32-E-5200 | LC52002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.37 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60003 |  | 32 | 1/2" | LS | 60003 | B-5 | HB | 60 | LS63047 | 32-D-6001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60004 |  | 32 | 3" | LS | 60004 | B-5 | HB | 80 | BDH60006 | 32-D-6002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60005 |  | 32 | 1-1/2" | LS | 60005 | B-5 | HB | 70 | LS63047 | 32-D-6002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60008 |  | 32 | 1-1/2" | LS | 60008 | B-5 | HB | 70 | 32-D-6002 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60009 |  | 32 | 1-1/2" | LS | 60009 | B-5 | HB | 70 | LS63047 | BDL60001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60010 |  | 32 | 1" | LS | 60010 | B-5 | HB | 70 | PURGE CONNECTION | BDL60042 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78A | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
HCM24074 |  | 32 | 3/4" | HCM | 24074 | D20S1 | HB | 30 | 32-P-2400B | BDL24065 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24074 |  | 32 | 8" | HCM | 24074 | D20S1 | HB | 40 | 32-P-2400B | BDL24065 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24075 |  | 32 | 6" | HCM | 24075 | D20S1 | P | 50 | HCM24073 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24076 |  | 32 | 3" | HCM | 24076 | D20S1 | HB | 30 | 32-T-2400 | BDL24079 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24077 |  | 32 | 3/4" | HCM | 24077 | D20S1 | P | 50 | 32-T-2400 | 32-E-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24078 |  | 32 | 2" | HCM | 24078 | D20S1 | P | 50 | 32-E-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24078 |  | 32 | 4" | HCM | 24078 | D20S1 | P | 50 | 32-E-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24079 |  | 32 | 1/2" | HCM | 24079 | D20S1 | HB | 30 | HCM24080 | HCM24078 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24079 |  | 32 | 1" | HCM | 24079 | D20S1 | HB | 30 | HCM24080 | HCM24078 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24079 |  | 32 | 2" | HCM | 24079 | D20S1 | HB | 30 | HCM24080 | HCM24078 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24080 |  | 32 | 6" | HCM | 24080 | D20S1 | ET | 30 | 32-E-2400 | HCM24059 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24081 |  | 32 | 3/4" | HCM | 24081 | D20S1 | ET | 30 | HCM24080 | HCM24059 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24082 |  | 32 | 3/4" | HCM | 24082 | D20S1 | N | 0 | HCM24083 | PR24007 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 530 | 15
HCM24082 |  | 32 | 2" | HCM | 24082 | D20S1 | N | 0 | HCM24083 | PR24007 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-02 |  | F | N | 141 | N | 530 | 15
HCM24083 |  | 32 | 1" | HCM | 24083 | D20S1 | N | 0 | 32-E-2403 | PR24037 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24083 |  | 32 | 2" | HCM | 24083 | D20S1 | N | 0 | 32-E-2403 | PR24037 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24085 |  | 32 | 1-1/2" | HCM | 24085 | D20S1 | P | 50 | HCM24097 | 32-E-2403 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 150.8 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
BDL24086 |  | 32 | 1/2" | BDL | 24086 | B32S1 | N | 0 | HCM24087 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24087 |  | 32 | 3/4" | BDL | 24087 | B32S1 | N | 0 | HCM24083 | BDL40046 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24087 |  | 32 | 2" | BDL | 24087 | B32S1 | N | 0 | HCM24083 | BDL40046 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24088 |  | 32 | 3/4" | BDL | 24088 | B32S1 | N | 0 | HCM24094 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24089 |  | 32 | 1" | BDL | 24089 | B32S1 | N | 0 | HCM24080 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CWR01010 |  | 32 | 3/4" | CWR | 01010 | UGB-1PE | N | 0 | CWR00C01 | 48"-CW-200002-B1 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
CWR01010 |  | 32 | 44" | CWR | 01010 | UGB-1PE | N | 0 | CWR00C01 | 48"-CW-200002-B1 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
PCW89009 | 08 | 32 | 12" | PCW | 89009 | 4CS2 | P | 100 | 32-Z-8906 | TP-N50401 (A-8900) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | SL | - | - | <1.5 | 60 | sh.68K | 2 | I | MOD.A | Y | 5 | N | 32-P-070-07 |  | M | N | 110 | N | 451 | 3,6
PCW89011 | 08 | 32 | 12" | PCW | 89011 | 1CS2 | P | 100 | TP-N50802 (S-8910A/B) | TP-N50901 (E-8900A) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PCW89012 | 08 | 32 | 16" | PCW | 89012 | 1CS2 | P | 100 | TPN50402 (A-8900) | TP-N50601 (S-8909A/B/C/D) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PCW89015 | 08 | 32 | 2" | PCW | 89015 | 1CS2 | P | 50 | TP-N51705 (XV-8941) | PCW89012 | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
N52030 |  | 32 | 3/4" | N | 52030 | 1CS2 | N | 0 | N52035 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N52031 |  | 32 | 1/2" | N | 52031 | 1CS2 | N | 0 | N67044 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N52033 |  | 32 | 1/2" | N | 52033 | 1CS2 | N | 0 | N67043 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N52033 |  | 32 | 1" | N | 52033 | 1CS2 | N | 0 | N67043 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N52036 |  | 32 | 3/4" | N | 52036 | 1CS2 | N | 0 | N67045 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N52037 |  | 32 | 3/4" | N | 52037 | 1CS2 | HB | 30 | N52042 | PN52021 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | NA | NA | NA | NR | N | 32-P-052-02 |  | M | N | 000 | N | 154
N52041 |  | 32 | 3/4" | N | 52041 | 1CS2 | N | 0 | N67064 | PN52029 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 166
N52041 |  | 32 | 1-1/2" | N | 52041 | 1CS2 | N | 0 | N67064 | PN52029 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 166
N52042 |  | 32 | 3/4" | N | 52042 | 1CS2 | N | 0 | N52041 | N52043 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | NA | NA | NA | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 154
N52042 |  | 32 | 1-1/2" | N | 52042 | 1CS2 | N | 0 | N52041 | N52043 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | NA | NA | NA | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 154
N52043 |  | 32 | 2" | N | 52043 | 1CS2 | N | 0 | N52042 | VA52013 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | NA | NA | NA | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 154
JWS23004 |  | 32 | 1-1/2" | JWS | 23004 | B-1 | N | 0 | JWS64057 | 32-E-2350 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS24010 |  | 32 | 3/4" | JWS | 24010 | D20S1 | N | 0 | JWS64051 | 32-E-2400 | 49.0/49.0 | -45.0/150.0 | 5.0 | 30.0 |  | 73.51 | 128.56 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-01 |  | M | N | 000 | N | 1020
JWS24011 |  | 32 | 3/4" | JWS | 24011 | D20S1 | N | 0 | JWS64052 | 32-E-2403 | 49.0/49.0 | -45.0/150.0 | 5.0 | 30.0 |  | 73.51 | 128.56 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-01 |  | M | N | 000 | N | 1020
PR33016 |  | 32 | 8" | PR | 33016 | D20S1 | N | 0 | PR33015 | 32-P-3300A | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33018 |  | 32 | 1" | PR | 33018 | D20S1 | N | 0 | PR33017 | 32-P-3300B | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33018 |  | 32 | 10" | PR | 33018 | D20S1 | N | 0 | PR33017 | 32-P-3300B | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33019 |  | 32 | 1/2" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33019 |  | 32 | 1" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33019 |  | 32 | 3" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33019 |  | 32 | 4" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33019 |  | 32 | 6" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33020 |  | 32 | 3/4" | PR | 33020 | D20S1 | N | 0 | 32-P-3300B | PR33025 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33020 | 08 | 32 | 6" | PR | 33020 | D20S1 | N | 0 | 32-P-3300B | PR33025 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33022 | 08 | 32 | 4" | PR | 33022 | D20S1 | N | 0 | PR33019 | PR33021 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33023 | 08 | 32 | 1" | PR | 33023 | C42S1 | N | 0 | PR72002 | PR40022 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33023 | 08 | 32 | 2" | PR | 33023 | C42S1 | N | 0 | PR72002 | PR40022 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33024 | 08 | 32 | 1" | PR | 33024 | C42S1 | N | 0 | PR33023 | TP-011 (PR610116) | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33027 | 08 | 32 | 1/2" | PR | 33027 | C42S1 | N | 0 | 32-E-3301 | BDL33003 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33027 | 08 | 32 | 3" | PR | 33027 | C42S1 | N | 0 | 32-E-3301 | BDL33003 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33028 | 08 | 32 | 1/2" | PR | 33028 | C42S1 | N | 0 | PR33015 | BDL33008 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
LS13001 |  | 32 | 1" | LS | 13001 | B-5 | HB | 70 | LS63069 | LS13002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13002 |  | 32 | 1-1/2" | LS | 13002 | B-5 | HB | 70 | LS13001 | 32-D-1300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13004 |  | 32 | 1/2" | LS | 13004 | B-5 | HB | 60 | 32-D-1301 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13004 |  | 32 | 3/4" | LS | 13004 | B-5 | HB | 60 | 32-D-1301 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13004 |  | 32 | 1-1/2" | LS | 13004 | B-5 | HB | 70 | 32-D-1301 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13005 |  | 32 | 1-1/2" | LS | 13005 | B-5 | HB | 70 | 32-D-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13006 |  | 32 | 3/4" | LS | 13006 | B-5 | HB | 60 | JLS13001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13008 |  | 32 | 3/4" | LS | 13008 | B-5 | HB | 60 | LS63004 | 32-E-1300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-P-025-01 |  | E | N | 000 | N | 90
LS13009 |  | 32 | 3/4" | LS | 13009 | B-5 | HB | 60 | 32-E-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13010 |  | 32 | 1/2" | LS | 13010 | B-5 | HB | 60 | 32-S-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13011 |  | 32 | 1/2" | LS | 13011 | B-5 | HB | 60 | 32-P-1300 | LS63054 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS14001 |  | 32 | 1/2" | LS | 14001 | B-5 | HB | 60 | 32-E-1400A | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS14002 |  | 32 | 3/4" | LS | 14002 | B-5 | HB | 60 | 32-E-1400B | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS14003 |  | 32 | 3/4" | LS | 14003 | B-5 | HB | 60 | JLS14001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
PR50010 |  | 32 | 4" | PR | 50010 | B4S1 | P | 50 | P50013 | 32-T-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
PR50011 | 08 | 32 | 3/4" | PR | 50011 | B4S1 | N | 0 | 32-T-5001 | TP-N1 (PR510101) | 5.0/-1.0 | 180.0/180.0 | 0.2 | 40.0 |  | 7.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.35 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 373 | ,10
PR50012 | 08 | 32 | 6" | PR | 50012 | B4S1 | N | 0 | PR50011 | BDL50002 | 5.0/-1.0 | 180.0/180.0 | 0.2 | 40.0 |  | 7.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.35 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 373 | ,10
PR50013 |  | 32 | 3/4" | PR | 50013 | 1CS2 | ET | 30 | 32-D-5001 | PROPYLENE TO S-3400 DIFF. PRESS. TRANS. | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.02 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | 27 | N | 32-P-050-01 |  | G | N | 141 | N | 390 | ,10
PR50015 |  | 32 | 6" | PR | 50015 | B4S1 | P | 50 | PR50010 | BDL50001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
PR51015 | 08 | 32 | 1/2" | PR | 51015 | B4S1 | ST | 30 | TP-N2 (PR510110) | TP-001, PR530101 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | I | MOD.A | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR51015 | 08 | 32 | 3" | PR | 51015 | B4S1 | ST | 30 | TP-N2 (PR510110) | TP-001, PR530101 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | I | MOD.A | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR51017 | 08 | 32 | 2" | PR | 51017 | B4S1 | ST | 30 | D-5110 (TP-N15) | PR51016 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR51017 | 08 | 32 | 6" | PR | 51017 | B4S1 | ST | 30 | D-5110 (TP-N15) | PR51016 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR51018 | 08 | 32 | 1/2" | PR | 51018 | B4S1 | ST | 30 | PR51015 | BDL51022 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | Art 4.3 | NA | N | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
LC52001 |  | 32 | 3/4" | LC | 52001 | B-5 | HB | 30 | LS52007 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC52002 |  | 32 | 1" | LC | 52002 | B-5 | HB | 40 | LS52008 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC52002 |  | 32 | 1-1/2" | LC | 52002 | B-5 | HB | 40 | LS52008 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC52003 |  | 32 | 3/4" | LC | 52003 | B-5 | HB | 30 | LS52006 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC52005 |  | 32 | 3/4" | LC | 52005 | B-5 | HB | 30 | LS52006 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC52007 |  | 32 | 3/4" | LC | 52007 | B-5 | HB | 30 | LS52007 | WW52011 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC60001 |  | 32 | 1/2" | LC | 60001 | B-5 | HB | 30 | LS60002 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.41 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC60002 |  | 32 | 3/4" | LC | 60002 | B-5 | HB | 30 | LS63046 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS63042 |  | 32 | 1/2" | LS | 63042 | B-5 | HB | 60 | LS63193 | LS63044 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63043 |  | 32 | 1/2" | LS | 63043 | B-5 | HB | 60 | LS63040 | HCM23066 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63044 |  | 32 | 1/2" | LS | 63044 | B-5 | HB | 60 | LS63042 | JLS23017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63045 |  | 32 | 3/4" | LS | 63045 | B-5 | HB | 60 | LS63193 | JLS23009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63045 |  | 32 | 2" | LS | 63045 | B-5 | HB | 80 | LS63193 | JLS23009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63046 |  | 32 | 1/2" | LS | 63046 | B-5 | HB | 60 | LS63206 | 32-D-6011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63046 |  | 32 | 1" | LS | 63046 | B-5 | HB | 70 | LS63206 | 32-D-6011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AG |  | 32 | 1/2" | LS | 630AG | B-5 | HB | 60 | LS63201 | PR31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AH |  | 32 | 1/2" | LS | 630AH | B-5 | HB | 60 | LS63193 | PR31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AI |  | 32 | 1/2" | LS | 630AI | B-5 | HB | 60 | LS63193 | PR31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AJ |  | 32 | 3/4" | LS | 630AJ | B-5 | HB | 60 | LS63201 | HCM23057 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AK |  | 32 | 3/4" | LS | 630AK | B-5 | HB | 60 | LS630AL | JLS23009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AL |  | 32 | 1" | LS | 630AL | B-5 | HB | 70 | LS63193 | JLS23010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AP |  | 32 | 1" | LS | 630AP | B-5 | HB | 70 | LS63199 | PR31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AR |  | 32 | 1" | LS | 630AR | B-5 | HB | 70 | LS63201 | PR31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AS |  | 32 | 1" | LS | 630AS | B-5 | HB | 70 | LS630AR | PR31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AT |  | 32 | 3/4" | LS | 630AT | B-5 | HB | 60 | LS63193 | PR31016 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AU |  | 32 | 1-1/2" | LS | 630AU | B-5 | HB | 70 | LS63193 | PR31023 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
O15015 |  | 32 | 1-1/2" | O | 15015 | B4S2 | ET | 30 | 32-D-1501 | 32-D-1401A | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15016 |  | 32 | 1" | O | 15016 | B4S2 | ET | 30 | O15015 | 32-D-1401B | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15019 |  | 32 | 1" | O | 15019 | 1FS4 | ET | 30 | O15025 | O15020 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15020 |  | 32 | 2" | O | 15020 | 1FS4 | ET | 30 | O15019 | O15006 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15021 |  | 32 | 1/2" | O | 15021 | 1FS4 | ET | 30 | O15007 | O15022 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15022 |  | 32 | 2" | O | 15022 | 1FS4 | ET | 30 | O15021 | O15023 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15023 |  | 32 | 1/2" | O | 15023 | 1FS4 | ET | 30 | O15022 | 32-P-1501A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15023 |  | 32 | 3/4" | O | 15023 | 1FS4 | ET | 30 | O15022 | 32-P-1501A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O66011 |  | 32 | 3/4" | O | 66011 | B4S2 | HH | 30 | 32-P-6601 | O66024 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66011 |  | 32 | 3" | O | 66011 | B4S2 | HH | 30 | 32-P-6601 | O66024 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66012 |  | 32 | 3" | O | 66012 | 1CS2 | JP | 0 | O66011 | O66013 | 4.0 | 200.0 | 2.0 | 110.0 |  | 6.41 | 28.5 | IO | OIL | L | - | - | <1.5 | 110 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | A | N | 110 | N | 229 | 23,25
O66013 |  | 32 | 2" | O | 66013 | B4S2 | HH | 30 | O66012 | 32-D-6600 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66015 | 08 | 32 | 3/4" | O | 66015 | 1CS2 | N | 0 | 32-S-6601 | O66023 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66019 | 08 | 32 | 3/4" | O | 66019 | 1CS2 | N | 0 | 32-P-6600 | 32-S-6601 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66019 |  | 32 | 2" | O | 66019 | 1CS2 | ET | 30 | 32-P-6600 | 32-S-6601 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66020 |  | 32 | 1" | O | 66020 | 1CS2 | ET | 30 | O66019 | O66021 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66021 |  | 32 | 2" | O | 66021 | 1CS2 | ET | 30 | O66020 | O66022 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66022 |  | 32 | 1-1/2" | O | 66022 | 1CS2 | ET | 30 | O66021 | 32-P-6600 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66023 |  | 32 | 1" | O | 66023 | 1CS2 | ET | 30 | O66015 | O66003 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66027 |  | 32 | 3/4" | O | 66027 | B4S2 | ET | 30 | O66025 | 32-P-6601 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66027 |  | 32 | 2" | O | 66027 | B4S2 | ET | 30 | O66025 | 32-P-6601 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66036 |  | 32 | 1" | O | 66036 | 1CS2 | ET | 30 | O66015 | HCM32024 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66037 |  | 32 | 1/2" | O | 66037 | 1CS2 | ET | 30 | O66015 | O66038 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66037 |  | 32 | 1" | O | 66037 | 1CS2 | ET | 30 | O66015 | O66038 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66038 |  | 32 | 1" | O | 66038 | 1CS2 | ET | 30 | O66037 | O34001 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66039 |  | 32 | 1" | O | 66039 | 1CS2 | ET | 30 | O66015 | FO11003 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66039 |  | 32 | 1-1/2" | O | 66039 | 1CS2 | ET | 30 | O66015 | FO11003 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
LC13002 |  | 32 | 3/4" | LC | 13002 | B-5 | HB | 30 | LS13006 | LC13003 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13003 |  | 32 | 1/2" | LC | 13003 | B-5 | HB | 30 | LC13002 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13003 |  | 32 | 3/4" | LC | 13003 | B-5 | HB | 30 | LC13002 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13004 |  | 32 | 3/4" | LC | 13004 | B-5 | HB | 30 | LC13001 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13005 |  | 32 | 1/2" | LC | 13005 | B-5 | HB | 30 | LS13007 | LC13004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13005 |  | 32 | 3/4" | LC | 13005 | B-5 | HB | 30 | LS13007 | LC13004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13006 |  | 32 | 1/2" | LC | 13006 | B-5 | HB | 30 | LS13010 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13006 |  | 32 | 3/4" | LC | 13006 | B-5 | HB | 30 | LS13010 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14001 |  | 32 | 3/4" | LC | 14001 | B-5 | HB | 30 | LS63007 | LC14002 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14002 |  | 32 | 3/4" | LC | 14002 | B-5 | HB | 30 | LC14001 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14002 |  | 32 | 1-1/2" | LC | 14002 | B-5 | HB | 40 | LC14001 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14003 |  | 32 | 3/4" | LC | 14003 | B-5 | HB | 30 | LS63005 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14004 |  | 32 | 3/4" | LC | 14004 | B-5 | HB | 30 | LS14001 | LC14002 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14005 |  | 32 | 1/2" | LC | 14005 | B-5 | HB | 30 | LS14003 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14005 |  | 32 | 3/4" | LC | 14005 | B-5 | HB | 30 | LS14003 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23024 |  | 32 | 1/2" | LC | 23024 | B-5 | HB | 30 | LS23024 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23025 |  | 32 | 1/2" | LC | 23025 | B-5 | HB | 30 | LS23031 | LC23023 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS43010 |  | 32 | 1/2" | LS | 43010 | C6S1 | HB | 50 | LS63025 | 32-E-4303 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | E | N | 141 | N | 1092
LS43010 |  | 32 | 3/4" | LS | 43010 | C6S1 | HB | 50 | LS63025 | 32-E-4303 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | E | N | 141 | N | 1092
LS43011 |  | 32 | 1/2" | LS | 43011 | C6S1 | HB | 50 | 32-E-4303 | LC43001 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.33 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | E | N | 141 | N | 1092
LS50001 |  | 32 | 1/2" | LS | 50001 | 3CS6 | HB | 50 | LS50002 | LS50006 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50001 |  | 32 | 2" | LS | 50001 | 3CS6 | HB | 50 | LS50002 | LS50006 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50001 |  | 32 | 6" | LS | 50001 | 3CS6 | HB | 70 | LS50002 | LS50006 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50002 |  | 32 | 1/2" | LS | 50002 | 3CS6 | HB | 50 | LS50049 | LS50001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50002 |  | 32 | 3/4" | LS | 50002 | 3CS6 | HB | 50 | LS50049 | LS50001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50002 |  | 32 | 4" | LS | 50002 | 3CS6 | HB | 70 | LS50049 | LS50001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50002 |  | 32 | 6" | LS | 50002 | 3CS6 | HB | 70 | LS50049 | LS50001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50002 |  | 32 | 8" | LS | 50002 | 3CS6 | HB | 70 | LS50049 | LS50001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50003 |  | 32 | 1/2" | LS | 50003 | 3CS6 | HB | 50 | LS50002 | LS50004 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50003 |  | 32 | 3/4" | LS | 50003 | 3CS6 | HB | 50 | LS50002 | LS50004 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50003 |  | 32 | 2" | LS | 50003 | 3CS6 | HB | 50 | LS50002 | LS50004 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50003 |  | 32 | 4" | LS | 50003 | 3CS6 | HB | 70 | LS50002 | LS50004 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50004 |  | 32 | 1-1/2" | LS | 50004 | 3CS6 | HB | 30 | LS50003 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS60014 |  | 32 | 1" | LS | 60014 | B-5 | HB | 70 | PURGE CONNECTION | BDL60044 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78A | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
PR72002 | 08 | 32 | 3/4" | PR | 72002 | C42S1 | N | 0 | 32-S-7201A | 32-D-3300 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72002 | 08 | 32 | 6" | PR | 72002 | C42S1 | N | 0 | 32-S-7201A | 32-D-3300 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72003 | 08 | 32 | 1" | PR | 72003 | C42S1 | HB | 30 | PR72019 | PR72011 | 43.7/43.7 | -45.0/120.0 | 30.0 | 65.0 |  | 65.55 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 65 | sh.51 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-007-04 |  | G | N | 141 | N | 356 | 10
PR72014 | 08 | 32 | 6" | PR | 72014 | C42S1 | N | 0 | 32-T-7201 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72015 | 08 | 32 | 1" | PR | 72015 | C42S1 | N | 0 | 32-E-7203 | 32-T-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72015 | 08 | 32 | 6" | PR | 72015 | C42S1 | N | 0 | 32-E-7203 | 32-T-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72016 | 08 | 32 | 3/4" | PR | 72016 | C42S1 | N | 0 | 32-E-7202 | 32-E-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
LC23029 |  | 32 | 1/2" | LC | 23029 | B-5 | HB | 30 | LS23028 | LC23047 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23030 |  | 32 | 1/2" | LC | 23030 | B-5 | HB | 30 | LS23025 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23031 | 08 | 32 | 1/2" | LC | 23031 | B-5 | HB | 30 | LS23027 | LC31021 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23032 |  | 32 | 3/4" | LC | 23032 | B-5 | HB | 30 | LS23018 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.18 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23034 |  | 32 | 1/2" | LC | 23034 | B-5 | HB | 30 | LS23024 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23035 |  | 32 | 1/2" | LC | 23035 | B-5 | HB | 30 | LS23026 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23036 |  | 32 | 1/2" | LC | 23036 | B-5 | HB | 30 | LS23023 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23038 |  | 32 | 1/2" | LC | 23038 | B-5 | HB | 30 | LS23031 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23042 |  | 32 | 1/2" | LC | 23042 | B-5 | HB | 30 | LS23030 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23044 |  | 32 | 1/2" | LC | 23044 | B-5 | HB | 30 | LS23025 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31004 |  | 32 | 3/4" | LC | 31004 | B-5 | HB | 30 | LS31026 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31007 |  | 32 | 3/4" | LC | 31007 | B-5 | HB | 30 | LS31023 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31010 |  | 32 | 1/2" | LC | 31010 | B-5 | HB | 30 | LS31017 | LC31011 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31010 |  | 32 | 3/4" | LC | 31010 | B-5 | HB | 30 | LS31017 | LC31011 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31011 |  | 32 | 3/4" | LC | 31011 | B-5 | P | 50 | LC31010 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31013 |  | 32 | 3/4" | LC | 31013 | B-5 | HB | 30 | LS31025 | LC31015 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31014 |  | 32 | 1/2" | LC | 31014 | B-5 | HB | 30 | LS31030 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31014 |  | 32 | 3/4" | LC | 31014 | B-5 | HB | 30 | LS31030 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31015 |  | 32 | 1" | LC | 31015 | B-5 | HB | 40 | LS31026 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31015 |  | 32 | 1-1/2" | LC | 31015 | B-5 | HB | 40 | LS31026 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31016 |  | 32 | 1" | LC | 31016 | B-5 | P | 50 | LS31021 | LC31036 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31017 |  | 32 | 3/4" | LC | 31017 | B-5 | HB | 30 | LC23026 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31017 |  | 32 | 1" | LC | 31017 | B-5 | HB | 40 | LC23026 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31018 | 08 | 32 | 3/4" | LC | 31018 | B-5 | HB | 30 | LS31023 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31018 | 08 | 32 | 1" | LC | 31018 | B-5 | HB | 40 | LS31023 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31019 |  | 32 | 1" | LC | 31019 | B-5 | HB | 40 | LS31024 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31020 |  | 32 | 1/2" | LC | 31020 | B-5 | HB | 30 | LS31028 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31021 |  | 32 | 1/2" | LC | 31021 | B-5 | HB | 30 | LS31028 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS63005 |  | 32 | 1/2" | LS | 63005 | B-5 | HB | 60 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63005 |  | 32 | 1-1/2" | LS | 63005 | B-5 | HB | 70 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63006 |  | 32 | 1" | LS | 63006 | B-5 | HB | 70 | LS63178 | JLS14001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63007 |  | 32 | 1/2" | LS | 63007 | B-5 | HB | 60 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63007 |  | 32 | 1" | LS | 63007 | B-5 | HB | 70 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63007 |  | 32 | 1-1/2" | LS | 63007 | B-5 | HB | 70 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63008 |  | 32 | 1-1/2" | LS | 63008 | B-5 | HB | 70 | LS01001 | LS63013 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63009 |  | 32 | 3/4" | LS | 63009 | B-5 | HB | 60 | LS01001 | CAP | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300A |  | 32 | 3/4" | LS | 6300A | B-5 | HB | 60 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300D |  | 32 | 1" | LS | 6300D | B-5 | HB | 70 | LS6300A | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300E |  | 32 | 1" | LS | 6300E | B-5 | HB | 70 | LS6300A | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300F |  | 32 | 1" | LS | 6300F | B-5 | HB | 70 | LS63206 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300I |  | 32 | 1/2" | LS | 6300I | B-5 | HB | 60 | LS63199 | 32-S-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300J |  | 32 | 1/2" | LS | 6300J | B-5 | HB | 60 | LS63193 | 32-S-2300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300K |  | 32 | 3/4" | LS | 6300K | B-5 | HB | 60 | LS01001 | LS63065 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300K |  | 32 | 1" | LS | 6300K | B-5 | HB | 70 | LS01001 | LS63065 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300K |  | 32 | 1-1/2" | LS | 6300K | B-5 | HB | 70 | LS01001 | LS63065 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300O |  | 32 | 1" | LS | 6300O | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63035 |  | 32 | 3/4" | LS | 63035 | B-5 | HB | 60 | LS01001 | 32-D-3200 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63038 |  | 32 | 1" | LS | 63038 | B-5 | HB | 70 | LS63189 | JLS24001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63039 |  | 32 | 1/2" | LS | 63039 | B-5 | HB | 60 | LS63199 | 32-D-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63039 |  | 32 | 1" | LS | 63039 | B-5 | HB | 70 | LS63199 | 32-D-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63039 |  | 32 | 2" | LS | 63039 | B-5 | HB | 80 | LS63199 | 32-D-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63040 |  | 32 | 1/2" | LS | 63040 | B-5 | HB | 60 | LS63193 | LS63043 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63041 | 08 | 32 | 1" | LS | 63041 | B-5 | HB | 70 | LS63193 | LS31027 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
O11001 | 08 | 32 | 3/4" | O | 11001 | 1CS2 | N | 0 | FO11003 | FO15B05 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O11001 | 08 | 32 | 1" | O | 11001 | 1CS2 | N | 0 | FO11003 | FO15B05 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O12005 | 7A | 32 | 1" | O | 12005 | 1CS2 | P | 50 | O13011 | 32-D-1200C | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-022-01 |  | M | N | 110 | N | 235 | 23,25
O13002 |  | 32 | 1" | O | 13002 | 1CS2 | JP | 0 | O13025 | O13026 | 6.0 | 200.0 | 5.0 | 100.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 100 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | A | N | 010 | N | 231 | 23,25
O13003 | 08 | 32 | 1-1/2" | O | 13003 | 1CS2 | N | 0 | O13027 | O13021 | 6.0 | 200.0 | 5.0 | 100.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 100 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-025-01 |  | A | N | 010 | N | 231 | 23,25
O13005 |  | 32 | 1" | O | 13005 | 1CS2 | ST | 30 | O13009 | 32-D-1400A | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.7 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13007 | 7A | 32 | 1" | O | 13007 | 1CS2 | P | 50 | 32-S-1301 | 32-D-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13009 | 7A | 32 | 1" | O | 13009 | 1CS2 | P | 50 | O13020 | O13005 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O14009 |  | 32 | 1/2" | O | 14009 | 1FS4 | ET | 30 | 32-D-1401A | O14001 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O14010 |  | 32 | 1/2" | O | 14010 | 1CS2 | ET | 30 | O15003 | 32-Z-1400A | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-01 |  | M | N | 110 | N | 236 | 23,25
O14011 |  | 32 | 1/2" | O | 14011 | 1CS2 | ET | 30 | O15004 | 32-Z-1400B | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-02 |  | M | N | 110 | N | 236 | 23,25
O15002 |  | 32 | 1/2" | O | 15002 | 1FS4 | ET | 30 | O15007 | 32-HX-1431 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15004 |  | 32 | 1/2" | O | 15004 | 1FS4 | ET | 30 | O15007 | O15003 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15005 |  | 32 | 1" | O | 15005 | 1CS2 | ET | 30 | 32-S-1501 | SP 1505 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 236 | 23,25
O15006 |  | 32 | 1/2" | O | 15006 | 1FS4 | ET | 30 | O15020 | 32-P-1501B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15006 |  | 32 | 1" | O | 15006 | 1FS4 | ET | 30 | O15020 | 32-P-1501B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15007 |  | 32 | 1/2" | O | 15007 | 1FS4 | ET | 30 | 32-P-1501A | O15009 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15008 |  | 32 | 1/2" | O | 15008 | 1FS4 | ET | 30 | O15007 | O15009 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15009 |  | 32 | 1/2" | O | 15009 | 1FS4 | ET | 30 | O15008 | TP-11 (Z-2101) | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15010 |  | 32 | 1" | O | 15010 | B4S2 | ET | 30 | O13014 | 32-D-1501 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15011 |  | 32 | 1/2" | O | 15011 | 1CS2 | ET | 30 | O15013 | N15002 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 110 | N | 236 | 23,25
O15011 |  | 32 | 3" | O | 15011 | 1CS2 | ET | 30 | O15013 | N15002 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 110 | N | 236 | 23,25
O15012 |  | 32 | 1-1/2" | O | 15012 | B4S2 | ET | 30 | 32-D-1501 | 32-S-1500 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15013 |  | 32 | 3/4" | O | 15013 | 1CS2 | ET | 30 | 32-S-1500 | O15001 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 236 | 23,25
O15014 |  | 32 | 1-1/2" | O | 15014 | B4S2 | ET | 30 | 32-D-1501 | VZ15006 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15015 |  | 32 | 1" | O | 15015 | B4S2 | ET | 30 | 32-D-1501 | 32-D-1401A | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
PR40026 |  | 32 | 2" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR43031 | 08 | 32 | 1-1/2" | PR | 43031 | C42S1 | N | 0 | 32-P-4300 | PR43032 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43034 | 08 | 32 | 1" | PR | 43034 | C42S1 | N | 0 | PR43024 | BU73047 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 141 | N | 350 | ,15
PR43035 | 08 | 32 | 1" | PR | 43035 | C42S1 | N | 0 | PR43033 | PR43024 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43036 |  | 32 | 1/2" | PR | 43036 | C42S1 | HB | 30 | 32-P-4300 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43036 |  | 32 | 1" | PR | 43036 | C42S1 | HB | 30 | 32-P-4300 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43037 | 08 | 32 | 1" | PR | 43037 | C42S1 | N | 0 | PR43039 | 32-P-4300 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 350 | ,15
PR43037 | 08 | 32 | 3" | PR | 43037 | C42S1 | N | 0 | PR43039 | 32-P-4300 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 350 | ,15
PR43038 |  | 32 | 2" | PR | 43038 | C42S1 | HB | 30 | PR43039 | 32AT 2401-4 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43038 |  | 32 | 4" | PR | 43038 | C42S1 | HB | 30 | PR43039 | 32AT 2401-4 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43039 |  | 32 | 2" | PR | 43039 | C42S1 | HB | 30 | 32-T-4300 | PR43038 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43040 |  | 32 | 4" | PR | 43040 | C42S1 | HB | 30 | 32-E-4303 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43042 |  | 32 | 3/4" | PR | 43042 | C42S1 | HB | 30 | 32-E-4302 | PR43043 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43042 |  | 32 | 1-1/2" | PR | 43042 | C42S1 | HB | 30 | 32-E-4302 | PR43043 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43042 |  | 32 | 3" | PR | 43042 | C42S1 | HB | 30 | 32-E-4302 | PR43043 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43043 | 08 | 32 | 2" | PR | 43043 | C42S1 | N | 0 | PR43042 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43044 | 08 | 32 | 1-1/2" | PR | 43044 | C42S1 | N | 0 | 32-T-4300 | 32-E-4302 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43044 | 08 | 32 | 4" | PR | 43044 | C42S1 | N | 0 | 32-T-4300 | 32-E-4302 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43045 |  | 32 | 4" | PR | 43045 | C42S1 | ST | 30 | 32-E-4302 | PR43028 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43046 | 08 | 32 | 1-1/2" | PR | 43046 | D20S1 | N | 0 | PR43042 | PR24007 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
LC32001 |  | 32 | 1" | LC | 32001 | B-5 | HB | 40 | LS32001 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC32002 |  | 32 | 1/2" | LC | 32002 | B-5 | HB | 30 | LS32002 | LC32001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC32003 |  | 32 | 3/4" | LC | 32003 | B-5 | HB | 30 | LS32003 | LC63091 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC32004 |  | 32 | 3/4" | LC | 32004 | B-5 | HB | 30 | LS32001 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC32005 |  | 32 | 1/2" | LC | 32005 | B-5 | HB | 30 | LS32002 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC32006 |  | 32 | 1/2" | LC | 32006 | B-5 | HB | 30 | LS32003 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC33001 |  | 32 | 3/4" | LC | 33001 | B-5 | HB | 30 | LS33002 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.25 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC33001 |  | 32 | 1" | LC | 33001 | B-5 | HB | 40 | LS33002 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.25 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC33002 |  | 32 | 3/4" | LC | 33002 | B-5 | HA | 30 | LS33002 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.25 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC33003 |  | 32 | 3/4" | LC | 33003 | B-5 | HB | 30 | LS33003 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.25 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34002 |  | 32 | 1/2" | LC | 34002 | B-5 | HB | 30 | LS34004 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC34004 | 08 | 32 | 3/4" | LC | 34004 | B-5 | HB | 30 | LS34004 | LC24015 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34005 |  | 32 | 3/4" | LC | 34005 | B-5 | HB | 30 | LS34005 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34006 |  | 32 | 1/2" | LC | 34006 | B-5 | HB | 30 | LS34006 | LC630AC | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34006 |  | 32 | 3/4" | LC | 34006 | B-5 | HB | 30 | LS34006 | LC630AC | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC43001 |  | 32 | 1" | LC | 43001 | B-5 | HB | 40 | LS43011 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.33 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS63047 |  | 32 | 1/2" | LS | 63047 | B-5 | HB | 60 | LS63206 | BDH60006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63047 |  | 32 | 3/4" | LS | 63047 | B-5 | HB | 60 | LS63206 | BDH60006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63047 |  | 32 | 1-1/2" | LS | 63047 | B-5 | HB | 70 | LS63206 | BDH60006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63048 |  | 32 | 3" | LS | 63048 | B-5 | HB | 80 | LS63177 | LS33001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63049 |  | 32 | 2" | LS | 63049 | B-5 | HB | 80 | LS01001 | LS61002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63052 |  | 32 | 1" | LS | 63052 | B-5 | HB | 70 | LS63199 | LS50048 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63052 |  | 32 | 1-1/2" | LS | 63052 | B-5 | HB | 70 | LS63199 | LS50048 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63054 |  | 32 | 3/4" | LS | 63054 | B-5 | HB | 60 | LS63178 | 32-S-1300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63055 |  | 32 | 3/4" | LS | 63055 | B-5 | HB | 60 | LS63206 | 32-D-5104 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63056 |  | 32 | 3/4" | LS | 63056 | B-5 | HB | 60 | LS63206 | 32-D-5101 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63057 |  | 32 | 3/4" | LS | 63057 | B-5 | HB | 60 | LS63206 | 32-D-5102 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63058 |  | 32 | 3/4" | LS | 63058 | B-5 | HB | 60 | LS63206 | 32-D-5100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63059 |  | 32 | 3/4" | LS | 63059 | B-5 | HB | 60 | LS63183 | LS71010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63059 |  | 32 | 3" | LS | 63059 | B-5 | HB | 80 | LS63183 | LS71010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63064 |  | 32 | 1" | LS | 63064 | B-5 | HB | 70 | LS63206 | 32-D-6500 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63065 |  | 32 | 1" | LS | 63065 | B-5 | HB | 70 | LS6300K | JLS20001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63067 |  | 32 | 1/2" | LS | 63067 | B-5 | HB | 60 | LS63199 | 32-E-2301 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63067 |  | 32 | 4" | LS | 63067 | B-5 | HB | 90 | LS63199 | 32-E-2301 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
O15023 |  | 32 | 1" | O | 15023 | 1FS4 | ET | 30 | O15022 | 32-P-1501A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15025 |  | 32 | 3/4" | O | 15025 | 1FS4 | ET | 30 | 32-P-1501B | O15019 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O20001 |  | 32 | 1/2" | O | 20001 | 1FS4 | ET | 30 | O15008 | 32-Z-2001B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O20002 |  | 32 | 1/2" | O | 20002 | 1FS4 | ET | 30 | O15008 | 32-Z-2005 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-042-01 |  | M | N | 110 | N | 245 | 23,25
O20003 | 08 | 32 | 3/4" | O | 20003 | 1FS4 | N | 0 | 32-Z-2005 | 32-R-2000 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O20004 |  | 32 | 1/2" | O | 20004 | 1FS4 | ET | 30 | O15008 | TEA20004 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O20005 |  | 32 | 1/2" | O | 20005 | 1FS4 | ET | 30 | O15008 | 32-Z-2001A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O20006 |  | 32 | 1/2" | O | 20006 | 1FS4 | ET | 30 | O20005 | 32-HV-2001 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O20007 |  | 32 | 1/4" | O | 20007 | 1FS4 | ET | 30 | O20001 | 32-Z-2002B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O20009 | 08 | 32 | 1/2" | O | 20009 | 1FS4 | N | 0 | 32-Z-2001B | BDL20001 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O21007 |  | 32 | 1/2" | O | 21007 | 1FS4 | ET | 30 | O15009 | TP-8 (Z-2012, FO-2106) | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O31007 |  | 32 | 1/2" | O | 31007 | 1CS2 | ET | 30 | O66037 | O31015 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O31010 | 08 | 32 | 1" | O | 31010 | B4S2 | N | 0 | O31016 | FO35015 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 225 | 23,25
O31011 | 08 | 32 | 1-1/2" | O | 31011 | B4S2 | N | 0 | O31012 | O31010 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
O31016 | 08 | 32 | 1" | O | 31016 | B4S2 | N | 0 | O31014 | O31010 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
O65003 | 08 | 32 | 1/2" | O | 65003 | B4S2 | N | 0 | O65011 | SP 6501 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-01 |  | E | N | 110 | N | 221
O65010 |  | 32 | 1-1/2" | O | 65010 | B4S2 | ET | 30 | 32-D-6500 | O65002 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 225 | 23,25
O65011 | 08 | 32 | 1/2" | O | 65011 | B4S2 | N | 0 | 32-D-6500 | O65003 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-01 |  | E | N | 110 | N | 225 | 23,25
O66001 |  | 32 | 1-1/2" | O | 66001 | B4S2 | ET | 30 | 32-D-6600 | O66022 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66010 |  | 32 | 2" | O | 66010 | B4S2 | ET | 30 | 32-D-6600 | O66027 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66040 |  | 32 | 1" | O | 66040 | 1CS2 | ET | 30 | O66015 | O13014 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O67010 |  | 32 | 1" | O | 67010 | 1CS2 | ET | 30 | O66015 | PX86022 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O67011 |  | 32 | 1" | O | 67011 | 1CS2 | ET | 30 | O66015 | O67012 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O67012 |  | 32 | 1" | O | 67012 | 1CS2 | ET | 30 | O67011 | PR36017 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
OG01004 | 7A | 32 | 1/2" | OG | 01004 | 1FS4 | P | 50 | OG00A01 | PPG80001 | 42.0/42.0 | -40.0/200.0 | 3.0/3.0 | 60.0/10.0 |  | 67.34 | 148.95 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-U-034-01 |  | G | N | 141 | N | 503 | 10
OG01004 | 7A | 32 | 1" | OG | 01004 | 1FS4 | P | 50 | OG00A01 | PPG80001 | 42.0/42.0 | -40.0/200.0 | 3.0/3.0 | 60.0/10.0 |  | 67.34 | 148.95 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-U-034-01 |  | G | N | 141 | N | 503 | 10
OG01004 | 7A | 32 | 3" | OG | 01004 | 1FS4 | P | 50 | OG00A01 | PPG80001 | 42.0/42.0 | -40.0/200.0 | 3.0/3.0 | 60.0/10.0 |  | 67.34 | 148.95 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.1 | 1 | II | MOD.A2 | Y | 5 | Y | 32-U-034-01 |  | G | N | 141 | N | 503 | 10
IA89010 | 08 | 32 | 1" | IA | 89010 | B-13 | N | 0 | IA89037 | SA81018 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89012 | 08 | 32 | 1/2" | IA | 89012 | B-13 | N | 0 | IA62006 | TP-N51710 (PCV-8968) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89014 | 08 | 32 | 1/2" | IA | 89014 | B-13 | N | 0 | IA62006 | TP-N50905 (E-8900A) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89015 | 08 | 32 | 1" | IA | 89015 | B-13 | N | 0 | IA89037 | SA81019 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89036 | 08 | 32 | 1/2" | IA | 89036 | B-13 | N | 0 | IA62006 | Z-8901, PCV-8910 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89037 | 08 | 32 | 1-1/2" | IA | 89037 | B-13 | N | 0 | IA62006 | IA620A0 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
LC13001 |  | 32 | 3/4" | LC | 13001 | B-5 | HB | 30 | LS13004 | LC13004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC13002 |  | 32 | 1/2" | LC | 13002 | B-5 | HB | 30 | LS13006 | LC13003 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC16001 |  | 32 | 3/4" | LC | 16001 | B-5 | HB | 30 | LS16001 | LC13003 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.10 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC20001 | 08 | 32 | 1/2" | LC | 20001 | B-5 | HB | 30 | LC43003 | LS20001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC20001 | 08 | 32 | 3/4" | LC | 20001 | B-5 | HB | 30 | LC43003 | LS20001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC21001 |  | 32 | 1" | LC | 21001 | B-5 | HB | 40 | LS21001 | WW21001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23017 |  | 32 | 1-1/2" | LC | 23017 | B-5 | HB | 40 | LS23018 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.18 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23018 |  | 32 | 1/2" | LC | 23018 | B-5 | HB | 30 | LS23014 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.17 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23019 |  | 32 | 1/2" | LC | 23019 | B-5 | HB | 30 | LC23020 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23020 |  | 32 | 3/4" | LC | 23020 | B-5 | HB | 30 | LS23021 | LC23019 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23021 |  | 32 | 3/4" | LC | 23021 | B-5 | HB | 30 | LS23022 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23021 |  | 32 | 1" | LC | 23021 | B-5 | HB | 40 | LS23022 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23022 |  | 32 | 1/2" | LC | 23022 | B-5 | HB | 30 | LS23023 | LC23023 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23023 |  | 32 | 1/2" | LC | 23023 | B-5 | HB | 30 | LC23022 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS50004 |  | 32 | 8" | LS | 50004 | 3CS6 | HB | 40 | LS50003 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50006 |  | 32 | 1" | LS | 50006 | 3CS6 | HB | 30 | LS50001 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50008 |  | 32 | 1" | LS | 50008 | 3CS6 | HB | 50 | LS50002 | 32-J-5001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50009 |  | 32 | 1/2" | LS | 50009 | 3CS6 | HB | 30 | LS63002 | 32-T-5001 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-02 |  | M | N | 000 | N | 91
LS50009 |  | 32 | 2" | LS | 50009 | 3CS6 | HB | 40 | LS63002 | 32-T-5001 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-02 |  | M | N | 000 | N | 91
LS50009 |  | 32 | 4" | LS | 50009 | 3CS6 | HB | 50 | LS63002 | 32-T-5001 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-02 |  | M | N | 000 | N | 91
LS50032 |  | 32 | 1" | LS | 50032 | B-5 | HB | 30 | LS50033 | JLS50005 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS50033 |  | 32 | 1" | LS | 50033 | B-5 | HB | 30 | LS50048 | LS50031 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS50034 |  | 32 | 1/2" | LS | 50034 | B-5 | HB | 30 | LS50033 | 32-D-5011 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50035 |  | 32 | 3/4" | LS | 50035 | B-5 | HB | 30 | JLS50006 | LS50034 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50036 |  | 32 | 1" | LS | 50036 | B-5 | HB | 30 | LS50033 | 32-D-5200 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS50038 |  | 32 | 1/2" | LS | 50038 | B-5 | HB | 60 | 32-S-5001 | LC50009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50038 |  | 32 | 2" | LS | 50038 | B-5 | HB | 80 | 32-S-5001 | LC50009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50045 |  | 32 | 3/4" | LS | 50045 | B-5 | HB | 30 | 32-D-5001 | LC50004 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50045 |  | 32 | 1-1/2" | LS | 50045 | B-5 | HB | 30 | 32-D-5001 | LC50004 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50046 |  | 32 | 1/2" | LS | 50046 | B-5 | HB | 30 | P50017 | LC50003 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50047 |  | 32 | 1-1/2" | LS | 50047 | B-5 | HB | 30 | JLS50005 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50048 |  | 32 | 1-1/2" | LS | 50048 | B-5 | HB | 30 | LS63052 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS50048 |  | 32 | 4" | LS | 50048 | B-5 | HB | 40 | LS63052 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
PR72005 |  | 32 | 1/2" | PR | 72005 | C42S1 | ST | 30 | PR72028 | 32-D-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72005 |  | 32 | 1" | PR | 72005 | C42S1 | ST | 30 | PR72028 | 32-D-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72006 | 08 | 32 | 1" | PR | 72006 | C42S1 | N | 0 | 32-D-7201 | PW72007 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72009 | 08 | 32 | 1/2" | PR | 72009 | C42S1 | N | 0 | 32-D-7200 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72009 | 08 | 32 | 2" | PR | 72009 | C42S1 | N | 0 | 32-D-7200 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72009 | 08 | 32 | 8" | PR | 72009 | C42S1 | N | 0 | 32-D-7200 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72011 | 08 | 32 | 6" | PR | 72011 | C42S1 | N | 0 | 32-E-7202 | 32-T-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72012 |  | 32 | 12" | PR | 72012 | C42S1 | HA | 30 | 32-E-7201 | 32-T-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 20 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72013 |  | 32 | 8" | PR | 72013 | C42S1 | HA | 30 | 32-E-7201 | 32-T-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 20 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
LC23045 | 08 | 32 | 1/2" | LC | 23045 | B-5 | HB | 30 | LS23027 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.106 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23046 |  | 32 | 1/2" | LC | 23046 | B-5 | HB | 30 | LS23033 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23047 |  | 32 | 1/2" | LC | 23047 | B-5 | HB | 30 | LS23033 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23050 |  | 32 | 1/2" | LC | 23050 | B-5 | HB | 30 | LS23048 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23052 | 08 | 32 | 3/4" | LC | 23052 | B-5 | HB | 30 | LS23036 | LC23023 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23056 | 08 | 32 | 1" | LC | 23056 | B-5 | HB | 40 | LS23038 | LC31038 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23059 |  | 32 | 1" | LC | 23059 | B-5 | HB | 40 | LS23040 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23061 |  | 32 | 1" | LC | 23061 | B-5 | P | 50 | LS630AM | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23062 |  | 32 | 1/2" | LC | 23062 | B-5 | P | 50 | LS23049 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24010 |  | 32 | 3/4" | LC | 24010 | B-5 | HB | 30 | LS24010 | LC63093 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24010 |  | 32 | 1" | LC | 24010 | B-5 | HB | 40 | LS24010 | LC63093 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24011 |  | 32 | 1-1/2" | LC | 24011 | B-5 | HB | 40 | LS24014 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24013 | 08 | 32 | 1" | LC | 24013 | B-5 | HB | 40 | LS24016 | LC24010 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24015 |  | 32 | 3/4" | LC | 24015 | B-5 | HB | 30 | LS63073 | LC34004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24018 | 08 | 32 | 3/4" | LC | 24018 | B-5 | HB | 30 | LC24015 | LS24011 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31001 |  | 32 | 1/2" | LC | 31001 | B-5 | HB | 30 | LS31017 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31002 |  | 32 | 1/2" | LC | 31002 | B-5 | HB | 30 | LS31018 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31021 |  | 32 | 3/4" | LC | 31021 | B-5 | HB | 30 | LS31028 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31029 |  | 32 | 1/2" | LC | 31029 | B-5 | HB | 30 | LS31031 | LC34006 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31032 |  | 32 | 1/2" | LC | 31032 | B-5 | HB | 30 | LS31034 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31033 | 08 | 32 | 1" | LC | 31033 | B-5 | HB | 40 | LS31038 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31034 | 08 | 32 | 1" | LC | 31034 | B-5 | HB | 40 | LS31039 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS60015 |  | 32 | 1" | LS | 60015 | B-5 | HB | 70 | PURGE CONNECTION | BDL60045 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60019 |  | 32 | 1" | LS | 60019 | B-5 | HB | 70 | PURGE CONNECTION | BDL60049 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60021 |  | 32 | 1" | LS | 60021 | B-5 | HB | 70 | PURGE CONNECTION | BDL60051 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60022 |  | 32 | 1" | LS | 60022 | B-5 | HB | 70 | PURGE CONNECTION | BDL60052 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60025 |  | 32 | 1" | LS | 60025 | B-5 | HB | 70 | Hose connection | BDL60055 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60030 |  | 32 | 1" | LS | 60030 | B-5 | HB | 70 | HOSE CONNECTION | BDL60060 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS61001 |  | 32 | 3/4" | LS | 61001 | B-5 | HB | 60 | JLS61001 | LC61001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS61002 |  | 32 | 3/4" | LS | 61002 | B-5 | HB | 60 | LS63049 | LC61003 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63001 |  | 32 | 3/4" | LS | 63001 | B-5 | HB | 60 | LS01001 | LS50049 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63001 |  | 32 | 8" | LS | 63001 | B-5 | HB | 100 | LS01001 | LS50049 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63002 |  | 32 | 4" | LS | 63002 | B-5 | HB | 90 | LS01001 | LS630AE | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63004 |  | 32 | 1" | LS | 63004 | B-5 | HB | 70 | LS63178 | LS13008 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300P |  | 32 | 1" | LS | 6300P | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300R |  | 32 | 1" | LS | 6300R | B-5 | HB | 70 | LS6300L | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300T |  | 32 | 1" | LS | 6300T | B-5 | HB | 70 | HOSE CONNECTION | LS01001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300Y |  | 32 | 1-1/2" | LS | 6300Y | B-5 | HB | 70 | LS63178 | 32-1122-S-007 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300Z |  | 32 | 2" | LS | 6300Z | B-5 | HB | 80 | LS63206 | 32-1127-S-008 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63010 |  | 32 | 1" | LS | 63010 | B-5 | HB | 70 | LS63178 | JLS16001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63013 |  | 32 | 1" | LS | 63013 | B-5 | HB | 70 | LS63008 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63014 |  | 32 | 3/4" | LS | 63014 | B-5 | HB | 60 | LS63013 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63016 |  | 32 | 1" | LS | 63016 | B-5 | HB | 70 | LS63013 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63025 |  | 32 | 3/4" | LS | 63025 | B-5 | HB | 60 | LS01001 | LS43010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01,32-P-047-03 |  | E | N | 000 | N | 90
LS63025 |  | 32 | 3" | LS | 63025 | B-5 | HB | 80 | LS01001 | LS43010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01,32-P-047-03 |  | E | N | 000 | N | 90
LS63027 |  | 32 | 3/4" | LS | 63027 | B-5 | HB | 60 | LS63199 | 32-E-5200 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63027 |  | 32 | 4" | LS | 63027 | B-5 | HB | 90 | LS63199 | 32-E-5200 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63030 |  | 32 | 3/4" | LS | 63030 | B-5 | HB | 60 | LS63014 | 32-E-3400 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63031 |  | 32 | 1" | LS | 63031 | B-5 | HB | 70 | LS63199 | 32-D-3400 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63031 |  | 32 | 1-1/2" | LS | 63031 | B-5 | HB | 70 | LS63199 | 32-D-3400 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63032 |  | 32 | 1/2" | LS | 63032 | B-5 | HB | 60 | LS63199 | PR31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63034 |  | 32 | 1/2" | LS | 63034 | B-5 | HB | 60 | LS63133 | 32-E-3200 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
O13011 | 7A | 32 | 1-1/2" | O | 13011 | 1CS2 | P | 50 | O13020 | 32-D-1200B | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13012 | 7A | 32 | 1" | O | 13012 | 1CS2 | P | 50 | O13020 | CT14010 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13014 |  | 32 | 1" | O | 13014 | 1CS2 | ET | 30 | O66040 | O14003 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O13016 |  | 32 | 3/4" | O | 13016 | 1CS2 | ET | 30 | 32-P-1301 | 32-S-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13017 |  | 32 | 1" | O | 13017 | 1CS2 | ET | 30 | O13016 | O13038 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13019 |  | 32 | 1" | O | 13019 | 1CS2 | ET | 30 | O66040 | 32-D-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13020 | 7A | 32 | 1/2" | O | 13020 | 1CS2 | P | 50 | O13007 | O13009 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13020 | 7A | 32 | 1" | O | 13020 | 1CS2 | P | 50 | O13007 | O13009 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13021 |  | 32 | 3/4" | O | 13021 | 1CS2 | ST | 30 | JLS13001 | 32-P-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13022 |  | 32 | 1" | O | 13022 | 1CS2 | ST | 30 | 32-P-1300 | 32-S-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13023 |  | 32 | 1" | O | 13023 | 1CS2 | ST | 30 | O13022 | O13024 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13024 |  | 32 | 1-1/2" | O | 13024 | 1CS2 | ST | 30 | O13023 | O13021 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13026 |  | 32 | 1" | O | 13026 | 1CS2 | ST | 30 | O13002 | 32-D-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13026 |  | 32 | 4" | O | 13026 | 1CS2 | ST | 30 | O13002 | 32-D-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13036 |  | 32 | 1/2" | O | 13036 | B4S2 | ET | 30 | VZ13005 | O13037 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O13037 |  | 32 | 1" | O | 13037 | B4S2 | ET | 30 | OIL DRUM | 32-P-1301 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O13038 |  | 32 | 1-1/2" | O | 13038 | B4S2 | ET | 30 | O13017 | O13037 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O13039 |  | 32 | 1" | O | 13039 | 1CS2 | ET | 30 | O66040 | 32-D-1602 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O14001 |  | 32 | 1" | O | 14001 | B4S2 | ET | 30 | O14009 | O14003 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O14002 |  | 32 | 1/2" | O | 14002 | 1FS4 | ET | 30 | 32-HX-1431 | O14003 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
PR40026 |  | 32 | 3" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR40026 |  | 32 | 4" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR40026 |  | 32 | 6" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR40027 |  | 32 | 1/2" | PR | 40027 | C42S1 | ST | 30 | PR40028 | PR40023 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR40027 |  | 32 | 4" | PR | 40027 | C42S1 | ST | 30 | PR40028 | PR40023 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR40028 |  | 32 | 3/4" | PR | 40028 | C42S1 | HB | 30 | PR40029 | PR40027 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR40028 |  | 32 | 1-1/2" | PR | 40028 | C42S1 | HB | 30 | PR40029 | PR40027 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR40029 |  | 32 | 3/4" | PR | 40029 | C42S1 | ET | 30 | ET40005 | PR40020 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 338 | 10
PR40032 |  | 32 | 1-1/2" | PR | 40032 | C42S1 | HB | 30 | PR40029 | BDL40025 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 338 | 10
PR40033 |  | 32 | 6" | PR | 40033 | C42S1 | HB | 30 | PR40026 | BDL40036 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR43024 | 08 | 32 | 1-1/2" | PR | 43024 | C42S1 | N | 0 | PR43035 | HCM43001 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43025 | 08 | 32 | 1-1/2" | PR | 43025 | C42S1 | N | 0 | PR43030 | P31012 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43026 |  | 32 | 1-1/2" | PR | 43026 | C42S1 | ST | 30 | PR43027 | PR40027 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43027 |  | 32 | 1" | PR | 43027 | C42S1 | HB | 30 | PR43045 | 32AT 2401-3 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43027 |  | 32 | 2" | PR | 43027 | C42S1 | HB | 30 | PR43045 | 32AT 2401-3 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43028 |  | 32 | 1" | PR | 43028 | C42S1 | ST | 30 | PR43045 | OG43001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43030 | 08 | 32 | 1-1/2" | PR | 43030 | C42S1 | N | 0 | 32-E-4301 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43030 | 08 | 32 | 4" | PR | 43030 | C42S1 | N | 0 | 32-E-4301 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43031 | 08 | 32 | 3/4" | PR | 43031 | C42S1 | N | 0 | 32-P-4300 | PR43032 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43048 | 08 | 32 | 3/4" | PR | 43048 | C42S1 | N | 0 | 32-T-4300 | BDL43019 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43048 | 08 | 32 | 1-1/2" | PR | 43048 | C42S1 | N | 0 | 32-T-4300 | BDL43019 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43048 | 08 | 32 | 3" | PR | 43048 | C42S1 | N | 0 | 32-T-4300 | BDL43019 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43049 | 08 | 32 | 2" | PR | 43049 | C42S1 | N | 0 | 32-T-4300 | BDL43018 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43050 |  | 32 | 1/2" | PR | 43050 | C42S1 | HB | 30 | PR43045 | BDL43026 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43050 |  | 32 | 1-1/2" | PR | 43050 | C42S1 | HB | 30 | PR43045 | BDL43026 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43050 |  | 32 | 3" | PR | 43050 | C42S1 | HB | 30 | PR43045 | BDL43026 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR50010 |  | 32 | 3/4" | PR | 50010 | B4S1 | P | 50 | P50013 | 32-T-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
PR50010 |  | 32 | 2" | PR | 50010 | B4S1 | P | 50 | P50013 | 32-T-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
LC31035 | 08 | 32 | 1-1/2" | LC | 31035 | B-5 | HB | 40 | LS31043 | LC23027 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31038 |  | 32 | 1-1/2" | LC | 31038 | B-5 | P | 50 | LS31033 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31039 | 08 | 32 | 1/2" | LC | 31039 | B-5 | P | 50 | LS31036 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31040 | 08 | 32 | 1/2" | LC | 31040 | B-5 | P | 50 | PR31014 | LS63199 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31041 | 08 | 32 | 1/2" | LC | 31041 | B-5 | HB | 30 | LS31035 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31042 | 08 | 32 | 1-1/2" | LC | 31042 | B-5 | HB | 40 | LS31046 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31043 |  | 32 | 3/4" | LC | 31043 | B-5 | P | 50 | LS31042 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31044 | 08 | 32 | 1-1/2" | LC | 31044 | B-5 | HB | 40 | LS31044 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC32001 |  | 32 | 3/4" | LC | 32001 | B-5 | HB | 30 | LS32001 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC43002 |  | 32 | 3/4" | LC | 43002 | B-5 | HB | 30 | LS43011 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.33 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | E | Y | 000 | N | 130
LC43003 |  | 32 | 1" | LC | 43003 | B-5 | HB | 40 | LS43010 | LC20001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.33 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50001 |  | 32 | 3/4" | LC | 50001 | B-5 | HB | 30 | LC5001A | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50003 |  | 32 | 3/4" | LC | 50003 | B-5 | HB | 30 | LS50046 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50004 |  | 32 | 1" | LC | 50004 | B-5 | HB | 40 | LS50045 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50006 |  | 32 | 1" | LC | 50006 | B-5 | P | 50 | P50016 | TO TRENCH | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-01 |  | E | Y | 000 | N | 133 | 77
LC50009 |  | 32 | 3/4" | LC | 50009 | B-5 | HB | 30 | LS50038 | LC43001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50010 |  | 32 | 1/2" | LC | 50010 | B-5 | HB | 30 | LS50038 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC50014 |  | 32 | 1/2" | LC | 50014 | B-5 | HB | 30 | LS50009 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | Y | 000 | N | 130
LC51001 |  | 32 | 3/4" | LC | 51001 | B-5 | HB | 30 | LS51004 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC51002 |  | 32 | 3/4" | LC | 51002 | B-5 | HB | 30 | LS51002 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC51003 |  | 32 | 3/4" | LC | 51003 | B-5 | HB | 30 | LS51003 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC51008 |  | 32 | 3/4" | LC | 51008 | B-5 | HB | 30 | LS51002 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | Y | 000 | N | 130
LC52001 |  | 32 | 1/2" | LC | 52001 | B-5 | HB | 30 | LS52007 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS63069 |  | 32 | 3/4" | LS | 63069 | B-5 | HB | 60 | LS63178 | LS13001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63069 |  | 32 | 1" | LS | 63069 | B-5 | HB | 70 | LS63178 | LS13001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63070 |  | 32 | 1" | LS | 63070 | B-5 | HB | 70 | LS630BE | JLS23010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63072 |  | 32 | 1/2" | LS | 63072 | B-5 | HB | 60 | LS63189 | 32-D-2300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63072 |  | 32 | 1-1/2" | LS | 63072 | B-5 | HB | 70 | LS63189 | 32-D-2300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63073 |  | 32 | 4" | LS | 63073 | B-5 | HB | 90 | LS01001 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | I | MOD.A | Y | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS63073 |  | 32 | 8" | LS | 63073 | B-5 | HB | 100 | LS01001 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | I | MOD.A | Y | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS63074 |  | 32 | 1" | LS | 63074 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63079 |  | 32 | 1" | LS | 63079 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63080 |  | 32 | 1" | LS | 63080 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63085 |  | 32 | 1" | LS | 63085 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63091 |  | 32 | 1" | LS | 63091 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63092 |  | 32 | 1" | LS | 63092 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63093 |  | 32 | 1" | LS | 63093 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AA |  | 32 | 2" | LS | 630AA | B-5 | HB | 80 | LS63206 | 32-1127-S-009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AF |  | 32 | 1" | LS | 630AF | B-5 | HB | 70 | LS63193 | JLS31009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
HD22005 | 08 | 32 | 1" | HD | 22005 | 3FS4 | N | 0 | HD01002 | HD40006 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.13 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD22006 | 08 | 32 | 3/4" | HD | 22006 | 3FS4 | N | 0 | HD01002 | PR21009 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.13 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD22007 | 08 | 32 | 1/2" | HD | 22007 | 3FS4 | N | 0 | HD01002 | ET22007 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.13 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD40006 | 08 | 32 | 1/2" | HD | 40006 | 3FS4 | N | 0 | N40007 | HCM40001 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.30 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD40006 | 08 | 32 | 1" | HD | 40006 | 3FS4 | N | 0 | N40007 | HCM40001 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.30 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
CWR93001 | 08 | 32 | 3/4" | CWR | 93001 | B-1 | N | 0 | 32-E-9001B | CWR93006 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93001 | 08 | 32 | 3" | CWR | 93001 | B-1 | N | 0 | 32-E-9001B | CWR93006 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93002 | 08 | 32 | 3/4" | CWR | 93002 | B-1 | N | 0 | 32-E-9001A | CWR93005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93002 | 08 | 32 | 3" | CWR | 93002 | B-1 | N | 0 | 32-E-9001A | CWR93005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93006 | 08 | 32 | 3/4" | CWR | 93006 | B-1 | N | 0 | CWR93001 | VA31002 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR94005 | 08 | 32 | 1-1/2" | CWR | 94005 | B-1 | N | 0 | 32-E-9002 | CWR94004 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR94005 | 08 | 32 | 3" | CWR | 94005 | B-1 | N | 0 | 32-E-9002 | CWR94004 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR94005 | 08 | 32 | 4" | CWR | 94005 | B-1 | N | 0 | 32-E-9002 | CWR94004 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWS01008 | 08 | 32 | 3" | CWS | 01008 | UGB-1PE | N | 0 | CWS01012 | CWS64006 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-02 |  | E | N | 000 | N | 15
CWS01008 | 08 | 32 | 20" | CWS | 01008 | UGB-1PE | N | 0 | CWS01012 | CWS64006 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-02 |  | E | N | 000 | N | 15
CWS01009 | 08 | 32 | 3/4" | CWS | 01009 | UGB-1PE | N | 0 | CW200001 OSBL LINE | CWS01012 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS01009 | 08 | 32 | 40" | CWS | 01009 | UGB-1PE | N | 0 | CW200001 OSBL LINE | CWS01012 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
HOS89002 | 08 | 32 | 4" | HOS | 89002 | C-2 | HA | 90 | TP-N60201 (32-E-8908AA) | TP-N42901 (32-S-8900A/B) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL SUPPLY | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 208
BDL60051 | 08 | 32 | 1" | BDL | 60051 | B32S1 | N | 0 | N67104 | BDL60029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60052 | 08 | 32 | 1" | BDL | 60052 | B32S1 | N | 0 | N67103 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60053 | 08 | 32 | 1" | BDL | 60053 | B32S1 | N | 0 | N67102 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60055 | 08 | 32 | 1" | BDL | 60055 | B32S1 | N | 0 | N67110 | BDL61018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60060 | 08 | 32 | 1" | BDL | 60060 | B32S1 | N | 0 | N60001 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60062 | 08 | 32 | 2" | BDL | 60062 | B32S1 | N | 0 | BDL32017 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FW68L25 | 08 | 32 | 1-1/2" | FW | 68L25 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L26 | 08 | 32 | 1" | FW | 68L26 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L27 | 08 | 32 | 1" | FW | 68L27 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68L28 | 08 | 32 | 1" | FW | 68L28 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68M04 | 08 | 32 | 1" | FW | 68M04 | B-13 | N | 0 | SWIVEL JOINT | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M05 | 08 | 32 | 2" | FW | 68M05 | B-13 | N | 0 | FW68M13 | FW68M46 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M11 | 08 | 32 | 1" | FW | 68M11 | B-13 | N | 0 | FW68M13 | FW68M12 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M25 | 08 | 32 | 3" | FW | 68M25 | B-13 | N | 0 | FW68K06 | FW68M23 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M39 | 08 | 32 | 3" | FW | 68M39 | B-13 | N | 0 | FW68K06 | FW68M32 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M42 | 08 | 32 | 2" | FW | 68M42 | B-13 | N | 0 | FW68M39 | FW68M43 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M43 | 08 | 32 | 1-1/2" | FW | 68M43 | B-13 | N | 0 | FW68M42 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M46 | 08 | 32 | 1" | FW | 68M46 | B-13 | N | 0 | FW68M05 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M49 | 08 | 32 | 1" | FW | 68M49 | B-13 | N | 0 | FW68M25 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M52 | 08 | 32 | 1-1/2" | FW | 68M52 | B-13 | N | 0 | FW68M25 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
CHWR14005 |  | 32 | 1/2" | CHWR | 14005 | B-1 | CF | 25 | 32-D-1401A | VA14008 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR14006 |  | 32 | 1/2" | CHWR | 14006 | B-1 | CF | 25 | 32-D-1401B | VA14007 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR14006 |  | 32 | 1" | CHWR | 14006 | B-1 | CF | 25 | 32-D-1401B | VA14007 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR14007 | 08 | 32 | 1-1/2" | CHWR | 14007 | B-5 | N | 0 | JLS14001 | JLS14001 | 9.0 | 280.0 | 6.0/6.0 | 10.0/170.0 |  | 14.51 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 10 | sh.7 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-023-01 |  | A | N | 010 | N | 54
CHWR14010 |  | 32 | 1" | CHWR | 14010 | B-1 | CF | 25 | CHWR15007 | CHWR61016 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15001 | 08 | 32 | 1/2" | CHWR | 15001 | B-1 | CF | 25 | JCHW14001 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15002 | 08 | 32 | 3/4" | CHWR | 15002 | B-1 | CF | 25 | JCHW14002 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15005 | 08 | 32 | 1/2" | CHWR | 15005 | B-1 | CF | 25 | CHW1526 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15006 | 08 | 32 | 1-1/2" | CHWR | 15006 | B-1 | CF | 25 | HEADER | HEADER | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15007 |  | 32 | 1-1/2" | CHWR | 15007 | B-1 | CF | 25 | CAP | CHWS14005 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR20001 |  | 32 | 1/2" | CHWR | 20001 | B-1 | CF | 25 | JCHW15001 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR20002 |  | 32 | 1" | CHWR | 20002 | B-1 | CF | 25 | CHWS20005 | CHWR43011 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR20003 |  | 32 | 1" | CHWR | 20003 | B-1 | CF | 25 | 32-Z-2004 | CHWR43011 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21006 |  | 32 | 1" | CHWR | 21006 | B-1 | CF | 25 | 32-R-2100 | 32-P-2101 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21006 |  | 32 | 6" | CHWR | 21006 | B-1 | CF | 40 | 32-R-2100 | 32-P-2101 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21007 |  | 32 | 3" | CHWR | 21007 | B-1 | CF | 25 | CHWR21006 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21008 |  | 32 | 4" | CHWR | 21008 | D3S1 | CF | 25 | 32-E-2100 | CHWR21009 | 55.0 | 150.0 | 4.0 | 7.0 |  | 82.51 | 153.15 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.12 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 1049
CHWR21009 |  | 32 | 4" | CHWR | 21009 | B-1 | CF | 25 | CHWR21008 | CHWR43011 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWS61003 |  | 32 | 1-1/2" | CHWS | 61003 | B-1 | CF | 25 | CHWS61028 | CHWS14008 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61004 |  | 32 | 3/4" | CHWS | 61004 | B-1 | CF | 25 | CHWS61028 | CHWS14010 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61004 |  | 32 | 1-1/2" | CHWS | 61004 | B-1 | CF | 25 | CHWS61028 | CHWS14010 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61004 |  | 32 | 2" | CHWS | 61004 | B-1 | CF | 25 | CHWS61028 | CHWS14010 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61005 |  | 32 | 1" | CHWS | 61005 | B-1 | CF | 25 | CHWS61028 | CHWS14005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61013 |  | 32 | 1" | CHWS | 61013 | B-1 | CF | 25 | CHWS61001 | 32-P-6100B | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61013 |  | 32 | 10" | CHWS | 61013 | B-1 | CF | 40 | CHWS61001 | 32-P-6100B | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61014 |  | 32 | 1" | CHWS | 61014 | B-1 | CF | 25 | 32-P-6100A | CHWS623 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61015 |  | 32 | 8" | CHWS | 61015 | B-1 | CF | 40 | CHWS61002 | CHWR61005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61017 | 08 | 32 | 3/4" | CHWS | 61017 | B-1 | CF | 25 | TP-033 | 32-D-6100 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61017 | 08 | 32 | 8" | CHWS | 61017 | B-1 | CF | 40 | TP-033 | 32-D-6100 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61017 | 08 | 32 | 12" | CHWS | 61017 | B-1 | CF | 40 | TP-033 | 32-D-6100 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61020 |  | 32 | 1/2" | CHWS | 61020 | B-1 | CF | 25 | CHWS61027 | TP-N10 (CHWS510109) | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61020 |  | 32 | 3" | CHWS | 61020 | B-1 | CF | 25 | CHWS61027 | TP-N10 (CHWS510109) | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61021 |  | 32 | 1" | CHWS | 61021 | B-1 | CF | 25 | CHWS61029 | 32-Z-2004 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61022 |  | 32 | 1" | CHWS | 61022 | B-1 | CF | 25 | CHWS61029 | CHWS20005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61023 |  | 32 | 4" | CHWS | 61023 | B-1 | CF | 25 | CHWS61029 | CHWS21006 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61024 |  | 32 | 3/4" | CHWS | 61024 | B-1 | CF | 25 | CHWS61002 | CHWR21006 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61024 |  | 32 | 2" | CHWS | 61024 | B-1 | CF | 25 | CHWS61002 | CHWR21006 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
HCM24087 |  | 32 | 1/2" | HCM | 24087 | D20S1 | P | 50 | HCM24097 | BDL24086 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24088 |  | 32 | 1/2" | HCM | 24088 | D20S1 | P | 50 | 32-T-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24088 |  | 32 | 1" | HCM | 24088 | D20S1 | P | 50 | 32-T-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24088 |  | 32 | 2" | HCM | 24088 | D20S1 | P | 50 | 32-T-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24089 |  | 32 | 2" | HCM | 24089 | D20S1 | P | 50 | HCM23060 | PR23013 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24090 |  | 32 | 14" | HCM | 24090 | D20S1 | HB | 40 | 32-T-2400 | 32-E-2402 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 106.76 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24091 |  | 32 | 18" | HCM | 24091 | D20S1 | HB | 40 | 32-E-2402 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.2 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24092 | 08 | 32 | 1" | HCM | 24092 | D20S1 | N | 0 | BDL24063 | 32-P-2400A | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24092 | 08 | 32 | 10" | HCM | 24092 | D20S1 | N | 0 | BDL24063 | 32-P-2400A | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24093 | 08 | 32 | 8" | HCM | 24093 | D20S1 | N | 0 | BDL24066 | 32-P-2400B | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24094 |  | 32 | 3/4" | HCM | 24094 | D20S1 | P | 50 | HCM24085 | HCM24025 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 328 | 15
HCM24094 |  | 32 | 1-1/2" | HCM | 24094 | D20S1 | P | 50 | HCM24085 | HCM24025 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 328 | 15
HCM24095 | 08 | 32 | 1/2" | HCM | 24095 | D20S1 | P | 50 | HCM23065 | 32-R-2300 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.15A | 1 | III | MOD.G | Y | 1 | N | 32-P-044-01 |  | F | N | 141 | N | 530 | 15
BDL21010 | 08 | 32 | 3/4" | BDL | 21010 | B32S1 | N | 0 | PR21017 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL21011 | 08 | 32 | 1/2" | BDL | 21011 | B32S1 | N | 0 | PR21015 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL21012 | 08 | 32 | 3/4" | BDL | 21012 | B32S1 | N | 0 | PR21009 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL21012 | 08 | 32 | 1" | BDL | 21012 | B32S1 | N | 0 | PR21009 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL21013 | 08 | 32 | 3/4" | BDL | 21013 | B32S1 | N | 0 | TP-7 (Z-2012) | BDL31024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
JCW86015 |  | 32 | 1/2" | JCW | 86015 | B-1 | HB | 30 | CWS86017 | CWR86012 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86016 |  | 32 | 1/2" | JCW | 86016 | B-1 | HB | 30 | CWS86021 | JCW86013 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86016 |  | 32 | 1-1/2" | JCW | 86016 | B-1 | HB | 30 | CWS86021 | JCW86013 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86017 |  | 32 | 1-1/2" | JCW | 86017 | B-1 | HB | 30 | PX86025 | PX86002 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86018 |  | 32 | 1/2" | JCW | 86018 | B-1 | HB | 30 | CWS86018 | CWR86014 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86021 |  | 32 | 2" | JCW | 86021 | B-1 | HB | 30 | JCW86020 | CWR86017 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86022 |  | 32 | 1-1/2" | JCW | 86022 | B-1 | HB | 30 | PX86037 | PX86002 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JLS14001 |  | 32 | 3" | JLS | 14001 | B-5 | HB | 50 | CHWR14007 | CHWR14007 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 000 | N | 111 | 1
JLS16001 | 08 | 32 | 2" | JLS | 16001 | B-5 | HB | 50 | LS16010 | LS16001 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.10 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-023-01 |  | E | N | 000 | N | 105
JLS21002 |  | 32 | 1" | JLS | 21002 | B-5 | HB | 50 | CHWS21003 | CHWS21004 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.12 | 2 | I | MOD.A | Y | 20 | N | 32-U-023-01 |  | E | N | 000 | N | 111 | 1
N60001 | 08 | 32 | 1" | N | 60001 | B-1 | N | 0 | N67050 | BDL60060 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N61004 | 08 | 32 | 1/2" | N | 61004 | B-1 | N | 0 | N67016 | 32-AFR-6101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
LO89003 | 08 | 32 | 3" | LO | 89003 | QXB-55 | N | 0 | TP-N20103 (BEARING NDE) | TP-N21103 (D-8913) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LO89004 | 08 | 32 | 3" | LO | 89004 | QXB-55 | N | 0 | TP-N20104 (BEARING NDE) | TP-N21104 (D-8913) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LPN01001 | 08 | 32 | 3/4" | LPN | 01001 | 1C13 | N | 0 | N01008 | SP-0105 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
N67039 | 08 | 32 | 1/2" | N | 67039 | B-1 | N | 0 | N67005 | N67038 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N67039 | 08 | 32 | 1" | N | 67039 | B-1 | N | 0 | N67005 | N67038 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
PR33029 | 08 | 32 | 1/2" | PR | 33029 | C42S1 | N | 0 | PR33017 | BDL33010 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33032 | 08 | 32 | 3/4" | PR | 33032 | D20S1 | N | 0 | PR33019 | BDL33021 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR34001 |  | 32 | 6" | PR | 34001 | B4S1 | P | 50 | 32-S-3400 | BDL34013 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34002 |  | 32 | 3/4" | PR | 34002 | B4S1 | P | 50 | 32-S-3400 | BDL34018 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34002 |  | 32 | 10" | PR | 34002 | B4S1 | P | 100 | 32-S-3400 | BDL34018 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34015 |  | 32 | 6" | PR | 34015 | B4S1 | P | 50 | 32-S-3400 | 32-S-3401A | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34017 |  | 32 | 3/4" | PR | 34017 | B4S1 | ET | 40 | 32-D-3400 | PR34029 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34018 |  | 32 | 1" | PR | 34018 | B4S1 | ET | 50 | PR34017 | BDL34014 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34018 |  | 32 | 2" | PR | 34018 | B4S1 | ET | 50 | PR34017 | BDL34014 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34019 |  | 32 | 1" | PR | 34019 | QXB26S1 | ET | 30 | N34007 | PR34028 | 8.0/8.0 | 200.0/-45.0 | 5.0 | 80.0 |  | 12.83 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-048-01 |  | G | N | 141 | N | 392 | 10
PR34020 |  | 32 | 1" | PR | 34020 | B4S1 | ET | 50 | PR34021 | 32-D-3400 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34020 |  | 32 | 2" | PR | 34020 | B4S1 | ET | 50 | PR34021 | 32-D-3400 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34021 |  | 32 | 3/4" | PR | 34021 | D20S1 | HB | 30 | PR36009 | PR34020 | 55.0/55.0 | -45.0/190.0 | 40.0/40.0 | 80.0/121.0 |  | 82.81 | 153.15 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-048-01 |  | G | N | 141 | N | 334 | 10
PR34021 |  | 32 | 1-1/2" | PR | 34021 | D20S1 | HB | 30 | PR36009 | PR34020 | 55.0/55.0 | -45.0/190.0 | 40.0/40.0 | 80.0/121.0 |  | 82.81 | 153.15 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-048-01 |  | G | N | 141 | N | 334 | 10
PR34022 |  | 32 | 1" | PR | 34022 | B4S1 | P | 50 | 32-S-3401A | 32-E-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34023 |  | 32 | 1-1/2" | PR | 34023 | B4S1 | P | 50 | 32-S-3401A | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01,32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34024 |  | 32 | 10" | PR | 34024 | B4S1 | P | 100 | 32-S-3401B | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01,32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34025 |  | 32 | 1" | PR | 34025 | B4S1 | P | 50 | 32-S-3401B | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01,32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34026 |  | 32 | 1" | PR | 34026 | B4S1 | P | 50 | 32-S-3401A | BDL34016 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
LS15096 |  | 32 | 1/2" | LS | 15096 | B-5 | HB | 60 | LS63199 | 32-B-5001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS20001 |  | 32 | 3/4" | LS | 20001 | B-5 | HB | 60 | JLS20001 | LC20001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS21001 |  | 32 | 3/4" | LS | 21001 | B-5 | HB | 60 | JLS21002 | LC21001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.12 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N81058 | 08 | 32 | 1/2" | N | 81058 | 1CS2 | N | 0 | N89060 | N810328 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.62 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81059 | 08 | 32 | 1/2" | N | 81059 | B-1 | N | 0 | N89069 | N81052 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N83001 | 08 | 32 | 1/2" | N | 83001 | 1CS2 | N | 0 | N89043 | TP-206 (32-V-8300) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.63 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N83002 | 08 | 32 | 1/2" | N | 83002 | 1CS2 | N | 0 | IA89053 | TP-205 (32-S-8300) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.63 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-094-01 |  | M | N | 000 | N | 166
N89001 | 08 | 32 | 3/4" | N | 89001 | B-1 | N | 0 | N01001 | N89030 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89001 | 08 | 32 | 2" | N | 89001 | B-1 | N | 0 | N89001 | N89001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N89002 | 08 | 32 | 1/2" | N | 89002 | B-1 | N | 0 | N89068 | N81018 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
BDL32027 | 08 | 32 | 3/4" | BDL | 32027 | B32S1 | N | 0 | HCM32024 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32028 | 08 | 32 | 3/4" | BDL | 32028 | B32S1 | N | 0 | HCM32024 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32029 | 08 | 32 | 8" | BDL | 32029 | B32S1 | HB | 30 | HCM32044, PSV-3280 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32030 | 08 | 32 | 3" | BDL | 32030 | B32S1 | HB | 30 | HCM32036 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32030 | 08 | 32 | 8" | BDL | 32030 | B32S1 | HB | 30 | HCM32036 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32032 | 08 | 32 | 2" | BDL | 32032 | B32S1 | N | 0 | TP-04A (32-D-3202A) | BDL32031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32039 | 08 | 32 | 2" | BDL | 32039 | B32S1 | N | 0 | TP-32B, (32-D-3203B) | BDL32036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24G | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL33001 | 08 | 32 | 3" | BDL | 33001 | B32S1 | N | 0 | PR33002 | BDL33002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33001 | 08 | 32 | 4" | BDL | 33001 | B32S1 | N | 0 | PR33002 | BDL33002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33002 | 08 | 32 | 3/4" | BDL | 33002 | B32S1 | N | 0 | BDL33001 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33002 | 08 | 32 | 4" | BDL | 33002 | B32S1 | N | 0 | BDL33001 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33002 | 08 | 32 | 10" | BDL | 33002 | B32S1 | N | 0 | BDL33001 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33003 | 08 | 32 | 2" | BDL | 33003 | B32S1 | N | 0 | PR33027 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33003 | 08 | 32 | 4" | BDL | 33003 | B32S1 | N | 0 | PR33027 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33004 | 08 | 32 | 1" | BDL | 33004 | B32S1 | N | 0 | PR33014 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
CWS01010 | 08 | 32 | 32" | CWS | 01010 | UGB-1PE | N | 0 | CWS01009 | CWS64001 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS01012 | 08 | 32 | 44" | CWS | 01012 | UGB-1PE | N | 0 | CWS01009 | CWS01013 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS01013 | 08 | 32 | 36" | CWS | 01013 | UGB-1PE | N | 0 | CWS01012 | CWS00C01 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
FW68A17 | 08 | 45 | 20" | FW | 68A17 | PEB-69 | N | 0 | FW68A03 | FW68B02 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A19 | 08 | 45 | 12" | FW | 68A19 | B-7 | N | 0 | FW68A96 | FW68K11 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A20 | 08 | 45 | 18" | FW | 68A20 | PEB-69 | N | 0 | FW68A17 | FW68A21 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A21 | 08 | 45 | 16" | FW | 68A21 | PEB-69 | N | 0 | FW68A20 | FW68A95 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
BDL61001 | 08 | 32 | 8" | BDL | 61001 | B32S1 | N | 0 | BDL61007 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61002 | 08 | 32 | 3/4" | BDL | 61002 | B32S1 | N | 0 | TP-003 (32-D-6103) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61007 | 08 | 32 | 4" | BDL | 61007 | B32S1 | N | 0 | TP-018 (32-PSV-6169) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42C | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61008 | 08 | 32 | 1" | BDL | 61008 | B32S1 | N | 0 | TP-026 (LO610171) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61009 | 08 | 32 | 3" | BDL | 61009 | B32S1 | N | 0 | TP-020 (32-PSV-6177) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61010 | 08 | 32 | 6" | BDL | 61010 | B32S1 | N | 0 | TP-022 (32-PSV-6180) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61013 | 08 | 32 | 3/4" | BDL | 61013 | B32S1 | N | 0 | E-6101, VM-61199 | BDL61012 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61014 | 08 | 32 | 3/4" | BDL | 61014 | B32S1 | N | 0 | TP-043 (PR610116) | BDL61024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61016 | 08 | 32 | 1/2" | BDL | 61016 | B32S1 | N | 0 | TP-046 (32-D-6108) | BDL61015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61018 | 08 | 32 | 4" | BDL | 61018 | B32S1 | N | 0 | BDL71027 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61019 | 08 | 32 | 1/2" | BDL | 61019 | B32S1 | N | 0 | TP-029 (E-6102) | BDL61008 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61020 | 08 | 32 | 1/2" | BDL | 61020 | B32S1 | N | 0 | TP-052 (E-6102) | BDL61019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61021 | 08 | 32 | 3/4" | BDL | 61021 | B32S1 | N | 0 | TP-056 (PR610106) | BDL61022 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61022 | 08 | 32 | 3/4" | BDL | 61022 | B32S1 | N | 0 | TP-057 (PR610112) | BDL61019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61024 | 08 | 32 | 1" | BDL | 61024 | B32S1 | N | 0 | PR33024 | BDL61016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL65001 | 08 | 32 | 2" | BDL | 65001 | B4S1 | N | 0 | BDL65005 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL65002 | 08 | 32 | 3/4" | BDL | 65002 | B4S1 | N | 0 | 32-D-6500 | BDL65003 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 1 | N | 32-P-031-01 |  | G | N | 141 | N | 470 | ,10
CHWR24003 |  | 32 | 3/4" | CHWR | 24003 | C42S1 | CF | 25 | 32-E-2404 | CHWR24004 | 42.0/42.0 | 150.0/-45.0 | 2.0 | 7.0 |  | 63.01 | 76.65 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.19 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-02 |  | M | N | 010 | N | 1054
CHWR24004 |  | 32 | 6" | CHWR | 24004 | B-1 | CF | 40 | CHWR24003 | CHWR43011 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.19 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR43010 |  | 32 | 1" | CHWR | 43010 | C42S1 | CF | 25 | 32-E-4302 | CHWR43011 | 28.0/28.0 | 180.0/-45.0 | 2.0 | 7.0 |  | 42.12 | 76.65 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.33 | 2 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | M | N | 010 | N | 1052
CHWR43011 |  | 32 | 6" | CHWR | 43011 | B-1 | CF | 40 | CHWR24004 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR43011 |  | 32 | 8" | CHWR | 43011 | B-1 | CF | 40 | CHWR24004 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWS61024 |  | 32 | 4" | CHWS | 61024 | B-1 | CF | 25 | CHWS61002 | CHWR21006 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61025 |  | 32 | 3" | CHWS | 61025 | B-1 | CF | 25 | CHWS61029 | CHWS24002 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61025 |  | 32 | 6" | CHWS | 61025 | B-1 | CF | 40 | CHWS61029 | CHWS24002 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61026 |  | 32 | 3/4" | CHWS | 61026 | B-1 | CF | 25 | CHWS61027 | 32-D-6500 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61026 |  | 32 | 1-1/2" | CHWS | 61026 | B-1 | CF | 25 | CHWS61027 | 32-D-6500 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61027 |  | 32 | 3" | CHWS | 61027 | B-1 | CF | 25 | CHWS61002 | CHWS61020 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61029 |  | 32 | 6" | CHWS | 61029 | B-1 | CF | 40 | CHWS61002 | CHWS43010 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61029 |  | 32 | 8" | CHWS | 61029 | B-1 | CF | 40 | CHWS61002 | CHWS43010 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61030 | 08 | 32 | 1-1/2" | CHWS | 61030 | C42S1 | CF | 25 | TP-010, E-6102 | TP-032 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 5.5 | 2.0 |  | 28.05 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42E | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | M | N | 010 | N | 1057
CO26025 | 08 | 32 | 3/4" | CO | 26025 | 1IS5 | N | 0 | CO26033 | CO26026 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26026 | 08 | 32 | 3/4" | CO | 26026 | 1IS5 | N | 0 | CO26025 | BDL26003 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26027 | 08 | 32 | 3/4" | CO | 26027 | 1IS5 | N | 0 | 32-R-2300 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26028 | 08 | 32 | 1/2" | CO | 26028 | 1IS5 | N | 0 | CO26029 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26028 | 08 | 32 | 1" | CO | 26028 | 1IS5 | N | 0 | CO26029 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26029 | 08 | 32 | 1/2" | CO | 26029 | 1IS5 | N | 0 | 32-R-2300 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26029 | 08 | 32 | 1" | CO | 26029 | 1IS5 | N | 0 | 32-R-2300 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26030 | 08 | 32 | 1/2" | CO | 26030 | 1IS5 | N | 0 | CO26037 | CO26032 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26032 | 08 | 32 | 3/4" | CO | 26032 | 1IS5 | N | 0 | CO26030 | CO26029 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26036 | 08 | 32 | 1/2" | CO | 26036 | 1IS5 | N | 0 | 1 ST. EMERGENCY KILLER SYSTEM | CO26025 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
HCM23054 |  | 32 | 1/2" | HCM | 23054 | 1FS4 | HB | 30 | HCM23050 | P23023 | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23055 |  | 32 | 3/4" | HCM | 23055 | 1FS4 | ET | 30 | P23022 | TP-11 (PR230112) | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23057 |  | 32 | 1" | HCM | 23057 | 1FS4 | JP | 0 | JLS23009 | JLS23011 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23058 |  | 32 | 6" | HCM | 23058 | C42S1 | HB | 40 | HCM23046 | BDL23046 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23059 |  | 32 | 2" | HCM | 23059 | C42S1 | P | 50 | HCM23046 | VA23003 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23060 |  | 32 | 1/2" | HCM | 23060 | C42S1 | HB | 30 | HCM23004 | HCM24089 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23060 |  | 32 | 4" | HCM | 23060 | C42S1 | HB | 40 | HCM23004 | HCM24089 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23061 |  | 32 | 1/2" | HCM | 23061 | 1FS4 | JP | 0 | HCM23057 | HCM23066 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23061 | 08 | 32 | 1" | HCM | 23061 | 1FS4 | N | 0 | HCM23057 | HCM23066 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
BDL21014 | 08 | 32 | 3/4" | BDL | 21014 | B32S1 | N | 0 | HD22006 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
BDL22012 | 08 | 32 | 3/4" | BDL | 22012 | B32S1 | N | 0 | HD01002 | BDL22015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.13 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL22015 | 08 | 32 | 3/4" | BDL | 22015 | B32S1 | N | 0 | BDL22012 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.13 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL22016 | 08 | 32 | 3/4" | BDL | 22016 | B32S1 | N | 0 | ET22010 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.13 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL22017 | 08 | 32 | 1/2" | BDL | 22017 | B32S1 | N | 0 | ET22008 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.13 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL22019 | 08 | 32 | 3/4" | BDL | 22019 | B32S1 | N | 0 | PR33019 | BDL24084 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.13 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL22020 | 08 | 32 | 1" | BDL | 22020 | B32S1 | N | 0 | BDL43021 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL22021 | 08 | 32 | 1/2" | BDL | 22021 | B32S1 | N | 0 | 32-D-2202 | BDL00001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.13 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23013 | 08 | 32 | 1/2" | BDL | 23013 | B32S1 | N | 0 | P23018 | BDL23043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23014 | 08 | 32 | 1/2" | BDL | 23014 | B32S1 | N | 0 | P23019 | BDL23013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23016 | 08 | 32 | 4" | BDL | 23016 | B32S1 | N | 0 | BDL23024 | BDL24079 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23024 | 08 | 32 | 3" | BDL | 23024 | B32S1 | N | 0 | HCM23018 | BDL23016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23025 | 08 | 32 | 3/4" | BDL | 23025 | B32S1 | N | 0 | P23021 | BDL23043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FL60006 |  | 32 | 12" | FL | 60006 | B32S1 | ST | 40 | 32-D-6001 | 32-D-6002 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 490 | 10
JLS23008 |  | 32 | 1" | JLS | 23008 | B-5 | HB | 50 | HCM23045 | HCM23048 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23009 |  | 32 | 3/4" | JLS | 23009 | B-5 | HB | 40 | HCM23048 | HCM23057 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23010 |  | 32 | 3" | JLS | 23010 | B-5 | HB | 50 | LS63070 | LS23022 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23011 |  | 32 | 1/2" | JLS | 23011 | B-5 | HB | 40 | HCM23057 | HCM23063 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23012 |  | 32 | 1/2" | JLS | 23012 | B-5 | HB | 40 | JLS23011 | LS23026 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23013 |  | 32 | 1/2" | JLS | 23013 | B-5 | HB | 40 | LS63045 | LS23032 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23013 |  | 32 | 1-1/2" | JLS | 23013 | B-5 | HB | 50 | LS63045 | LS23032 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23014 |  | 32 | 3/4" | JLS | 23014 | B-5 | HB | 40 | LS63045 | LS23023 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23015 | 08 | 32 | 1/2" | JLS | 23015 | B-5 | HB | 40 | LS63043 | LS23027 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23015 | 08 | 32 | 1-1/2" | JLS | 23015 | B-5 | HB | 50 | LS63043 | LS23027 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23016 |  | 32 | 1/2" | JLS | 23016 | B-5 | HB | 40 | LS63044 | HCM23067 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23017 |  | 32 | 1/2" | JLS | 23017 | B-5 | JP | 0 | LS63044 | LS23031 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23017 |  | 32 | 1-1/2" | JLS | 23017 | B-5 | JP | 0 | LS63044 | LS23031 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23018 |  | 32 | 1-1/2" | JLS | 23018 | B-5 | HB | 50 | LS63042 | LS23029 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23019 |  | 32 | 1/2" | JLS | 23019 | B-5 | HB | 40 | LS63146 | LS23030 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23020 | 08 | 32 | 1/2" | JLS | 23020 | B-5 | HB | 40 | LS63147 | LS23028 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23020 | 08 | 32 | 1-1/2" | JLS | 23020 | B-5 | HB | 50 | LS63147 | LS23028 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23021 |  | 32 | 1-1/2" | JLS | 23021 | B-5 | HB | 50 | LS63140 | LS23033 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS24001 |  | 32 | 3" | JLS | 24001 | B-5 | HB | 50 | LS63038 | LS24010 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-046-01 |  | E | N | 000 | N | 111 | 1
PN52015 |  | 32 | 1-1/2" | PN | 52015 | B4S2 | P | 50 | 32-D-5200 | 32-T-5200 | 0.5 | 120.0 | 0.2 | 100.0 |  | .55 | 26.46 | P | PROCESS NITROGEN | G | - | - | >1.5 | 100 | sh.37 | 2 | NA | NA | NA | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 142
PN52016 | 7A | 32 | 6" | PN | 52016 | 1CS2 | HA | 40 | 32-E-5200 | 32-A-5200 | 6.9 | 200.0 | 0.5/0.5 | 110.0/30.0 |  | 9.18 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.37 | 2 | I | MOD.A | Y | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 151
PN52016 | 7A | 32 | 20" | PN | 52016 | 1CS2 | HA | 40 | 32-E-5200 | 32-A-5200 | 6.9 | 200.0 | 0.5/0.5 | 110.0/30.0 |  | 9.18 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.37 | 2 | I | MOD.A | Y | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 151
PN52018 | 7A | 32 | 3/4" | PN | 52018 | 1CS2 | HB | 30 | PN52027 | 32-E-5200 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52018 | 7A | 32 | 20" | PN | 52018 | 1CS2 | HB | 40 | PN52027 | 32-E-5200 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52019 | 08 | 32 | 16" | PN | 52019 | 1CS2 | N | 0 | PN52024 | PN52015 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52020 | 7A | 32 | 3/4" | PN | 52020 | 1CS2 | HB | 30 | 32-T-5200 | ACW | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52020 | 7A | 32 | 20" | PN | 52020 | 1CS2 | HB | 40 | 32-T-5200 | ACW | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52021 | 7A | 32 | 16" | PN | 52021 | 1CS2 | HB | 40 | PN52020 | 32-Z-5201A | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52022 | 7A | 32 | 16" | PN | 52022 | 1CS2 | HB | 40 | PN52020 | 32-Z-5201B | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52023 | 7A | 32 | 16" | PN | 52023 | 1CS2 | HB | 40 | PN52028 | PN52026 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52024 | 7A | 32 | 16" | PN | 52024 | 1CS2 | HB | 40 | PN52027 | PN52025 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52025 | 7A | 32 | 16" | PN | 52025 | 1CS2 | HB | 40 | PN52024 | VA52012 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52026 | 7A | 32 | 16" | PN | 52026 | 1CS2 | HB | 40 | PN52023 | VA52010 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52027 | 7A | 32 | 3/4" | PN | 52027 | 1CS2 | HB | 30 | 32-Z-5202A | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52027 | 7A | 32 | 20" | PN | 52027 | 1CS2 | HB | 40 | 32-Z-5202A | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52028 | 7A | 32 | 14" | PN | 52028 | 1CS2 | HB | 40 | 32-Z-5202B | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52029 | 08 | 32 | 1" | PN | 52029 | 1CS2 | N | 0 | N52041 | N52041 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52030 | 7A | 32 | 4" | PN | 52030 | 1CS2 | HB | 40 | PN52020 | VA52016 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
N67039 | 08 | 32 | 1-1/2" | N | 67039 | B-1 | N | 0 | N67005 | N67038 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N67040 | 08 | 32 | 3/4" | N | 67040 | B-1 | N | 0 | N67029 | N52025 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67041 | 08 | 32 | 1/2" | N | 67041 | B-1 | N | 0 | N67029 | JWR13171 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67041 | 08 | 32 | 3/4" | N | 67041 | B-1 | N | 0 | N67029 | JWR13171 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67044 | 08 | 32 | 1/2" | N | 67044 | B-1 | N | 0 | N67029 | N52031 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67045 | 08 | 32 | 1" | N | 67045 | B-1 | N | 0 | N67029 | N67043 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67046 | 08 | 32 | 1" | N | 67046 | B-1 | N | 0 | N01001 | N2 FILTER, N710146 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67048 | 08 | 32 | 1" | N | 67048 | B-1 | N | 0 | N67003 | PR72051 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67049 | 08 | 32 | 3/4" | N | 67049 | B-1 | N | 0 | N67050 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67050 | 08 | 32 | 1-1/2" | N | 67050 | B-1 | N | 0 | HEADER | N01001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67052 | 08 | 32 | 3" | N | 67052 | B-1 | N | 0 | N67029 | N50002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67053 | 08 | 32 | 3/4" | N | 67053 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67054 | 08 | 32 | 3/4" | N | 67054 | B-1 | N | 0 | N67010 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67055 | 08 | 32 | 1-1/2" | N | 67055 | B-1 | N | 0 | N67005 | N67002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67056 | 08 | 32 | 1/2" | N | 67056 | B-1 | N | 0 | N67055 | N12027 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67057 | 08 | 32 | 1/2" | N | 67057 | B-1 | N | 0 | N67055 | N12023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67058 | 08 | 32 | 1/2" | N | 67058 | B-1 | N | 0 | N67055 | N12025 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67060 | 08 | 32 | 1-1/2" | N | 67060 | B-1 | N | 0 | N01001 | TP-6 (PN400105) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67061 | 08 | 32 | 2" | N | 67061 | B-1 | N | 0 | N67051 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67062 | 08 | 32 | 1/2" | N | 67062 | B-1 | N | 0 | N67017 | 32-D-5101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 000 | N | 140
PR34027 |  | 32 | 1" | PR | 34027 | B4S1 | P | 50 | 32-S-3401B | BDL34017 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34029 |  | 32 | 1/2" | PR | 34029 | QXB26S1 | ET | 30 | PR34017 | OTHER SECTIONS | 8.0/8.0 | 200.0/-45.0 | 5.0 | 80.0 |  | 12.83 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 27 | N | 32-P-048-01 |  | G | N | 141 | N | 392 | 10
JWS64009 | 08 | 32 | 20" | JWS | 64009 | B-1 | N | 0 | 32-P-6400B | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64010 | 08 | 32 | 14" | JWS | 64010 | B-1 | N | 0 | 32-P-6400C | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64012 |  | 32 | 16" | JWS | 64012 | B-1 | SB | 100 | JWS64008 | JWR64006 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64014 | 08 | 32 | 3" | JWS | 64014 | B-1 | N | 0 | JWS64054 | TP-12,JWS710118 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64017 | 08 | 32 | 6" | JWS | 64017 | B-1 | N | 0 | JWS64056 | JWS72004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64018 | 08 | 32 | 4" | JWS | 64018 | B-1 | N | 0 | JWS64056 | JWS72003 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64019 | 08 | 32 | 4" | JWS | 64019 | B-1 | N | 0 | JWS64054 | JWS32001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64020 | 08 | 32 | 2" | JWS | 64020 | B-1 | N | 0 | JWS64059 | TP 23B (JWS320118) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64021 | 08 | 32 | 2" | JWS | 64021 | B-1 | N | 0 | JWS64059 | TP-23A, JWS320118, JWS320318 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64022 | 08 | 32 | 3" | JWS | 64022 | B-1 | N | 0 | JWS64056 | JWS33001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64023 | 08 | 32 | 4" | JWS | 64023 | B-1 | N | 0 | JWS64054 | TP-149, (JWS360139) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64024 | 08 | 32 | 3" | JWS | 64024 | B-1 | N | 0 | JWS64054 | 32-E-3500 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64025 | 08 | 32 | 1-1/2" | JWS | 64025 | B-1 | N | 0 | JWS64055 | 32-E-4001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64025 | 08 | 32 | 14" | JWS | 64025 | B-1 | N | 0 | JWS64055 | 32-E-4001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64026 | 08 | 32 | 2" | JWS | 64026 | B-1 | N | 0 | JWS64025 | TP-3 (JWS400100) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64027 | 08 | 32 | 3" | JWS | 64027 | B-1 | N | 0 | JWS64054 | JWS43001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64028 | 08 | 32 | 1-1/2" | JWS | 64028 | B-1 | N | 0 | JWS64027 | JW43001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
N89003 | 08 | 32 | 1/2" | N | 89003 | B-1 | N | 0 | N89012 | TP-N2 (32-XV-8127) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89004 | 08 | 32 | 1/2" | N | 89004 | B-1 | N | 0 | N89068 | N81020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89005 | 08 | 32 | 1/2" | N | 89005 | B-1 | N | 0 | N89060 | N81014 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89006 | 08 | 32 | 1/2" | N | 89006 | B-1 | N | 0 | N89068 | N81019 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89007 | 08 | 32 | 1/2" | N | 89007 | B-1 | N | 0 | N89068 | N81021 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89008 | 08 | 32 | 1/2" | N | 89008 | B-1 | N | 0 | N89011 | N80012 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89008 | 08 | 32 | 1" | N | 89008 | B-1 | N | 0 | N89011 | N80012 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89009 | 08 | 32 | 1/2" | N | 89009 | B-1 | N | 0 | N89068 | N81017 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89010 | 08 | 32 | 2" | N | 89010 | B-1 | N | 0 | N89034 | N80018 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89011 | 08 | 32 | 1" | N | 89011 | B-1 | N | 0 | N89034 | N89010 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89011 | 08 | 32 | 1-1/2" | N | 89011 | B-1 | N | 0 | N89034 | N89010 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89013 | 08 | 32 | 1" | N | 89013 | B-1 | N | 0 | N89034 | 32-D-8107 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89030 | 08 | 32 | 3/4" | N | 89030 | B-1 | N | 0 | N89001 | FX-6763 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89035 | 08 | 32 | 1" | N | 89035 | B-1 | N | 0 | N89034 | LN89007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89043 | 08 | 32 | 1/2" | N | 89043 | B-1 | N | 0 | N89067 | N83001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89044 | 08 | 32 | 3/4" | N | 89044 | B-1 | N | 0 | N01001 | IW89028 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N89047 | 08 | 32 | 1/2" | N | 89047 | B-1 | N | 0 | N89098 | TP-N20331 (32-Z-8900) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N89049 | 08 | 32 | 3/4" | N | 89049 | B-1 | N | 0 | N89034 | 32-US-1211-10 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
BDL33005 | 08 | 32 | 3/4" | BDL | 33005 | B32S1 | N | 0 | PR72002 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33005 | 08 | 32 | 2" | BDL | 33005 | B32S1 | N | 0 | PR72002 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33006 | 08 | 32 | 2" | BDL | 33006 | B32S1 | N | 0 | PR33023 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33007 | 08 | 32 | 3/4" | BDL | 33007 | B32S1 | N | 0 | PR33006 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33007 | 08 | 32 | 8" | BDL | 33007 | B32S1 | N | 0 | PR33006 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33008 | 08 | 32 | 1/2" | BDL | 33008 | B32S1 | N | 0 | PR33028 | BDL33010 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33009 | 08 | 32 | 1" | BDL | 33009 | B32S1 | N | 0 | 32-P-3300A | BDL33013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33010 | 08 | 32 | 1/2" | BDL | 33010 | B32S1 | N | 0 | PR33029 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33011 | 08 | 32 | 1/2" | BDL | 33011 | B32S1 | N | 0 | PR33015 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33012 | 08 | 32 | 3/4" | BDL | 33012 | B32S1 | N | 0 | PR33019 | BDL33015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33012 | 08 | 32 | 1" | BDL | 33012 | B32S1 | N | 0 | PR33019 | BDL33015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33013 | 08 | 32 | 1/2" | BDL | 33013 | B32S1 | N | 0 | BDL33009 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33014 | 08 | 32 | 1/2" | BDL | 33014 | B32S1 | N | 0 | BDL33016 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33014 | 08 | 32 | 1" | BDL | 33014 | B32S1 | N | 0 | BDL33016 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33015 | 08 | 32 | 3/4" | BDL | 33015 | B32S1 | N | 0 | BDL33012 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33015 | 08 | 32 | 1" | BDL | 33015 | B32S1 | N | 0 | BDL33012 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33016 | 08 | 32 | 1" | BDL | 33016 | B32S1 | N | 0 | 32-P-3300B | BDL33014 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
FW68A23 | 08 | 45 | 6" | FW | 68A23 | PEB-69 | N | 0 | FW68A20 | FW68A94 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A26 | 08 | 45 | 6" | FW | 68A26 | B-13 | N | 0 | FW68A34 | FOR HOSE REEL ON THE STRUCTURE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A27 | 08 | 45 | 6" | FW | 68A27 | PEB-69 | N | 0 | FW68A20 | FW68A99 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A29 | 08 | 45 | 6" | FW | 68A29 | PEB-69 | N | 0 | FW68A20 | FW68A0A | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A34 | 08 | 45 | 1" | FW | 68A34 | B-13 | N | 0 | FW68A97 | FOR HOSE REEL ON THE STRUCTURE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A38 | 08 | 45 | 6" | FW | 68A38 | B-7 | N | 0 | FW68A0Q | FW68A0F | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A39 | 08 | 45 | 6" | FW | 68A39 | PEB-69 | N | 0 | FW68A0F | FW68A10 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A42 | 08 | 45 | 1-1/2" | FW | 68A42 | B-7 | N | 0 | FW68A38 | 45-HR-6803 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A44 | 08 | 45 | 6" | FW | 68A44 | PEB-69 | N | 0 | FW68A17 | FW68A0O | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A49 | 08 | 45 | 6" | FW | 68A49 | PEB-69 | N | 0 | FW68A46 | FW68A0J | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A54 | 08 | 45 | 8" | FW | 68A54 | B-7 | N | 0 | FW68B93 | FW68D09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A55 | 08 | 45 | 10" | FW | 68A55 | PEB-69 | N | 0 | FW68B03 | FW68B92 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A56 | 08 | 45 | 3/4" | FW | 68A56 | B-7 | N | 0 | FW68B92 | FW68D09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A57 | 08 | 45 | 6" | FW | 68A57 | PEB-69 | N | 0 | FW68A10 | FW68A0R | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A59 | 08 | 45 | 6" | FW | 68A59 | PEB-69 | N | 0 | FW68A10 | FW68A0E | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A61 | 08 | 45 | 6" | FW | 68A61 | PEB-69 | N | 0 | FW68A10 | FW68A0C | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A66 | 08 | 45 | 12" | FW | 68A66 | B-7 | N | 0 | FW68A0H | FW68C01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A68 | 08 | 45 | 12" | FW | 68A68 | B-7 | N | 0 | FW68A0I | FW68C01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A71 | 08 | 45 | 1-1/2" | FW | 68A71 | B-13 | N | 0 | FW68A34 | 45-HR-6851 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
BDL65003 | 08 | 32 | 2" | BDL | 65003 | B4S1 | N | 0 | BDL65002 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL65005 | 08 | 32 | 1-1/2" | BDL | 65005 | B4S1 | N | 0 | BDL65002 | BDL65001 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 1 | N | 32-P-031-01 |  | G | N | 141 | N | 470 | ,10
BDL71021 | 08 | 32 | 1" | BDL | 71021 | B4S1 | N | 0 | ET71037 | BDL71034 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71025 | 08 | 32 | 1" | BDL | 71025 | B4S1 | N | 0 | BDL71035 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71026 | 08 | 32 | 2" | BDL | 71026 | B4S1 | N | 0 | ET71076 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71026 | 08 | 32 | 3" | BDL | 71026 | B4S1 | N | 0 | ET71076 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71027 | 08 | 32 | 1-1/2" | BDL | 71027 | B4S1 | N | 0 | ET71077 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71028 | 08 | 32 | 1/2" | BDL | 71028 | B4S1 | N | 0 | ET71082 | BDL71027 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71030 | 08 | 32 | 4" | BDL | 71030 | B4S1 | N | 0 | BDL71039 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-P-006-02 |  | G | N | 141 | N | 470 | ,10
BDL71031 | 08 | 32 | 1/2" | BDL | 71031 | B4S1 | N | 0 | ET71081 | BDL71027 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.49 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71033 | 08 | 32 | 2" | BDL | 71033 | B4S1 | N | 0 | ET71074 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71033 | 08 | 32 | 3" | BDL | 71033 | B4S1 | N | 0 | ET71074 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71034 | 08 | 32 | 1" | BDL | 71034 | B4S1 | N | 0 | ET71061 | BDL71041 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.49 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71035 | 08 | 32 | 1" | BDL | 71035 | B4S1 | N | 0 | ET71058 | BDL71025 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.49 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71036 | 08 | 32 | 4" | BDL | 71036 | B4S1 | N | 0 | ET71064 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71039 | 08 | 32 | 1" | BDL | 71039 | B4S1 | N | 0 | ET71079 | BDL71030 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71041 | 08 | 32 | 3" | BDL | 71041 | B4S1 | N | 0 | TP-14 (FL710121) | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL72001 | 08 | 32 | 1/2" | BDL | 72001 | B32S1 | N | 0 | PR72016 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72020 | 08 | 32 | 3/4" | BDL | 72020 | B32S1 | N | 0 | PR72040 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
FW68F30 | 08 | 32 | 4" | FW | 68F30 | B-13 | N | 0 | FW68R08 | DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68G02 | 08 | 45 | 3" | FW | 68G02 | B-13 | N | 0 | FW68G10 | FW68G10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G08 | 08 | 45 | 1" | FW | 68G08 | B-13 | N | 0 | FW68D08 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G08 | 08 | 45 | 3" | FW | 68G08 | B-13 | N | 0 | FW68D08 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G10 | 08 | 45 | 1" | FW | 68G10 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G10 | 08 | 45 | 3" | FW | 68G10 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G15 | 08 | 45 | 3" | FW | 68G15 | B-13 | N | 0 | FW68G22 | FW68G22 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68G21 | 08 | 45 | 2" | FW | 68G21 | B-13 | N | 0 | FW68D07 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68G22 | 08 | 45 | 2" | FW | 68G22 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68G41 | 08 | 45 | 2" | FW | 68G41 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68G44 | 08 | 45 | 1" | FW | 68G44 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68G44 | 08 | 45 | 3" | FW | 68G44 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
IA69P02 | 08 | 32 | 1/2" | IA | 69P02 | B-13 | N | 0 | IA69P03 | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.10 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-03 |  | - | N | 000 | - | 200
IA71005 | 08 | 32 | 1-1/2" | IA | 71005 | B-13 | N | 0 | IA62056 | N72008 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.48 | 2 | Art 4.3 | NA | N | 4 | N | 32-P-007-05 |  | - | N | 000 | - | 200
IA68F02 | 08 | 32 | 1" | IA | 68F02 | B-13 | N | 0 | IA68R10 | IA68F03 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | N | 000 | - | 200
IA68F03 | 08 | 32 | 1" | IA | 68F03 | B-13 | N | 0 | IA68F02 | IA68F02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | N | 000 | - | 200
IA68H01 | 08 | 32 | 1" | IA | 68H01 | B-13 | N | 0 | IA68H02 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H09 | 08 | 32 | 1" | IA | 68H09 | B-13 | N | 0 | IA68H11 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H14 | 08 | 32 | 1" | IA | 68H14 | B-13 | N | 0 | IA68H12 | IA68H22 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H15 | 08 | 32 | 1" | IA | 68H15 | B-13 | N | 0 | IA68C09 | SPINKLER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H16 | 08 | 32 | 1" | IA | 68H16 | B-13 | N | 0 | IA68H12 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H18 | 08 | 32 | 1" | IA | 68H18 | B-13 | N | 0 | IA68H24 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H19 | 08 | 32 | 1" | IA | 68H19 | B-13 | N | 0 | IA68H24 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68H24 | 08 | 32 | 1" | IA | 68H24 | B-13 | N | 0 | IA68C09 | IA68H17 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I02 | 08 | 32 | 1" | IA | 68I02 | B-13 | N | 0 | IA68I13 | - | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I04 | 08 | 32 | 1" | IA | 68I04 | B-13 | N | 0 | IA68I09 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I11 | 08 | 32 | 1" | IA | 68I11 | B-13 | N | 0 | IA68I14 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I12 | 08 | 32 | 1" | IA | 68I12 | B-13 | N | 0 | GLASS BULB | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I13 | 08 | 32 | 1" | IA | 68I13 | B-13 | N | 0 | IA68I03 | IA68I02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I14 | 08 | 32 | 1" | IA | 68I14 | B-13 | N | 0 | IA68I03 | IA68I11 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I20 | 08 | 32 | 1" | IA | 68I20 | B-13 | N | 0 | IA68C10 | IA68I23 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I23 | 08 | 32 | 1" | IA | 68I23 | B-13 | N | 0 | IA68I20 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I24 | 08 | 32 | 1" | IA | 68I24 | B-13 | N | 0 | GLASS BULB | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
CO26037 | 08 | 32 | 1/2" | CO | 26037 | 1IS5 | N | 0 | 2 ND. EMERGENCY KILLER SYSTEM | CO26030 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26040 | 08 | 32 | 1/2" | CO | 26040 | 1IS5 | N | 0 | 2 ND. EMERGENCY KILLER SYSTEM | CO26030 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO31001 | 08 | 32 | 1/2" | CO | 31001 | 1IS5 | N | 0 | CO31002 | CO2819 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
HCM23062 | 08 | 32 | 1/2" | HCM | 23062 | 1FS4 | N | 0 | HCM23061 | HCM23070 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23064 | 08 | 32 | 1/2" | HCM | 23064 | 1FS4 | N | 0 | HCM23063 | VZ23003 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23065 | 08 | 32 | 3/4" | HCM | 23065 | C42S1 | HB | 30 | HCM23004 | HCM24095 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15A | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23065 | 08 | 32 | 3" | HCM | 23065 | C42S1 | HB | 40 | HCM23004 | HCM24095 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15A | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23066 |  | 32 | 1/2" | HCM | 23066 | 1FS4 | JP | 0 | 32-R-2300 | 32-PDT-2301 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23066 |  | 32 | 1" | HCM | 23066 | 1FS4 | JP | 0 | 32-R-2300 | 32-PDT-2301 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23067 | 08 | 32 | 1/2" | HCM | 23067 | 1FS4 | N | 0 | JLS23016 | LS23024 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23068 |  | 32 | 1/2" | HCM | 23068 | 1FS4 | JP | 0 | HCM23070 | HCM23067 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23068 |  | 32 | 3/4" | HCM | 23068 | 1FS4 | JP | 0 | HCM23070 | HCM23067 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23069 |  | 32 | 3/4" | HCM | 23069 | C42S1 | HB | 30 | HCM23004 | P23017 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23069 |  | 32 | 2" | HCM | 23069 | C42S1 | HB | 40 | HCM23004 | P23017 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23070 | 08 | 32 | 1/2" | HCM | 23070 | 1FS4 | N | 0 | LS63147 | 32-R-2300 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23070 |  | 32 | 1" | HCM | 23070 | 1FS4 | JP | 0 | LS63147 | 32-R-2300 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23071 |  | 32 | 1/2" | HCM | 23071 | 3FS4 | HB | 30 | HCM24061 | PR23012 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23072 |  | 32 | 1/2" | HCM | 23072 | 3FS4 | HB | 30 | HCM24061 | HCM23075 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23073 | 08 | 32 | 1/2" | HCM | 23073 | D20S1 | N | 0 | HCM24089 | BDL23059 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM23074 |  | 32 | 1/2" | HCM | 23074 | 3FS4 | HB | 30 | HCM23072 | PR24041 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
BDL23025 | 08 | 32 | 1" | BDL | 23025 | B32S1 | N | 0 | P23021 | BDL23043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23027 | 08 | 32 | 1/2" | BDL | 23027 | B32S1 | N | 0 | P23020 | BDL24069 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23027 | 08 | 32 | 3/4" | BDL | 23027 | B32S1 | N | 0 | P23020 | BDL24069 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23028 |  | 32 | 1" | BDL | 23028 | B32S1 | ST | 30 | HCM23018 | BDL23043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23043 | 08 | 32 | 1/2" | BDL | 23043 | B32S1 | N | 0 | BDL23025 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23044 | 08 | 32 | 1" | BDL | 23044 | B32S1 | N | 0 | PR23032 | BDL31031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23045 | 08 | 32 | 2" | BDL | 23045 | B32S1 | N | 0 | HCM23059 | BDL23046 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23046 |  | 32 | 12" | BDL | 23046 | B32S1 | SB | 100 | HCM23058 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23047 | 08 | 32 | 10" | BDL | 23047 | B32S1 | N | 0 | HCM23046 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23048 | 08 | 32 | 2" | BDL | 23048 | B32S1 | N | 0 | HCM23045 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23048 | 08 | 32 | 4" | BDL | 23048 | B32S1 | N | 0 | HCM23045 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23049 | 08 | 32 | 3/4" | BDL | 23049 | B32S1 | N | 0 | HCM32019 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23049 | 08 | 32 | 1" | BDL | 23049 | B32S1 | N | 0 | HCM32019 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23050 | 08 | 32 | 2" | BDL | 23050 | B32S1 | N | 0 | TP-7 (PR230104) | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23051 |  | 32 | 1/2" | BDL | 23051 | B32S1 | ET | 30 | HCM22003 | BDL22019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | Art 4.3 | NA | N | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23053 | 08 | 32 | 3/4" | BDL | 23053 | B32S1 | N | 0 | HCM23069 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23054 | 08 | 32 | 1" | BDL | 23054 | B32S1 | N | 0 | PR22015 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL23055 | 08 | 32 | 3/4" | BDL | 23055 | B32S1 | N | 0 | BDL24083 | BDL60061 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FO10002 | 08 | 32 | 1/2" | FO | 10002 | 3DS3 | N | 0 | TEA10007 | FO10001 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.4 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO10011 | 08 | 32 | 1/2" | FO | 10011 | 3DS3 | N | 0 | VG15B09 | FO11005 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11001 | 08 | 32 | 1/2" | FO | 11001 | 3DS3 | N | 0 | TEA10001 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11002 | 08 | 32 | 1" | FO | 11002 | 3DS3 | N | 0 | 32-D-1100 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11003 |  | 32 | 3/4" | FO | 11003 | 1CS2 | ET | 30 | O66039 | FO11021 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11003 | 08 | 32 | 1" | FO | 11003 | 1CS2 | N | 0 | O66039 | FO11021 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11007 | 08 | 32 | 3/4" | FO | 11007 | B4S2 | N | 0 | 32-P-1101 | FO11023 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
JLS31006 |  | 32 | 1" | JLS | 31006 | B-5 | HB | 50 | JLS31008 | PR31015 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31006 |  | 32 | 3" | JLS | 31006 | B-5 | HB | 50 | JLS31008 | PR31015 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31008 | 08 | 32 | 1-1/2" | JLS | 31008 | B-5 | HB | 50 | LS31019 | JLS31006 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31009 |  | 32 | 3" | JLS | 31009 | B-5 | HB | 50 | PR31017 | PR31017 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31010 |  | 32 | 3" | JLS | 31010 | B-5 | HB | 50 | PR31022 | PR31016 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31011 | 08 | 32 | 3" | JLS | 31011 | B-5 | HB | 50 | JLS31011 | PR31014 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31012 |  | 32 | 3" | JLS | 31012 | B-5 | HB | 50 | PR31024 | PR31018 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | E | N | 000 | N | 111 | 1
JLS32002 |  | 32 | 2" | JLS | 32002 | B-5 | HB | 50 | LS63133 | LS32001 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | E | N | 000 | N | 111 | 1
JLS34001 | 08 | 32 | 3" | JLS | 34001 | B-5 | HB | 50 | LS63032 | JLS31011 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS50005 |  | 32 | 16" | JLS | 50005 | B-5 | HB | 40 | LS50032 | LS50047 | 1.0/-1.0 | 280.0/280.0 | 0.5 | 110.0 |  | 1.61 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 108
JLS61001 |  | 32 | 1" | JLS | 61001 | B-5 | HB | 50 | LS63049 | LS61001 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.42 | 2 | I | MOD.A | Y | 20 | N | 32-U-023-02 |  | E | N | 000 | N | 111 | 1
JLS66001 |  | 32 | 6" | JLS | 66001 | B-5 | HB | 60 | LS66003 | LS66001 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.46 | 2 | I | MOD.A | Y | 20 | N | 32-P-021-03 |  | E | N | 000 | N | 111 | 1
JLS73005 |  | 32 | 3" | JLS | 73005 | B-5 | HB | 50 | BU73045 | BU73044 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.55 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-001-02 |  | E | N | 000 | N | 111 | 1
JW73001 | 08 | 32 | 3" | JW | 73001 | B-1 | N | 0 | BU73040 | BU73040 | 9.0 | 175.0 | 7.0 | 80.0 |  | 13.53 | 29.4 | H | JACKET WATER | L | - | - | >1.5 | 80 | sh.55 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | E | N | 000 | N | 88
JWR14001 | 08 | 32 | 3/4" | JWR | 14001 | B-1 | N | 0 | 32-E-1451 | JWR14003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.7 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR14002 | 08 | 32 | 1" | JWR | 14002 | B-1 | N | 0 | 32-E-1450A | JWR14003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.7 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PN80005 | 7A | 32 | 3" | PN | 80005 | 1CS2 | HB | 40 | 32-V-8000A | P52010 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.56 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-01 |  | M | N | 000 | N | 152
PN80006 | 08 | 32 | 6" | PN | 80006 | 1CS2 | N | 0 | 32-H-8001 | P52010 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 152
PN80007 | 7A | 32 | 3" | PN | 80007 | 1CS2 | HB | 40 | 32-V-8000B | P52010 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.56 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-01 |  | M | N | 000 | N | 152
PP80002 | 08 | 32 | 14" | PP | 80002 | 5CS7 | N | 0 | 32-D-8002A | 32-ZF-8100A | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.58 | 1 | II | MOD.A2 | Y | NR | N | 32-P-060-01 |  | M | N | 110 | N | 439 | 6,23,25
PP81003 | 08 | 32 | 18" | PP | 81003 | 5CS7 | N | 0 | 32-ZF-8108 | TP-N11201 (32-H-8901) | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.59 | 1 | III | MOD.G | Y | NR | N | 32-P-070-01 |  | M | N | 110 | N | 439 | 6,23,25
PP81005 | 08 | 32 | 14" | PP | 81005 | 5CS7 | N | 0 | 32-Z-8110 | 32-ZF-8108 | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.59 | 1 | II | MOD.A2 | Y | NR | N | 32-P-061-01 |  | M | N | 110 | N | 439 | 6,23,25
PP81010 | 08 | 32 | 8" | PP | 81010 | 5CS7 | N | 0 | TP-081 (32-VM-8160) | 32-D-8007 | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.62 | 1 | II | MOD.A2 | Y | NR | N | 32-P-082-07 |  | M | N | 110 | N | 439 | 6,23,25
PP83004 | 08 | 32 | 8" | PP | 83004 | 5CS7 | N | 0 | 32-PK-8300 | PP81003 | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.63 | 1 | II | MOD.A2 | Y | NR | N | 32-P-070-01 |  | M | N | 110 | N | 439 | 6,23,25
PP89010 | 08 | 32 | 18" | PP | 89010 | 5CS7 | N | 0 | TP-N51103 (D-8901) | 32-D-8007 | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.67 | 1 | NA | NA | NA | NR | N | 32-P-080-01 |  | M | N | 110 | N | 443 | 6,25,23
PP89013 | 08 | 32 | 12" | PP | 89013 | 5CS7 | N | 0 | TP-N50406 (A-8900) | COLLECTING BOX AT GROUND FLOOR | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.68M | 1 | NA | NA | NA | NR | N | 32-P-070-07 |  | M | N | 110 | N | 443 | 6,25,23
PR00001 | 08 | 32 | 1" | PR | 00001 | B4S1 | N | 0 | 32-AH-0001 | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.109 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
N67062 | 08 | 32 | 1" | N | 67062 | B-1 | N | 0 | N67017 | 32-D-5101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 000 | N | 140
N67063 | 08 | 32 | 1" | N | 67063 | B-1 | N | 0 | N67017 | 32-D-5102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 000 | N | 140
N67064 | 08 | 32 | 1-1/2" | N | 67064 | B-1 | N | 0 | N67020 | N52041 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67066 | 08 | 32 | 1/2" | N | 67066 | B-1 | N | 0 | N67020 | 32-T-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 140
N67066 | 08 | 32 | 2" | N | 67066 | B-1 | N | 0 | N67020 | 32-T-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 140
N67067 | 08 | 32 | 3/4" | N | 67067 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67068 | 08 | 32 | 1-1/2" | N | 67068 | B-1 | N | 0 | N67003 | TP-009 (N720148) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67070 | 08 | 32 | 1" | N | 67070 | B-1 | N | 0 | N67013 | N01215 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67071 | 08 | 32 | 1/2" | N | 67071 | B-1 | N | 0 | N67013 | N63001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67072 | 08 | 32 | 1-1/2" | N | 67072 | B-1 | N | 0 | N01001 | TP-6 (PR230105) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67073 | 08 | 32 | 1/2" | N | 67073 | B-1 | N | 0 | N67020 | TP-6 (N240173) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67074 | 08 | 32 | 3/4" | N | 67074 | B-1 | N | 0 | N67079 | N80020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67076 | 08 | 32 | 3/4" | N | 67076 | B-1 | N | 0 | N67079 | N80021 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67077 | 08 | 32 | 1" | N | 67077 | B-1 | N | 0 | N67079 | N80015 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67078 | 08 | 32 | 1" | N | 67078 | B-1 | N | 0 | N67017 | 32-D-6500 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67079 | 08 | 32 | 1-1/2" | N | 67079 | B-1 | N | 0 | N67029 | N67075 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67080 | 08 | 32 | 3/4" | N | 67080 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67085 | 08 | 32 | 3/4" | N | 67085 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67087 | 08 | 32 | 3/4" | N | 67087 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67089 | 08 | 32 | 3/4" | N | 67089 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
JWS64029 | 08 | 32 | 1" | JWS | 64029 | B-1 | N | 0 | JWS64054 | 32-E-5001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64029 | 08 | 32 | 8" | JWS | 64029 | B-1 | N | 0 | JWS64054 | 32-E-5001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64030 | 08 | 32 | 2" | JWS | 64030 | B-1 | N | 0 | JWS64058 | E-5103 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64030 | 08 | 32 | 3" | JWS | 64030 | B-1 | N | 0 | JWS64058 | E-5103 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64031 | 08 | 32 | 4" | JWS | 64031 | B-1 | N | 0 | JWS64054 | 32-E-5201 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64033 | 08 | 32 | 2" | JWS | 64033 | B-1 | N | 0 | JWS64014 | JWS71001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64033 | 08 | 32 | 3" | JWS | 64033 | B-1 | N | 0 | JWS64014 | JWS71001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64035 | 08 | 32 | 2" | JWS | 64035 | B-1 | N | 0 | JWS64056 | TP-007 (JWS720141) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64037 | 08 | 32 | 1" | JWS | 64037 | B-1 | N | 0 | JWS64056 | JW73001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64038 | 08 | 32 | 1" | JWS | 64038 | B-1 | N | 0 | JWS64056 | TP-013, (JWS620138) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64039 | 08 | 32 | 6" | JWS | 64039 | B-1 | N | 0 | JWS64056 | 32-E-6300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64039 | 08 | 32 | 8" | JWS | 64039 | B-1 | N | 0 | JWS64056 | 32-E-6300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64040 | 08 | 32 | 1" | JWS | 64040 | B-1 | N | 0 | JWS64052 | TP-5 (Z-2012) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64047 | 08 | 32 | 3" | JWS | 64047 | B-1 | N | 0 | JWS64054 | 32-E-2300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64047 | 08 | 32 | 14" | JWS | 64047 | B-1 | N | 0 | JWS64054 | 32-E-2300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64048 | 08 | 32 | 2" | JWS | 64048 | B-1 | N | 0 | JWS64072 | TP-3 (JWS230100) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64049 | 08 | 32 | 1" | JWS | 64049 | B-1 | N | 0 | JWS64054 | 32-E-2401 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64049 | 08 | 32 | 10" | JWS | 64049 | B-1 | N | 0 | JWS64054 | 32-E-2401 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64049 | 08 | 32 | 12" | JWS | 64049 | B-1 | N | 0 | JWS64054 | 32-E-2401 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64050 | 08 | 32 | 1" | JWS | 64050 | B-1 | N | 0 | JWS64059 | TP-12 (JWS240150) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
N89050 | 08 | 32 | 3/4" | N | 89050 | B-1 | N | 0 | N89069 | N81050 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89051 | 08 | 32 | 3/4" | N | 89051 | B-1 | N | 0 | N89012 | N81048 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89052 | 08 | 32 | 3/4" | N | 89052 | B-1 | N | 0 | N89067 | 32-S-8123 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89053 | 08 | 32 | 3/4" | N | 89053 | B-1 | N | 0 | N89067 | 32-S-8124 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89055 | 08 | 32 | 3/4" | N | 89055 | B-1 | N | 0 | N89069 | N81044 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89056 | 08 | 32 | 3/4" | N | 89056 | B-1 | N | 0 | N89067 | N89052 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89057 | 08 | 32 | 3/4" | N | 89057 | B-1 | N | 0 | N89069 | N81040 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89059 | 08 | 32 | 3/4" | N | 89059 | B-1 | N | 0 | N89069 | N81043 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89060 | 08 | 32 | 1/2" | N | 89060 | B-1 | N | 0 | N89068 | N89005 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89061 | 08 | 32 | 1/2" | N | 89061 | B-1 | N | 0 | N89069 | N81055 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89064 | 08 | 32 | 1/2" | N | 89064 | B-1 | N | 0 | N89012 | N81057 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89065 | 08 | 32 | 1/2" | N | 89065 | B-1 | N | 0 | N89069 | N81053 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89066 | 08 | 32 | 1/2" | N | 89066 | B-1 | N | 0 | N89069 | N81054 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89067 | 08 | 32 | 2" | N | 89067 | B-1 | N | 0 | N89034 | N89053 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89068 | 08 | 32 | 2" | N | 89068 | B-1 | N | 0 | N89034 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89069 | 08 | 32 | 1-1/2" | N | 89069 | B-1 | N | 0 | N89068 | N89059 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89071 | 08 | 32 | 3" | N | 89071 | B-1 | N | 0 | N01001 | N80011 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N89072 | 08 | 32 | 1/2" | N | 89072 | B-1 | N | 0 | N01001 | 32-AFR-5212 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-03 |  | E | N | 000 | N | 140
N89098 | 08 | 32 | 1/2" | N | 89098 | B-1 | N | 0 | N01001 | N6700K | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
PR34029 |  | 32 | 1" | PR | 34029 | QXB26S1 | ET | 30 | PR34017 | OTHER SECTIONS | 8.0/8.0 | 200.0/-45.0 | 5.0 | 80.0 |  | 12.83 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 27 | N | 32-P-048-01 |  | G | N | 141 | N | 392 | 10
BDL33017 | 08 | 32 | 3/4" | BDL | 33017 | B32S1 | N | 0 | PR33022 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33018 | 08 | 32 | 1/2" | BDL | 33018 | B32S1 | N | 0 | PR33021 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33018 | 08 | 32 | 1" | BDL | 33018 | B32S1 | N | 0 | PR33021 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33021 | 08 | 32 | 2" | BDL | 33021 | B32S1 | N | 0 | PR33032 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33022 | 08 | 32 | 1" | BDL | 33022 | B32S1 | N | 0 | PR33012 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL34012 | 08 | 32 | 10" | BDL | 34012 | B32S1 | N | 0 | PR34015 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL34013 | 08 | 32 | 3/4" | BDL | 34013 | B4S1 | N | 0 | PR34001 | BDL34018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34013 | 08 | 32 | 14" | BDL | 34013 | B4S1 | N | 0 | PR34001 | BDL34018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34014 | 08 | 32 | 2" | BDL | 34014 | B4S1 | N | 0 | BDL31030 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34014 | 08 | 32 | 3" | BDL | 34014 | B4S1 | N | 0 | BDL31030 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34015 | 08 | 32 | 3/4" | BDL | 34015 | B32S1 | N | 0 | PR34021 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.26 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL34015 | 08 | 32 | 1" | BDL | 34015 | B32S1 | N | 0 | PR34021 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.26 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL34016 | 08 | 32 | 3/4" | BDL | 34016 | B4S1 | N | 0 | BDL34017 | BDL60037 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34016 | 08 | 32 | 2" | BDL | 34016 | B4S1 | N | 0 | BDL34017 | BDL60037 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34017 | 08 | 32 | 2" | BDL | 34017 | B4S1 | N | 0 | PR34027 | BDL34016 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34018 | 08 | 32 | 8" | BDL | 34018 | B4S1 | N | 0 | BDL34013 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34018 | 08 | 32 | 16" | BDL | 34018 | B4S1 | N | 0 | BDL34013 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL35008 | 08 | 32 | 3/4" | BDL | 35008 | B4S1 | N | 0 | PR36012 | BDL60031 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.27 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL35009 | 08 | 32 | 6" | BDL | 35009 | B4S1 | N | 0 | PR35015 | BDL60031 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
FW68A74 | 08 | 45 | 1-1/2" | FW | 68A74 | B-13 | N | 0 | FW68A34 | 45-HR-6854 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A75 | 08 | 45 | 1-1/2" | FW | 68A75 | B-13 | N | 0 | FW68A34 | 45-HR-6855 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A76 | 08 | 45 | 1-1/2" | FW | 68A76 | B-13 | N | 0 | FW68A34 | 45-HR-6856 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A77 | 08 | 45 | 1-1/2" | FW | 68A77 | B-13 | N | 0 | FW68A34 | 45-HR-6857 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A79 | 08 | 45 | 1-1/2" | FW | 68A79 | B-13 | N | 0 | FW68A26 | 45-HR-6859 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A81 | 08 | 45 | 1-1/2" | FW | 68A81 | B-13 | N | 0 | FW68A26 | 45-HR-6861 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A82 | 08 | 45 | 1-1/2" | FW | 68A82 | B-13 | N | 0 | FW68A26 | 45-HR-6862 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A87 | 08 | 45 | 6" | FW | 68A87 | PEB-69 | N | 0 | FW68A03 | FW68A0S | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A91 | 08 | 45 | 6" | FW | 68A91 | UGB-1PE | N | 0 | FW68A06 | 45-HY-6802 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A93 | 08 | 45 | 6" | FW | 68A93 | UGB-1PE | N | 0 | FW68A35 | 45-HM-6811 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A94 | 08 | 45 | 6" | FW | 68A94 | UGB-1PE | N | 0 | FW68A23 | 45-HM-6801 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A95 | 08 | 45 | 12" | FW | 68A95 | UGB-1PE | N | 0 | FW68A21 | FW68A22 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A96 | 08 | 45 | 16" | FW | 68A96 | UGB-1PE | N | 0 | FW68A18 | FW68A19 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A97 | 08 | 45 | 8" | FW | 68A97 | UGB-1PE | N | 0 | FW68A33 | FW68A34 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A99 | 08 | 45 | 6" | FW | 68A99 | UGB-1PE | N | 0 | FW68A27 | 45-HM-6802 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B03 | 08 | 45 | 16" | FW | 68B03 | PEB-69 | N | 0 | FW68A03 | FW68A55 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B04 | 08 | 45 | 6" | FW | 68B04 | PEB-69 | N | 0 | FW68A03 | FW68B0C | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B0D | 08 | 45 | 6" | FW | 68B0D | UGB-1PE | N | 0 | FW68B06 | FW68A88 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0G | 08 | 45 | 6" | FW | 68B0G | UGB-1PE | N | 0 | FW68B44 | FW68B43 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0H | 08 | 45 | 8" | FW | 68B0H | UGB-1PE | N | 0 | FW68B47 | FW68B48 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
BDL72020 | 08 | 32 | 2" | BDL | 72020 | B32S1 | N | 0 | PR72040 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72021 | 08 | 32 | 1" | BDL | 72021 | B32S1 | N | 0 | BDL72022 | BDL72026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72022 | 08 | 32 | 3/4" | BDL | 72022 | B32S1 | N | 0 | PR72009 | BDL72021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72023 | 08 | 32 | 1" | BDL | 72023 | B32S1 | N | 0 | PR72038 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72023 | 08 | 32 | 6" | BDL | 72023 | B32S1 | N | 0 | PR72038 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72025 | 08 | 32 | 3/4" | BDL | 72025 | B32S1 | N | 0 | PR72028 | BDL72026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72026 | 08 | 32 | 1" | BDL | 72026 | B32S1 | N | 0 | PR72050 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72026 | 08 | 32 | 1-1/2" | BDL | 72026 | B32S1 | N | 0 | PR72050 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72027 | 08 | 32 | 2" | BDL | 72027 | B32S1 | N | 0 | PR01001 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
CWS86022 | 08 | 32 | 1/2" | CWS | 86022 | B-1 | N | 0 | CWS64010 | 32-FT-8601 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89031 | 08 | 32 | 4" | CWS | 89031 | B-1 | N | 0 | CWS64010 | TP-N60103 (32-E-8906) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89032 | 08 | 32 | 4" | CWS | 89032 | B-1 | N | 0 | CWS64010 | TP-N20401 (32-E-8902) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89032 | 08 | 32 | 6" | CWS | 89032 | B-1 | N | 0 | CWS64010 | TP-N20401 (32-E-8902) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89035 | 08 | 32 | 2" | CWS | 89035 | B-1 | N | 0 | CWS64010 | TP-N21105 (E-8903) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89038 | 08 | 32 | 4" | CWS | 89038 | B-1 | N | 0 | CWS64010 | CWS89050 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
FW68G48 | 08 | 45 | 1" | FW | 68G48 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68G48 | 08 | 45 | 2" | FW | 68G48 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68G49 | 08 | 45 | 1" | FW | 68G49 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68G49 | 08 | 45 | 3" | FW | 68G49 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68H01 | 08 | 32 | 1" | FW | 68H01 | B-13 | N | 0 | FW68H02 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H14 | 08 | 32 | 1-1/2" | FW | 68H14 | B-13 | N | 0 | FW68H15 | FW68H17 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H17 | 08 | 32 | 1-1/2" | FW | 68H17 | B-13 | N | 0 | FW68H14 | FW68H18 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H19 | 08 | 32 | 1" | FW | 68H19 | B-13 | N | 0 | FW68H20 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H21 | 08 | 32 | 1-1/2" | FW | 68H21 | B-13 | N | 0 | FW68H26 | FW68H24 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H23 | 08 | 32 | 1" | FW | 68H23 | B-13 | N | 0 | FW68H27 | FW68H25 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H26 | 08 | 32 | 1-1/2" | FW | 68H26 | B-13 | N | 0 | FW68H27 | FW68H21 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H31 | 08 | 32 | 1" | FW | 68H31 | B-13 | N | 0 | FW68H29 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H36 | 08 | 32 | 1" | FW | 68H36 | B-13 | N | 0 | FW68H35 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H37 | 08 | 32 | 1" | FW | 68H37 | B-13 | N | 0 | FW68H39 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H38 | 08 | 32 | 1" | FW | 68H38 | B-13 | N | 0 | FW68H49 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H39 | 08 | 32 | 1-1/2" | FW | 68H39 | B-13 | N | 0 | FW68H34 | FW68H37 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H56 | 08 | 32 | 1-1/2" | FW | 68H56 | B-13 | N | 0 | FW68H58 | FW68H55 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H57 | 08 | 32 | 1" | FW | 68H57 | B-13 | N | 0 | FW68H59 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
BU73041 | 08 | 32 | 2" | BU | 73041 | D20S1 | N | 0 | JW73001 | 32-D-7302 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73043 |  | 32 | 1" | BU | 73043 | B32S1 | HB | 30 | 32-D-7302 | BDL73078 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73043 |  | 32 | 2" | BU | 73043 | B32S1 | HB | 30 | 32-D-7302 | BDL73078 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73044 |  | 32 | 1-1/2" | BU | 73044 | B32S1 | HB | 30 | JLS73005 | 32-D-7302 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | I | MOD.A | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73045 | 08 | 32 | 3/4" | BU | 73045 | B32S1 | N | 0 | BU73047 | JLS73005 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73046 | 08 | 32 | 1" | BU | 73046 | B32S1 | N | 0 | JLS73005 | JLS73005 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | A | N | 140 | N | 733 | 15
BU73047 | 08 | 32 | 1/2" | BU | 73047 | B32S1 | N | 0 | 32-S-7302A | 32-D-7302 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73047 | 08 | 32 | 1" | BU | 73047 | B32S1 | N | 0 | 32-S-7302A | 32-D-7302 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73049 | 08 | 32 | 1" | BU | 73049 | B32S1 | N | 0 | 32-D-7302 | 32-P-7300 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73049 | 08 | 32 | 3" | BU | 73049 | B32S1 | N | 0 | 32-D-7302 | 32-P-7300 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73050 | 08 | 32 | 1/2" | BU | 73050 | D20S1 | N | 0 | 32-D-7302 | 32-P-7300 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 153.15 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73050 | 08 | 32 | 1-1/2" | BU | 73050 | D20S1 | N | 0 | 32-D-7302 | 32-P-7300 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 153.15 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73051 | 08 | 32 | 1/2" | BU | 73051 | D20S1 | N | 0 | 32-P-7300 | BU73053 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
IA68I25 | 08 | 32 | 1" | IA | 68I25 | B-13 | N | 0 | IA68I20 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68K03 | 08 | 32 | 1" | IA | 68K03 | B-13 | N | 0 | IA68K11 | IA68K06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-17 |  | - | N | 000 | - | 200
IA68K07 | 08 | 32 | 1" | IA | 68K07 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68N05 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68K09 | 08 | 32 | 1" | IA | 68K09 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68K11 | 08 | 32 | 1-1/2" | IA | 68K11 | B-13 | N | 0 | 20 LTR TANK | IA68K01 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-17 |  | - | N | 000 | - | 200
IA68L03 | 08 | 32 | 1" | IA | 68L03 | B-13 | N | 0 | IA68K10 | IA68L02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68L04 | 08 | 32 | 1" | IA | 68L04 | B-13 | N | 0 | IA68K10 | IA68L20 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68L21 | 08 | 32 | 1" | IA | 68L21 | B-13 | N | 0 | FUSIBLE GLASS BULB | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68M01 | 08 | 32 | 1" | IA | 68M01 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M02 | 08 | 32 | 1" | IA | 68M02 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M03 | 08 | 32 | 1" | IA | 68M03 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M04 | 08 | 32 | 1" | IA | 68M04 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M08 | 08 | 32 | 1" | IA | 68M08 | B-13 | N | 0 | IA68M24 | IA68M01 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M10 | 08 | 32 | 1" | IA | 68M10 | B-13 | N | 0 | IA68M27 | IA68M27 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M18 | 08 | 32 | 1" | IA | 68M18 | B-13 | N | 0 | IA68M19 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M19 | 08 | 32 | 1" | IA | 68M19 | B-13 | N | 0 | IA68K08 | IA68M28 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M24 | 08 | 32 | 1" | IA | 68M24 | B-13 | N | 0 | SWIVEL JOINT | IA68M08 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M31 | 08 | 32 | 1" | IA | 68M31 | B-13 | N | 0 | IA68M29 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M63 | 08 | 32 | 1" | IA | 68M63 | B-13 | N | 0 | IA68K08 | IA68M65 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
FL01001 | 08 | 32 | 3/4" | FL | 01001 | B32S1 | N | 0 | FL60002 | NF050016 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
FL01001 | 08 | 32 | 8" | FL | 01001 | B32S1 | N | 0 | FL60002 | NF050016 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
HCM23075 |  | 32 | 1" | HCM | 23075 | 3FS4 | HB | 30 | HCM23072 | PR24043 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.15 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23078 | 08 | 32 | 1-1/2" | HCM | 23078 | C42S1 | N | 0 | PR24041 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.14 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23079 | 08 | 32 | 1-1/2" | HCM | 23079 | C42S1 | N | 0 | PR24043 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23080 | 08 | 32 | 1" | HCM | 23080 | C42S1 | N | 0 | PR24045 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23081 | 08 | 32 | 1" | HCM | 23081 | C42S1 | N | 0 | PR24047 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23082 |  | 32 | 1/2" | HCM | 23082 | 1FS4 | JP | 0 | JLS23021 | HCM23083 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23083 |  | 32 | 1/2" | HCM | 23083 | 1FS4 | JP | 0 | HCM23082 | HCM23086 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23085 |  | 32 | 1/2" | HCM | 23085 | D20S1 | HB | 30 | HCM23082 | 32-HV-2303B | 55.0/55.0 | 280.0/-45.0 | 30.0 | 100.0 |  | 88.69 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 321 | 10
HCM24025 | 08 | 32 | 1" | HCM | 24025 | D20S1 | N | 0 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24025 | 08 | 32 | 1-1/2" | HCM | 24025 | D20S1 | N | 0 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24025 |  | 32 | 3" | HCM | 24025 | D20S1 | P | 50 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24050 | 08 | 32 | 1" | HCM | 24050 | D20S1 | N | 0 | 32-S-2400 | BDL24073 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24051 | 08 | 32 | 1" | HCM | 24051 | 3FS4 | N | 0 | N24003 | HCM24062 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.21B | 1 | Art 4.3 | NA | N | 5 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
BDL23055 | 08 | 32 | 1" | BDL | 23055 | B32S1 | N | 0 | BDL24083 | BDL60061 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23056 | 08 | 32 | 3/4" | BDL | 23056 | B32S1 | N | 0 | HCM23060 | BDL24069 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23058 | 08 | 32 | 3/4" | BDL | 23058 | B32S1 | N | 0 | HCM24097 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23059 | 08 | 32 | 1/2" | BDL | 23059 | B32S1 | N | 0 | HCM23073 | BDL23060 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23060 | 08 | 32 | 1/2" | BDL | 23060 | B32S1 | N | 0 | FROM SAMPLE PROBE | TO SAMPLE CONDITIONING STATION | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23061 | 08 | 32 | 1/2" | BDL | 23061 | B32S1 | N | 0 | HCM23074 | BDL60029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23062 | 08 | 32 | 1/2" | BDL | 23062 | B32S1 | N | 0 | HCM23075 | BDL23061 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.15 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23063 | 08 | 32 | 1/2" | BDL | 23063 | B32S1 | N | 0 | HCM23076 | BDL43025 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.15 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23064 | 08 | 32 | 1/2" | BDL | 23064 | B32S1 | N | 0 | HCM23072 | BDL23052 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.15 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23065 | 08 | 32 | 1/2" | BDL | 23065 | B32S1 | N | 0 | 32-Z-2303B | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.15 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23067 | 08 | 32 | 1/2" | BDL | 23067 | B32S1 | N | 0 | P23031 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23067 | 08 | 32 | 3/4" | BDL | 23067 | B32S1 | N | 0 | P23031 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FO11007 | 08 | 32 | 1-1/2" | FO | 11007 | B4S2 | N | 0 | 32-P-1101 | FO11023 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11011 | 08 | 32 | 1/2" | FO | 11011 | 1CS2 | N | 0 | FO11003 | TEA11001 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11012 | 08 | 32 | 1/2" | FO | 11012 | 1CS2 | N | 0 | TEA11001 | TEA11013 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11013 | 08 | 32 | 3/4" | FO | 11013 | 3DS3 | N | 0 | TEA11014 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11014 | 08 | 32 | 1/2" | FO | 11014 | 3DS3 | N | 0 | TEA11013 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11015 | 08 | 32 | 1/2" | FO | 11015 | 3DS3 | N | 0 | TEA11004 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11018 | 08 | 32 | 1/2" | FO | 11018 | 3DS3 | N | 0 | TEA11006 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11021 |  | 32 | 1" | FO | 11021 | B4S2 | ET | 30 | 32-D-1102 | FO11006 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11022 |  | 32 | 1" | FO | 11022 | B4S2 | ET | 30 | FO11023 | FO11006 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11023 |  | 32 | 3/4" | FO | 11023 | B4S2 | ET | 30 | FO11007 | FO11022 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11024 | 08 | 32 | 1/2" | FO | 11024 | 3DS3 | N | 0 | TEA11026 | LPN11004 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO20001 | 08 | 32 | 1" | FO | 20001 | B4S2 | N | 0 | FO20003 | FO35015 | 6.0 | 100.0 | 3.0 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 212 | 23,25
FO20003 | 08 | 32 | 3/4" | FO | 20003 | B4S2 | N | 0 | TEA20004 | FO20001 | 6.0 | 100.0 | 3.0 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 212 | 23,25
FO22101 | 08 | 32 | 1/2" | FO | 22101 | B4S2 | N | 0 | 32-D-2202 | FO35015 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.13 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO35015 | 08 | 32 | 1" | FO | 35015 | B4S2 | N | 0 | FO11007 | 32-D-6500 | 6.0 | 180.0 | 0.5/0.5 | 40.0/50.0 |  | 9.03 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 210 | 23,25
FO35015 | 08 | 32 | 1-1/2" | FO | 35015 | B4S2 | N | 0 | FO11007 | 32-D-6500 | 6.0 | 180.0 | 0.5/0.5 | 40.0/50.0 |  | 9.03 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 210 | 23,25
JWR14003 | 08 | 32 | 3/4" | JWR | 14003 | B-1 | N | 0 | 32-E-1450B | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.8 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR14003 | 08 | 32 | 1" | JWR | 14003 | B-1 | N | 0 | 32-E-1450B | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.8 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR21002 | 08 | 32 | 1" | JWR | 21002 | B-1 | N | 0 | TP-6 (Z-2012) | JWR24008 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR22006 | 08 | 32 | 1" | JWR | 22006 | B-1 | N | 0 | OLIGOMER REMOVAL SYSTEM | JWR64045 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR23001 |  | 32 | 8" | JWR | 23001 | B-1 | HB | 30 | PJW23004 | JWR64003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR23002 | 08 | 32 | 14" | JWR | 23002 | B-1 | N | 0 | PJW23004 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR23004 | 08 | 32 | 3/4" | JWR | 23004 | B-1 | N | 0 | 32-E-2350 | SAFE LOCATION | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.18 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-044-04 |  | E | N | 000 | N | 11
JWR23004 | 08 | 32 | 1-1/2" | JWR | 23004 | B-1 | N | 0 | 32-E-2350 | SAFE LOCATION | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.18 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-044-04 |  | E | N | 000 | N | 11
PR01001 | 08 | 32 | 1/2" | PR | 01001 | C42S1 | N | 0 | PR01002 | 32-D-7200 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
PR01001 | 08 | 32 | 1" | PR | 01001 | C42S1 | N | 0 | PR01002 | 32-D-7200 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
JWR37008 | 08 | 32 | 1-1/2" | JWR | 37008 | B-1 | N | 0 | 32-Z-7300 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40001 |  | 32 | 6" | JWR | 40001 | B-1 | HB | 30 | JWR40003 | JWR64003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.30 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40003 | 08 | 32 | 3/4" | JWR | 40003 | B-1 | N | 0 | 32-E-4001 | JWR64043 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40003 | 08 | 32 | 6" | JWR | 40003 | B-1 | N | 0 | 32-E-4001 | JWR64043 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40003 | 08 | 32 | 18" | JWR | 40003 | B-1 | N | 0 | 32-E-4001 | JWR64043 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR43001 | 08 | 32 | 1-1/2" | JWR | 43001 | C3S1 | N | 0 | 32-E-4301 | JWR43002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.33 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR43001 | 08 | 32 | 4" | JWR | 43001 | C3S1 | N | 0 | 32-E-4301 | JWR43002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.33 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR43002 | 08 | 32 | 3" | JWR | 43002 | B-1 | N | 0 | JWR43001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR43004 | 08 | 32 | 1-1/2" | JWR | 43004 | B-1 | N | 0 | JW43001 | JWR43002 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR50001 | 08 | 32 | 8" | JWR | 50001 | B-1 | N | 0 | 32-E-5001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR50002 | 08 | 32 | 3/4" | JWR | 50002 | B-1 | N | 0 | COOLING DRUM | VA50009 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR50002 | 08 | 32 | 1-1/2" | JWR | 50002 | B-1 | N | 0 | COOLING DRUM | VA50009 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
N67090 | 08 | 32 | 3/4" | N | 67090 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67091 | 08 | 32 | 1" | N | 67091 | B-1 | N | 0 | N67104 | BDL60040 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67092 | 08 | 32 | 1" | N | 67092 | B-1 | N | 0 | N67028 | BDL60042 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67093 | 08 | 32 | 3/4" | N | 67093 | B-1 | N | 0 | N67028 | BDL60041 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67094 | 08 | 32 | 1" | N | 67094 | B-1 | N | 0 | N67020 | BDL60043 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67095 | 08 | 32 | 1" | N | 67095 | B-1 | N | 0 | N67017 | BDL60044 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67099 | 08 | 32 | 1" | N | 67099 | B-1 | N | 0 | N67029 | BDL60045 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N670AC | 08 | 32 | 3/4" | N | 670AC | B-1 | N | 0 | N67046 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67100 | 08 | 32 | 3/4" | N | 67100 | B-1 | N | 0 | N67029 | BDL60049 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67101 | 08 | 32 | 1" | N | 67101 | B-1 | N | 0 | N67029 | BDL60050 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
PR23031 | 08 | 32 | 3" | PR | 23031 | D20S1 | N | 0 | 32-D-2300 | BDL23016 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 153.15 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23032 |  | 32 | 3/4" | PR | 23032 | 1FS4 | ST | 30 | JLS31010 | PR23029 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.17 | 1 | II | MOD.A2 | Y | NR | N | 32-P-008-01 |  | H | N | 141 | N | 331 | 15
PR23032 |  | 32 | 1" | PR | 23032 | 1FS4 | ST | 30 | JLS31010 | PR23029 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.17 | 1 | II | MOD.A2 | Y | NR | N | 32-P-008-01 |  | H | N | 141 | N | 331 | 15
PR23032 |  | 32 | 1-1/2" | PR | 23032 | 1FS4 | ST | 30 | JLS31010 | PR23029 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.17 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | H | N | 141 | N | 331 | 15
PR24007 | 08 | 32 | 1/2" | PR | 24007 | D20S1 | N | 0 | HCM24082 | PPL80001 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR24007 | 08 | 32 | 1" | PR | 24007 | D20S1 | N | 0 | HCM24082 | PPL80001 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR24007 | 08 | 32 | 2" | PR | 24007 | D20S1 | N | 0 | HCM24082 | PPL80001 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR24007 | 08 | 32 | 4" | PR | 24007 | D20S1 | N | 0 | HCM24082 | PPL80001 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR24032 | 7A | 32 | 2" | PR | 24032 | 1FS4 | JP | 0 | HCM24099 | BDL31025 | 55.0/55.0 | -40.0/200.0 | 35.0 | 78.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 78 | sh.20 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-046-01 |  | A | N | 141 | N | 336 | 10
JWS64051 | 08 | 32 | 3" | JWS | 64051 | B-1 | N | 0 | JWS64054 | JWS24010 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64051 | 08 | 32 | 6" | JWS | 64051 | B-1 | N | 0 | JWS64054 | JWS24010 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64052 | 08 | 32 | 6" | JWS | 64052 | B-1 | N | 0 | JWS64054 | JWS24011 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64053 | 08 | 32 | 8" | JWS | 64053 | B-1 | N | 0 | JWS64054 | JWS64061 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64054 | 08 | 32 | 2" | JWS | 64054 | B-1 | N | 0 | JWS64008 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64054 | 08 | 32 | 16" | JWS | 64054 | B-1 | N | 0 | JWS64008 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64056 | 08 | 32 | 8" | JWS | 64056 | B-1 | N | 0 | JWS64054 | JWS64039 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64058 | 08 | 32 | 4" | JWS | 64058 | B-1 | N | 0 | JWS64054 | JWS64030 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64059 | 08 | 32 | 3" | JWS | 64059 | B-1 | N | 0 | JWS64054 | JWS64020 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64060 | 08 | 32 | 14" | JWS | 64060 | B-1 | N | 0 | 32-P-6400A | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64062 | 08 | 32 | 3/4" | JWS | 64062 | B-1 | N | 0 | JWS64057 | 32-Z-2400A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64062 | 08 | 32 | 1-1/2" | JWS | 64062 | B-1 | N | 0 | JWS64057 | 32-Z-2400A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
PR34029 |  | 32 | 2" | PR | 34029 | QXB26S1 | ET | 30 | PR34017 | OTHER SECTIONS | 8.0/8.0 | 200.0/-45.0 | 5.0 | 80.0 |  | 12.83 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 27 | N | 32-P-048-01 |  | G | N | 141 | N | 392 | 10
PR35011 | 08 | 32 | 1" | PR | 35011 | B4S1 | N | 0 | 32-D-3500 | PR36016 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35013 |  | 32 | 3" | PR | 35013 | B4S1 | P | 50 | PR36012 | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35015 | 08 | 32 | 3" | PR | 35015 | B4S1 | N | 0 | 32-D-3500 | BDL35009 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35016 | 08 | 32 | 3/4" | PR | 35016 | B4S2 | N | 0 | 32-P-3501 | PR35017 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35016 | 08 | 32 | 1-1/2" | PR | 35016 | B4S2 | N | 0 | 32-P-3501 | PR35017 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35017 | 08 | 32 | 1" | PR | 35017 | B4S2 | N | 0 | PR35016 | PR35018 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35018 | 08 | 32 | 2" | PR | 35018 | B4S2 | N | 0 | PR35017 | PR35020 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35019 | 08 | 32 | 1" | PR | 35019 | B4S1 | N | 0 | 32-E-3500 | 32-D-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35019 | 08 | 32 | 1-1/2" | PR | 35019 | B4S1 | N | 0 | 32-E-3500 | 32-D-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35019 | 08 | 32 | 12" | PR | 35019 | B4S1 | N | 0 | 32-E-3500 | 32-D-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35020 | 08 | 32 | 1" | PR | 35020 | B4S2 | N | 0 | PR35021 | 32-P-3501 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR36009 |  | 32 | 1/2" | PR | 36009 | C42S1 | HB | 30 | PR36013 | PR34021 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36010 |  | 32 | 3" | PR | 36010 | C42S1 | P | 50 | PR36013 | HCM31012 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-01 |  | G | Y | 141 | N | 353 | 10
PR36012 |  | 32 | 3/4" | PR | 36012 | C42S1 | P | 50 | PR36013 | PR35013 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | III | MOD.G | Y | 1 | N | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36012 |  | 32 | 6" | PR | 36012 | C42S1 | P | 50 | PR36013 | PR35013 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | III | MOD.G | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36013 | 08 | 32 | 3" | PR | 36013 | C42S1 | P | 50 | TP-125 (32-D-3607, FO-3667) | PR36032 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36014 |  | 32 | 1-1/2" | PR | 36014 | C42S1 | P | 50 | 32-PK-3600 | PR35021 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36015 |  | 32 | 3" | PR | 36015 | C42S1 | P | 50 | PR36013 | 32-E-4301 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36016 | 08 | 32 | 1" | PR | 36016 | B4S1 | N | 0 | PR35011 | PR36026 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 397 | ,10
BDL35010 | 08 | 32 | 1-1/2" | BDL | 35010 | B32S1 | N | 0 | PR35019 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL35011 | 08 | 32 | 1/2" | BDL | 35011 | B32S1 | N | 0 | VZ35002 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.27 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CWR64016 | 08 | 32 | 1-1/2" | CWR | 64016 | B-1 | N | 0 | 32-E-6400C | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64016 | 08 | 32 | 20" | CWR | 64016 | B-1 | N | 0 | 32-E-6400C | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR80001 | 08 | 32 | 1/2" | CWR | 80001 | B-1 | N | 0 | 32-E-8000 | CWR64011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR80001 | 08 | 32 | 4" | CWR | 80001 | B-1 | N | 0 | 32-E-8000 | CWR64011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
FW68B0I | 08 | 45 | 6" | FW | 68B0I | UGB-1PE | N | 0 | FW68B45 | 45-HY-6815 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0J | 08 | 45 | 8" | FW | 68B0J | UGB-1PE | N | 0 | FW68B49 | FW68B50 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0K | 08 | 45 | 8" | FW | 68B0K | UGB-1PE | N | 0 | FW68B51 | FW68B52 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0L | 08 | 45 | 6" | FW | 68B0L | UGB-1PE | N | 0 | FW68B39 | FW68B40 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0M | 08 | 45 | 6" | FW | 68B0M | UGB-1PE | N | 0 | FW68B35 | FW68B36 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0N | 08 | 45 | 8" | FW | 68B0N | UGB-1PE | N | 0 | FW68B33 | FW68B34 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0P | 08 | 45 | 6" | FW | 68B0P | UGB-1PE | N | 0 | FW68B37 | 45-HM-6809 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
HN72001 | 08 | 32 | 1-1/2" | HN | 72001 | C6S1 | N | 0 | SP-04-172B2-01 | PR72004 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52A | 2 | I | MOD.A | Y | 1 | N | 32-P-007-01 |  | E | N | 000 | N | 170
HN72003 | 08 | 32 | 1" | HN | 72003 | C6S1 | N | 0 | 172C0-09 | PR72024 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.53 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN72004 | 08 | 32 | 1" | HN | 72004 | C6S1 | N | 0 | 172C0-03 | PR72020 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.53 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN72005 | 08 | 32 | 1" | HN | 72005 | C6S1 | N | 0 | NITROGEN CONNECTION | PR01001 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.51 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 170
HN72006 | 08 | 32 | 1" | HN | 72006 | C6S1 | N | 0 | NITROGEN CONNECTION | PR72014 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.51 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 170
HN72007 | 08 | 32 | 1" | HN | 72007 | C6S1 | N | 0 | NITROGEN CONNECTION | PR72009 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.51 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 170
HN72008 | 08 | 32 | 1" | HN | 72008 | C6S1 | N | 0 | PR720105 | SP-04-172B1-10 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
HN72010 | 08 | 32 | 1-1/2" | HN | 72010 | C6S1 | N | 0 | PR720105 | SP-04-172B1-09 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
HN72011 | 08 | 32 | 1" | HN | 72011 | C6S1 | N | 0 | PR720105 | SP-04-172B1-03 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
CWS89041 | 08 | 32 | 14" | CWS | 89041 | B-1 | N | 0 | CWS64010 | TP-N50903 (E-8900A) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89042 | 08 | 32 | 3/4" | CWS | 89042 | B-1 | N | 0 | CWS64010 | CWS86016 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89042 | 08 | 32 | 2" | CWS | 89042 | B-1 | N | 0 | CWS64010 | CWS86016 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
FW68H58 | 08 | 32 | 1-1/2" | FW | 68H58 | B-13 | N | 0 | FW68H60 | FW68H59 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H59 | 08 | 32 | 1-1/2" | FW | 68H59 | B-13 | N | 0 | FW68H58 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I01 | 08 | 32 | 1-1/2" | FW | 68I01 | B-13 | N | 0 | FW68I19 | FW68I10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I02 | 08 | 32 | 2" | FW | 68I02 | B-13 | N | 0 | MSN-003 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I03 | 08 | 32 | 1-1/2" | FW | 68I03 | B-13 | N | 0 | MSN-003 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I04 | 08 | 32 | 1-1/2" | FW | 68I04 | B-13 | N | 0 | MSN-003 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I05 | 08 | 32 | 1-1/2" | FW | 68I05 | B-13 | N | 0 | FW68I20 | FW68I22 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I08 | 08 | 32 | 4" | FW | 68I08 | B-13 | N | 0 | FW68I18 | FW68I11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I10 | 08 | 32 | 3" | FW | 68I10 | B-13 | N | 0 | FW68I09 | FW68I16 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I11 | 08 | 32 | 1-1/2" | FW | 68I11 | B-13 | N | 0 | FW68I08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I13 | 08 | 32 | 3" | FW | 68I13 | B-13 | N | 0 | FW68I10 | FW68I02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I15 | 08 | 32 | 1-1/2" | FW | 68I15 | B-13 | N | 0 | FW68I17 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I16 | 08 | 32 | 1-1/2" | FW | 68I16 | B-13 | N | 0 | FW68I10 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I18 | 08 | 32 | 4" | FW | 68I18 | B-13 | N | 0 | FW68C08 | FW68I06 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I20 | 08 | 32 | 3" | FW | 68I20 | B-13 | N | 0 | FW68C08 | FW68I05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I22 | 08 | 32 | 1" | FW | 68I22 | B-13 | N | 0 | FW68I05 | FW68I34 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I26 | 08 | 32 | 1" | FW | 68I26 | B-13 | N | 0 | MSN-002 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
IA62018 | 08 | 32 | 2" | IA | 62018 | B-13 | N | 0 | IA62001 | 32-S-2300 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
BU73051 | 08 | 32 | 3/4" | BU | 73051 | D20S1 | N | 0 | 32-P-7300 | BU73053 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73051 | 08 | 32 | 1-1/2" | BU | 73051 | D20S1 | N | 0 | 32-P-7300 | BU73053 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73053 | 08 | 32 | 1/2" | BU | 73053 | D20S1 | N | 0 | BU73051 | BU73040 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73053 | 08 | 32 | 2" | BU | 73053 | D20S1 | N | 0 | BU73051 | BU73040 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73055 | 08 | 32 | 2" | BU | 73055 | B32S1 | N | 0 | BU01001 | 32-S-7302A | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73081 | 08 | 32 | 1" | BU | 73081 | B32S1 | N | 0 | 32-S-7302B | BDL73048 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73083 | 08 | 32 | 1/2" | BU | 73083 | B32S1 | N | 0 | 32-S-7302B | BDL73050 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73083 | 08 | 32 | 1" | BU | 73083 | B32S1 | N | 0 | 32-S-7302B | BDL73050 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73084 | 08 | 32 | 3/4" | BU | 73084 | B32S1 | N | 0 | 32-S-7302B | BDL73050 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73085 | 08 | 32 | 3/4" | BU | 73085 | B32S1 | N | 0 | 32-S-7302A | BDL73049 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73086 | 08 | 32 | 3/4" | BU | 73086 | B32S1 | N | 0 | 32-S-7302A | BDL73049 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73087 | 08 | 32 | 3/4" | BU | 73087 | B32S1 | N | 0 | 32-D-7302 | BDL73040 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73087 | 08 | 32 | 1-1/2" | BU | 73087 | B32S1 | N | 0 | 32-D-7302 | BDL73040 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73088 | 08 | 32 | 1/2" | BU | 73088 | B32S1 | N | 0 | BU73049 | BDL73074 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
CD31002 | 08 | 32 | 1/2" | CD | 31002 | 1CS2 | ET | 30 | NITROGEN CONNECTION | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD31006 | 08 | 32 | 1" | CD | 31006 | 1CS2 | N | 0 | 32-SP-04 | HCM31023 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | F | N | 100 | N | 288
CD34009 | 08 | 32 | 1" | CD | 34009 | 1CS2 | ET | 30 | CD34008 | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34011 | 08 | 32 | 1/2" | CD | 34011 | 1CS2 | ET | 30 | CD34009 | CD | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34011 | 08 | 32 | 1" | CD | 34011 | 1CS2 | ET | 30 | CD34009 | CD | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34012 | 08 | 32 | 1/2" | CD | 34012 | 1CS2 | ET | 30 | CD34009 | 32-SP-04-123CO-07 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
FW68Q10 | 08 | 32 | 1-1/2" | FW | 68Q10 | B-13 | N | 0 | FW68Q01 | FW68Q11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q11 | 08 | 32 | 1-1/2" | FW | 68Q11 | B-13 | N | 0 | FW68Q10 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q12 | 08 | 32 | 1" | FW | 68Q12 | B-13 | N | 0 | FW68Q09 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68R02 | 08 | 45 | 1/2" | FW | 68R02 | B-7 | N | 0 | FW68R07 | 45-XV-6820A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R04 | 08 | 45 | 2" | FW | 68R04 | B-13 | N | 0 | 45-XV-6821A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68R05 | 08 | 45 | 4" | FW | 68R05 | B-13 | N | 0 | 45-XV-6822A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-08 |  | - | Y | 000 | - | 74
FW68R06 | 08 | 45 | 1" | FW | 68R06 | B-13 | N | 0 | 45-XV-6820A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
FW68R07 | 08 | 45 | 2" | FW | 68R07 | B-7 | N | 0 | FW68B50 | FW68R09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R10 | 08 | 45 | 3/4" | FW | 68R10 | B-13 | N | 0 | HEADER | Funnel | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68R12 | 08 | 45 | 3/4" | FW | 68R12 | B-13 | N | 0 | 45-XV-6821A | FW68R10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68R15 | 08 | 45 | 6" | FW | 68R15 | B-7 | N | 0 | FW68R07 | 45-XV-6824A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
IA68N01 | 08 | 32 | 1" | IA | 68N01 | B-13 | N | 0 | IA68N06 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N05 | 08 | 32 | 1" | IA | 68N05 | B-13 | N | 0 | IA68K07 | IA68N04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N06 | 08 | 32 | 1" | IA | 68N06 | B-13 | N | 0 | IA68N04 | IA68N01 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N24 | 08 | 32 | 1" | IA | 68N24 | B-13 | N | 0 | IA68N29 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N29 | 08 | 32 | 1" | IA | 68N29 | B-13 | N | 0 | IA68K07 | IA68N43 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N33 | 08 | 32 | 1" | IA | 68N33 | B-13 | N | 0 | IA68N32 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N38 | 08 | 32 | 1" | IA | 68N38 | B-13 | N | 0 | IA68M11 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N40 | 08 | 32 | 1" | IA | 68N40 | B-13 | N | 0 | IA68N24 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
CHWS14001 |  | 32 | 1-1/2" | CHWS | 14001 | B-1 | CF | 25 | 32-P-1401 | JLS14001 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14002 |  | 32 | 1-1/2" | CHWS | 14002 | B-1 | CF | 25 | CHWS14007 | CHWS14021 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14004 |  | 32 | 3/4" | CHWS | 14004 | B-1 | HA | 30 | 32-P-1400B | 32-E-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14004 |  | 32 | 2" | CHWS | 14004 | B-1 | HA | 30 | 32-P-1400B | 32-E-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14005 |  | 32 | 1-1/2" | CHWS | 14005 | B-1 | CF | 25 | CHWR15007 | 32-P-1401 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14006 |  | 32 | 3/4" | CHWS | 14006 | B-1 | CF | 25 | CHWS14002 | CAP | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14007 |  | 32 | 1-1/2" | CHWS | 14007 | B-1 | CF | 25 | JLS14001 | CHW1523 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14008 |  | 32 | 1" | CHWS | 14008 | B-1 | HA | 30 | CHWS14012 | 32-P-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
HCM24055 | 08 | 32 | 1" | HCM | 24055 | 3FS4 | N | 0 | HCM24064 | OG01004 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 5 | N | 32-U-034-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24055 | 08 | 32 | 3" | HCM | 24055 | 3FS4 | N | 0 | HCM24064 | OG01004 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 5 | Y | 32-U-034-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24056 |  | 32 | 2" | HCM | 24056 | D20S1 | P | 50 | HCM24094 | 32-T-4300 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24056 |  | 32 | 3" | HCM | 24056 | D20S1 | P | 50 | HCM24094 | 32-T-4300 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24057 |  | 32 | 4" | HCM | 24057 | D20S1 | P | 50 | HCM24069 | P23027 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
BDH21001 | 08 | 32 | 6" | BDH | 21001 | C42S2 | N | 0 | 32-R-2100 | 32-D-6011 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | III | MOD.G | Y | 1 | Y | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH21001 | 08 | 32 | 10" | BDH | 21001 | C42S2 | N | 0 | 32-R-2100 | 32-D-6011 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | III | MOD.G | Y | 1 | Y | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH21004 | 08 | 32 | 1" | BDH | 21004 | C42S2 | N | 0 | SL21002 | BDH21001 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH21004 | 08 | 32 | 1-1/2" | BDH | 21004 | C42S2 | N | 0 | SL21002 | BDH21001 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH21005 | 08 | 32 | 1" | BDH | 21005 | C42S2 | N | 0 | HN21005 | BDH21001 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH60001 |  | 32 | 10" | BDH | 60001 | C42S2 | P | 100 | 32-D-6011 | CONTAINER | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.41 | 1 | III | MOD.G | Y | 1 | Y | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH60002 |  | 32 | 1" | BDH | 60002 | C42S1 | HB | 50 | BDH60003 | 32-D-6011 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-02 |  | F | N | 141 | N | 483 | 15
HCM32036 | 08 | 32 | 4" | HCM | 32036 | C42S1 | HB | 40 | HCM32019 | BDL32030 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-04 |  | G | Y | 141 | N | 351 | 10
HCM32037 | 08 | 32 | 2" | HCM | 32037 | C42S1 | HB | 30 | TP-03A (32-D-3201A) | HCM32031 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32042 | 08 | 32 | 2" | HCM | 32042 | C42S1 | HB | 30 | TP-03B (32-D-3201B) | HCM32032 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24G | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32043 | 08 | 32 | 1" | HCM | 32043 | C42S1 | HB | 30 | TP-05B (32-D-3202B) | HCM32032 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24G | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32044 | 08 | 32 | 4" | HCM | 32044 | C42S1 | HB | 40 | HCM32030 | BDL32029, PSV-3280 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24G | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM40001 | 08 | 32 | 1" | HCM | 40001 | C42S1 | N | 0 | ET71039 | 32-R-4001 | 40.0/40.0 | -45.0/150.0 | 20.0 | 40.0 |  | 60.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-049-01 |  | F | N | 141 | N | 326 | ,15
HCM40001 | 08 | 32 | 3" | HCM | 40001 | C42S1 | N | 0 | ET71039 | 32-R-4001 | 40.0/40.0 | -45.0/150.0 | 20.0 | 40.0 |  | 60.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-049-01 |  | F | N | 141 | N | 326 | ,15
HCM43001 |  | 32 | 1" | HCM | 43001 | D20S1 | P | 50 | PR43024 | HCM24025 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 530 | 15
HCM43001 |  | 32 | 1-1/2" | HCM | 43001 | D20S1 | P | 50 | PR43024 | HCM24025 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 530 | 15
N32018 | 08 | 32 | 2" | N | 32018 | B4S1 | N | 0 | TP-28B, (CYLINDER 1) | TP-34B, (32-D-3204B) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N32021 | 08 | 32 | 1" | N | 32021 | B-1 | N | 0 | TP-21B, (32-S-3202B) | N67020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N32023 | 08 | 32 | 3/4" | N | 32023 | B-1 | N | 0 | NITROGEN CONNECTION | HCM32024 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.24A | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-02 |  | E | N | 000 | N | 140
N32024 | 08 | 32 | 3/4" | N | 32024 | B-1 | N | 0 | N | HCM32024 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.24G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-02 |  | E | N | 000 | N | 140
JWR51001 | 08 | 32 | 2" | JWR | 51001 | B-1 | N | 0 | TO E-5102 | JWR64046 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52001 | 08 | 32 | 3/4" | JWR | 52001 | B-1 | N | 0 | 32-E-5201 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52001 | 08 | 32 | 4" | JWR | 52001 | B-1 | N | 0 | 32-E-5201 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52002 | 08 | 32 | 3/4" | JWR | 52002 | B-1 | N | 0 | Seal Pot | VA52017 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52002 | 08 | 32 | 3" | JWR | 52002 | B-1 | N | 0 | Seal Pot | VA52017 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52003 | 08 | 32 | 3/4" | JWR | 52003 | B-1 | N | 0 | Seal Pot | VA52018 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52003 | 08 | 32 | 1-1/2" | JWR | 52003 | B-1 | N | 0 | Seal Pot | VA52018 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52004 | 08 | 32 | 3/4" | JWR | 52004 | B-1 | N | 0 | 32-E-5252A | JWR64047 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52005 | 08 | 32 | 3/4" | JWR | 52005 | B-1 | N | 0 | 32-E-5252B | JWR52004 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR53001 | 08 | 32 | 2" | JWR | 53001 | B-1 | N | 0 | TP-008 (JWR530128) | JWR64046 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR62001 | 08 | 32 | 1" | JWR | 62001 | B-1 | N | 0 | TP-14, (JWR620101) | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PR24032 | 08 | 32 | 2" | PR | 24032 | 1FS4 | N | 0 | HCM24099 | BDL31025 | 55.0/55.0 | -40.0/200.0 | 35.0 | 78.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 78 | sh.20 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-046-01 |  | A | N | 141 | N | 336 | 10
PR24033 | 08 | 32 | 4" | PR | 24033 | C42S1 | N | 0 | HCM24083 | PR33008 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR24034 | 08 | 32 | 2" | PR | 24034 | C42S1 | N | 0 | 32-E-2404 | P23022 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24035 | 08 | 32 | 1" | PR | 24035 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24035 | 08 | 32 | 2" | PR | 24035 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24037 | 08 | 32 | 3/4" | PR | 24037 | D20S1 | N | 0 | HCM24083 | PR24039 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24037 | 08 | 32 | 3" | PR | 24037 | D20S1 | N | 0 | HCM24083 | PR24039 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24039 |  | 32 | 1-1/2" | PR | 24039 | D20S1 | P | 50 | HCM24084 | PR24040 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24040 |  | 32 | 1-1/2" | PR | 24040 | D20S1 | P | 50 | PR24039 | PR24041 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24041 |  | 32 | 1/2" | PR | 24041 | D20S1 | HB | 30 | PR24040 | HCM23078 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24041 |  | 32 | 1-1/2" | PR | 24041 | D20S1 | HB | 30 | PR24040 | HCM23078 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24042 |  | 32 | 3/4" | PR | 24042 | D20S1 | P | 50 | PR24039 | PR24043 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24043 |  | 32 | 1" | PR | 24043 | D20S1 | HB | 30 | PR24042 | HCM23079 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24044 |  | 32 | 3/4" | PR | 24044 | D20S1 | P | 50 | PR24039 | PR24045 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24045 |  | 32 | 1/2" | PR | 24045 | D20S1 | HB | 30 | PR24044 | HCM23080 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24045 |  | 32 | 1-1/2" | PR | 24045 | D20S1 | HB | 30 | PR24044 | HCM23080 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24046 |  | 32 | 3/4" | PR | 24046 | D20S1 | P | 50 | PR24039 | PR24047 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24047 |  | 32 | 1" | PR | 24047 | D20S1 | HB | 30 | PR24046 | HCM23081 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR36019 | 08 | 32 | 4" | PR | 36019 | B4S1 | P | 50 | D-3602 | TP-186, PSV-3684 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
PR36020 | 08 | 32 | 1" | PR | 36020 | C42S1 | P | 50 | PR36035 | PR36028 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28A | 1 | Art 4.3 | NA | N | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36022 |  | 32 | 1" | PR | 36022 | C42S1 | P | 50 | PR36028 | PR36014 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36029 | 08 | 32 | 1" | PR | 36029 | C42S1 | N | 0 | TP-121 (32-D-3606) | PR36040 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36030 | 08 | 32 | 1" | PR | 36030 | C42S1 | P | 50 | 32-D-3607 | PR36023 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36031 | 08 | 32 | 2" | PR | 36031 | B4S1 | N | 0 | TP-118,32-D-3605 | BDL36018 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
PR36032 | 08 | 32 | 1" | PR | 36032 | C42S1 | P | 50 | PR36013 | BDL36022 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36032 | 08 | 32 | 4" | PR | 36032 | C42S1 | P | 50 | PR36013 | BDL36022 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28B | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36035 | 08 | 32 | 2" | PR | 36035 | B32S1 | P | 50 | TP-108, (32-D-3602) | PR36020 | 10.0/10.0 | -45.0/180.0 | 5.5 | 107.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 107 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 357 | 10
PR36037 | 08 | 32 | 2" | PR | 36037 | B32S1 | P | 50 | TP-105 (32-D-3603) | PR36022 | 10.0/10.0 | -45.0/180.0 | 5.5 | 107.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 107 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 357 | 10
PR36039 | 08 | 32 | 2" | PR | 36039 | B32S1 | P | 50 | TP-188 (HCM360118) | PR36028 | 10.0/10.0 | -45.0/180.0 | 5.5 | 107.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 107 | sh.28B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-03 |  | G | Y | 141 | N | 357 | 10
PR40021 |  | 32 | 1" | PR | 40021 | D20S1 | ST | 30 | PR31015 | PR40029 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-048-01 |  | F | N | 141 | N | 330 | 15
PR40022 | 08 | 32 | 1" | PR | 40022 | C42S1 | N | 0 | PR33023 | HCM40001 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
CWR80002 | 08 | 32 | 2" | CWR | 80002 | B-1 | N | 0 | 32-E-8001 | CWR80005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR80006 | 08 | 32 | 3/4" | CWR | 80006 | B-1 | N | 0 | CWR80001 | VA80011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86001 |  | 32 | 3/4" | CWR | 86001 | B-1 | HB | 30 | PX86030 | CWR86011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86010 | 08 | 32 | 1/2" | CWR | 86010 | B-1 | N | 0 | 32-FT-8601 | CWR86019 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86011 | 08 | 32 | 2" | CWR | 86011 | B-1 | N | 0 | CWR86001 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86013 | 08 | 32 | 1/2" | CWR | 86013 | B-1 | N | 0 | JCW86014 | CWR86011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86014 |  | 32 | 1/2" | CWR | 86014 | B-1 | HB | 30 | JCW86018 | CWR86011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86016 | 08 | 32 | 1" | CWR | 86016 | B-1 | N | 0 | 32-D-8600 | CWR86021 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86017 |  | 32 | 1/2" | CWR | 86017 | B-1 | HB | 30 | JCW86021 | CWR86001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86019 | 08 | 32 | 1/2" | CWR | 86019 | B-1 | N | 0 | JCW86022 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86019 | 08 | 32 | 1" | CWR | 86019 | B-1 | N | 0 | JCW86022 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR88001 | 08 | 32 | 1-1/2" | CWR | 88001 | B-1 | N | 0 | 32-E-8005 | CWR88003 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.67 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
BDL43019 | 08 | 32 | 3/4" | BDL | 43019 | B32S1 | N | 0 | BDL24095 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43019 | 08 | 32 | 1-1/2" | BDL | 43019 | B32S1 | N | 0 | BDL24095 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43020 | 08 | 32 | 1" | BDL | 43020 | B32S1 | N | 0 | 32-E-4303 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | I | MOD.A | Y | 1 | N | 32-P-047-03 |  | G | N | 141 | N | 460 | 10
IA62019 | 08 | 32 | 1" | IA | 62019 | B-13 | N | 0 | IA62001 | 32-S-3100 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62042 | 08 | 32 | 1/2" | IA | 62042 | B-13 | N | 0 | IA62001 | PCV-1550 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62052 | 08 | 32 | 1/2" | IA | 62052 | B-13 | N | 0 | IA62075 | TP-07A (32-PCV-3256) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62055 | 08 | 32 | 1" | IA | 62055 | B-13 | N | 0 | IA62074 | TO OFF GAS DRYING TOWERS T-5300A/B AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62056 | 08 | 32 | 1-1/2" | IA | 62056 | B-13 | N | 0 | IA62073 | IA71005 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62073 | 08 | 32 | 1-1/2" | IA | 62073 | B-13 | N | 0 | IA62001 | IA62056 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62075 | 08 | 32 | 1" | IA | 62075 | B-13 | N | 0 | IA62001 | IA62052 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62076 | 08 | 32 | 1-1/2" | IA | 62076 | B-13 | N | 0 | IA62001 | IA62097 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62077 | 08 | 32 | 1" | IA | 62077 | B-13 | N | 0 | IA62001 | IA6200K | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62078 | 08 | 32 | 1" | IA | 62078 | B-13 | N | 0 | IA62001 | END CAP | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62082 | 08 | 32 | 1-1/2" | IA | 62082 | B-13 | N | 0 | IA62089 | 32-IAM-022 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62083 | 08 | 32 | 1-1/2" | IA | 62083 | B-13 | N | 0 | IA62089 | 32-IAM-026 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62084 | 08 | 32 | 1-1/2" | IA | 62084 | B-13 | N | 0 | IA62089 | 32-IAM-029 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62085 | 08 | 32 | 1-1/2" | IA | 62085 | B-13 | N | 0 | IA62089 | 32-IAM-033 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62091 | 08 | 32 | 1" | IA | 62091 | B-13 | N | 0 | IA62010 | VA62002 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-02 |  | - | N | 000 | - | 200
IA62092 | 08 | 32 | 2" | IA | 62092 | B-13 | N | 0 | IA01001 | VA62003 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
CD34012 | 08 | 32 | 1" | CD | 34012 | 1CS2 | ET | 30 | CD34009 | 32-SP-04-123CO-07 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34013 | 08 | 32 | 3/4" | CD | 34013 | 1IS5 | N | 0 | CO2 CYLINDER AT GROUND LEVEL (130 BARG MAX) | TO SAFE LOCATION | 130.0 | 150.0 | 50.0 | 80.0 |  | 75 | 75 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 80 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 292
CD34014 | 08 | 32 | 1" | CD | 34014 | 1CS2 | ET | 30 | CD34009 | 32-SP-04 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34015 | 08 | 32 | 1" | CD | 34015 | 1CS2 | ET | 30 | CD34009 | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34016 | 08 | 32 | 1" | CD | 34016 | 1CS2 | N | 0 | NITROGEN CONNECTION | PR34022 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-048-01 |  | F | N | 100 | N | 288
CD34017 | 08 | 32 | 1" | CD | 34017 | 1CS2 | N | 0 | 32-SP-04-13400-04 | PR34024 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-048-01 |  | F | N | 100 | N | 288
CD34018 | 08 | 32 | 1" | CD | 34018 | 1CS2 | N | 0 | 32-SP-04-13400-01 | N34007 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-048-01 |  | F | N | 100 | N | 288
CD34019 | 08 | 32 | 1" | CD | 34019 | 1CS2 | ET | 30 | NITROGEN CONNECTION | CD34009 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD36001 | 08 | 32 | 1-1/2" | CD | 36001 | 1CS2 | N | 0 | FX-3601 | PR36016 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.28 | 2 | Art 4.3 | NA | N | NR | N | 32-P-048-02 |  | F | N | 100 | N | 288
DO12018 | 08 | 32 | 3/4" | DO | 12018 | 3FS3 | N | 0 | 32-P-1200B | DO12019 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12019 | 08 | 32 | 1/2" | DO | 12019 | 3FS3 | N | 0 | DO12017 | DO12017 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12021 | 08 | 32 | 1/2" | DO | 12021 | 1CS2 | N | 0 | DO12014 | DO12013 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12022 |  | 32 | 1/2" | DO | 12022 | 3FS3 | ET | 30 | DO12008 | 32-P-1200A | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12022 |  | 32 | 1" | DO | 12022 | 3FS3 | ET | 30 | DO12008 | 32-P-1200A | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12023 |  | 32 | 3/4" | DO | 12023 | 3FS3 | ET | 30 | DO12008 | 32-P-1200B | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12030 | 08 | 32 | 1" | DO | 12030 | 1CS2 | N | 0 | DO12004 | 32-D-1200C | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12032 | 08 | 32 | 3/4" | DO | 12032 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12032 | 08 | 32 | 8" | DO | 12032 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12033 | 08 | 32 | 1/2" | DO | 12033 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
CHWS14009 |  | 32 | 1-1/2" | CHWS | 14009 | B-1 | HA | 30 | 32-P-1400A | 32-E-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14010 |  | 32 | 3/4" | CHWS | 14010 | B-1 | HA | 30 | CHWS14015 | 32-P-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14010 |  | 32 | 2" | CHWS | 14010 | B-1 | HA | 30 | CHWS14015 | 32-P-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14012 |  | 32 | 1" | CHWS | 14012 | B-1 | HA | 30 | 32-D-1400A | CHWS14008 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14012 |  | 32 | 2" | CHWS | 14012 | B-1 | HA | 30 | 32-D-1400A | CHWS14008 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14014 |  | 32 | 2" | CHWS | 14014 | B-1 | HA | 30 | 32-E-1400B | 32-D-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14015 |  | 32 | 1" | CHWS | 14015 | B-1 | HA | 30 | 32-D-1400B | CHWS14010 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14015 |  | 32 | 2" | CHWS | 14015 | B-1 | HA | 30 | 32-D-1400B | CHWS14010 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14021 |  | 32 | 3/4" | CHWS | 14021 | B-1 | CF | 25 | CHWS14002 | 32-D-1401A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14022 |  | 32 | 2" | CHWS | 14022 | B-1 | HA | 30 | 32-E-1400A | 32-D-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS15003 | 08 | 32 | 1/2" | CHWS | 15003 | B-1 | CF | 25 | CHWS14007 | JCHW15001 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20001 |  | 32 | 1" | CHWS | 20001 | B-1 | CF | 25 | CHWS20005 | CHWS20002 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20002 |  | 32 | 3/4" | CHWS | 20002 | B-1 | CF | 25 | 32-P-2000 | JLS20001 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20003 |  | 32 | 3/4" | CHWS | 20003 | B-1 | CF | 25 | JLS20001 | 32-R-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20003 |  | 32 | 1-1/2" | CHWS | 20003 | B-1 | CF | 25 | JLS20001 | 32-R-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20004 |  | 32 | 3/4" | CHWS | 20004 | B-1 | CF | 25 | 32-R-2000 | 32-Z-2005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20005 |  | 32 | 3/4" | CHWS | 20005 | B-1 | CF | 25 | 32-Z-2005 | 32-P-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS21003 |  | 32 | 3" | CHWS | 21003 | B-1 | CF | 25 | 32-P-2101 | CHWS21004 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS21005 |  | 32 | 6" | CHWS | 21005 | B-1 | CF | 40 | CHWS21004 | 32-R-2100 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
BDH60003 | 08 | 32 | 1" | BDH | 60003 | C42S1 | N | 0 | 32-D-6011 | BDH60002 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | Art 4.3 | NA | N | 6 | N | 32-U-031-02 |  | F | N | 141 | N | 483 | 15
BDH60004 | 08 | 32 | 3/4" | BDH | 60004 | C42S2 | N | 0 | 32-D-6011 | FL60004 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.41 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH60006 |  | 32 | 3/4" | BDH | 60006 | C42S1 | HB | 40 | LS63047 | LS60004 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | F | N | 141 | N | 483 | 15
BDH60008 | 08 | 32 | 1" | BDH | 60008 | C42S1 | N | 0 | 32-D-6011 | BDH60002 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | Art 4.3 | NA | N | 6 | N | 32-U-031-02 |  | F | N | 141 | N | 483 | 15
BDL01002 | 08 | 32 | 1/2" | BDL | 01002 | B32S1 | N | 0 | PR24007 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01002 | 08 | 32 | 2" | BDL | 01002 | B32S1 | N | 0 | PR24007 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01003 | 08 | 32 | 3/4" | BDL | 01003 | B32S1 | N | 0 | PR24007 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01005 | 08 | 32 | 3/4" | BDL | 01005 | B32S1 | N | 0 | PR01002 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01005 | 08 | 32 | 1" | BDL | 01005 | B32S1 | N | 0 | PR01002 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01006 | 08 | 32 | 1" | BDL | 01006 | B32S1 | N | 0 | OG01004 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01009 | 08 | 32 | 4" | BDL | 01009 | B32S1 | N | 0 | BDL61001 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01009 | 08 | 32 | 6" | BDL | 01009 | B32S1 | N | 0 | BDL61001 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01010 | 08 | 32 | 1/2" | BDL | 01010 | B4S1 | N | 0 | HD01002 | BDL01037 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL01011 | 08 | 32 | 1" | BDL | 01011 | B4S1 | N | 0 | HD01001 | BDL01009 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL01014 | 08 | 32 | 3/4" | BDL | 01014 | B32S1 | N | 0 | PR01002 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01018 | 08 | 32 | 1/2" | BDL | 01018 | B32S1 | N | 0 | BU01001 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01021 | 08 | 32 | 2" | BDL | 01021 | B32S1 | N | 0 | PR01003 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01024 | 08 | 32 | 1" | BDL | 01024 | B32S1 | N | 0 | BU01003 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
HD01001 | 08 | 32 | 1" | HD | 01001 | 3FS4 | N | 0 | HD700002 | 32-S-0101 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01001 | 08 | 32 | 4" | HD | 01001 | 3FS4 | N | 0 | HD700002 | 32-S-0101 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | Y | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01002 | 08 | 32 | 1/2" | HD | 01002 | 3FS4 | N | 0 | 32-S-0101 | ET22007 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01002 | 08 | 32 | 3/4" | HD | 01002 | 3FS4 | N | 0 | 32-S-0101 | ET22007 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01002 | 08 | 32 | 2" | HD | 01002 | 3FS4 | N | 0 | 32-S-0101 | ET22007 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | Y | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
N33001 | 08 | 32 | 1/2" | N | 33001 | B-1 | N | 0 | 32-P-3300A | N3538 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N33002 | 08 | 32 | 1/2" | N | 33002 | B-1 | N | 0 | N33001 | 32-P-3300B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N33004 | 08 | 32 | 1" | N | 33004 | B-1 | N | 0 | N | PR33016 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N33005 | 08 | 32 | 1" | N | 33005 | B-1 | N | 0 | N | PR33018 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N35005 | 08 | 32 | 1" | N | 35005 | B-1 | N | 0 | NITROGEN CONNECTION | PR35019 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.27 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-02 |  | E | N | 000 | N | 140
N36006 | 08 | 32 | 2" | N | 36006 | B4S1 | N | 0 | TP-165 (CYLINDER 1, STAGE 1, PACKING 1, C97) | TP-182 (32-D-3609) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36008 | 08 | 32 | 1-1/2" | N | 36008 | B4S1 | N | 0 | TP-173 (CYLINDER 3, STAGE 1, PACKING 3, C94) | N36006 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36011 | 08 | 32 | 2" | N | 36011 | B4S1 | N | 0 | TP-169 (CYLINDER 1, STAGE 1, PACKING 1, C94) | TP-181 (32-D-3609) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36012 | 08 | 32 | 2" | N | 36012 | B4S1 | N | 0 | TP-168 (CYLINDER 1, STAGE 1, PACKING 1, C79) | TP-178 (32-D-3608) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36013 | 08 | 32 | 1" | N | 36013 | B4S1 | N | 0 | TP-172 (CYLINDER 2, STAGE 2, PACKING 2, C94) | N36011 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36020 | 08 | 32 | 1/2" | N | 36020 | B4S1 | N | 0 | TP-189 (32-D-3609) | N36019 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N40004 | 08 | 32 | 1" | N | 40004 | B-1 | N | 0 | NITROGEN CONNECTION | P40029 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-049-01 |  | E | N | 000 | N | 140
N40007 | 08 | 32 | 1" | N | 40007 | B-1 | N | 0 | NITROGEN CONNECTION | HD40006 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-002-01 |  | E | N | 000 | N | 140
N40009 | 08 | 32 | 1" | N | 40009 | B-1 | N | 0 | NITROGEN CONNECTION | P40033 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.31 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-049-01 |  | E | N | 000 | N | 140
JWR63001 | 08 | 32 | 6" | JWR | 63001 | B-1 | N | 0 | 32-E-6300 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR63002 | 08 | 32 | 1-1/2" | JWR | 63002 | B-1 | N | 0 | 32-E-6350A | JWR63003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PR31014 |  | 32 | 1" | PR | 31014 | 1FS4 | JR | 0 | PR31015 | PR34021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31014 |  | 32 | 1-1/2" | PR | 31014 | 1FS4 | JR | 0 | PR31015 | PR34021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31015 |  | 32 | 1" | PR | 31015 | 1FS4 | JR | 0 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31015 |  | 32 | 1-1/2" | PR | 31015 | 1FS4 | JR | 0 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31015 | 08 | 32 | 2" | PR | 31015 | 1FS4 | N | 0 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31016 | 7A | 32 | 1-1/2" | PR | 31016 | 1FS4 | HB | 30 | PR31022 | JLS31010 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31017 | 08 | 32 | 1-1/2" | PR | 31017 | 1FS4 | N | 0 | PR31023 | JLS31009 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31018 |  | 32 | 1" | PR | 31018 | D20S1 | HB | 30 | JLS31012 | PR31019 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
PR31018 |  | 32 | 4" | PR | 31018 | D20S1 | HB | 30 | JLS31012 | PR31019 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
PR31019 |  | 32 | 2" | PR | 31019 | D20S1 | HB | 30 | 32-S-3100 | PR31018 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
PR31020 |  | 32 | 2" | PR | 31020 | D20S1 | HB | 30 | 32-S-3100 | PR31021 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
PR31022 | 08 | 32 | 1" | PR | 31022 | D20S1 | N | 0 | PR31023 | HCM31017 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR31023 |  | 32 | 1-1/2" | PR | 31023 | 1FS4 | JR | 0 | HCM32020 | PR31015 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31023 |  | 32 | 2" | PR | 31023 | 1FS4 | JR | 0 | HCM32020 | PR31015 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31024 |  | 32 | 1-1/2" | PR | 31024 | 1FS4 | JR | 0 | PR31015 | JLS31006 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-047-01 |  | A | N | 141 | N | 335 | 10
PR33002 | 08 | 32 | 1" | PR | 33002 | C42S1 | N | 0 | 32-D-3300 | BDL33002 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33004 |  | 32 | 3/4" | PR | 33004 | C42S1 | ST | 30 | PR33003 | TP-003 (PR530129) | 25.0/25.0 | -45.0/120.0 | 3.0 | 20.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 20 | sh.25 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 371 | 10
PR40023 |  | 32 | 1" | PR | 40023 | C42S1 | ST | 30 | PR40027 | 32-R-4001 | 30.0/30.0 | 150.0/-45.0 | 20.0 | 60.0 |  | 45 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 60 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 364 | 10
PR40026 |  | 32 | 3/4" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR40026 |  | 32 | 1-1/2" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
LA16023 |  | 32 | 1" | LA | 16023 | 4CS2 | ET | 30 | LA16003 | LA16024 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16024 |  | 32 | 1-1/2" | LA | 16024 | 4CS2 | ET | 30 | LA16023 | LA16022 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16024 |  | 32 | 2" | LA | 16024 | 4CS2 | ET | 30 | LA16023 | LA16022 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16025 |  | 32 | 1" | LA | 16025 | 1FS4 | ET | 30 | LA16010 | LA16026 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16026 |  | 32 | 1-1/2" | LA | 16026 | 1FS4 | ET | 30 | LA16025 | LA16027 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16027 |  | 32 | 3/4" | LA | 16027 | 1FS4 | ET | 30 | LA16026 | 32-P-1600A | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16028 |  | 32 | 1/2" | LA | 16028 | 1FS4 | ET | 30 | LA16030 | 32-P-1600B | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16028 |  | 32 | 1-1/2" | LA | 16028 | 1FS4 | ET | 30 | LA16030 | 32-P-1600B | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16030 |  | 32 | 1-1/2" | LA | 16030 | 1FS4 | ET | 30 | LA16029 | LA16028 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16030 |  | 32 | 2" | LA | 16030 | 1FS4 | ET | 30 | LA16029 | LA16028 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16031 |  | 32 | 1" | LA | 16031 | 1FS4 | ET | 30 | LA16011 | LA23006 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA21003 |  | 32 | 1/2" | LA | 21003 | 1FS4 | ET | 30 | LA16031 | P23017 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.16 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA21004 |  | 32 | 1/2" | LA | 21004 | 1FS4 | ET | 30 | 32-R-2100 | 32-R-2100 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.12 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA21004 |  | 32 | 1" | LA | 21004 | 1FS4 | ET | 30 | 32-R-2100 | 32-R-2100 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.12 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA23006 |  | 32 | 1" | LA | 23006 | 1FS4 | ET | 30 | LA16031 | LA23004 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.16 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
CWR88001 | 08 | 32 | 3" | CWR | 88001 | B-1 | N | 0 | 32-E-8005 | CWR88003 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.67 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR88003 | 08 | 32 | 3/4" | CWR | 88003 | B-1 | N | 0 | CWR88001 | VA88001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.67 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89008 | 08 | 32 | 1-1/2" | CWR | 89008 | B-1 | N | 0 | PX86018 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89009 | 08 | 32 | 16" | CWR | 89009 | B-1 | N | 0 | TP-N50904 (E-8900A) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68O | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89021 | 08 | 32 | 4" | CWR | 89021 | B-1 | N | 0 | TP-N60104 (32-E-8906) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68Q | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89022 | 08 | 32 | 6" | CWR | 89022 | B-1 | N | 0 | TP-N20402 (32-E-8902) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68D | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89025 | 08 | 32 | 2" | CWR | 89025 | B-1 | N | 0 | TP-N21106 (E-8903) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68E | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
BDL43021 |  | 32 | 3/4" | BDL | 43021 | B32S1 | P | 50 | PR43035 | BDL22020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43021 |  | 32 | 1" | BDL | 43021 | B32S1 | P | 50 | PR43035 | BDL22020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43022 | 08 | 32 | 1" | BDL | 43022 | B32S1 | N | 0 | PR43031 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43023 | 08 | 32 | 1/2" | BDL | 43023 | B32S1 | N | 0 | 32-P-4300 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43023 | 08 | 32 | 1" | BDL | 43023 | B32S1 | N | 0 | 32-P-4300 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43024 | 08 | 32 | 1/2" | BDL | 43024 | B32S1 | N | 0 | PR43041 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43025 | 08 | 32 | 3/4" | BDL | 43025 | B32S1 | N | 0 | PR43042 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43025 | 08 | 32 | 1" | BDL | 43025 | B32S1 | N | 0 | PR43042 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43026 | 08 | 32 | 1" | BDL | 43026 | B32S1 | N | 0 | PR43050 | BDL34016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL50001 |  | 32 | 6" | BDL | 50001 | B4S1 | ST | 30 | PR50015 | FL60001 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.34 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL50002 | 08 | 32 | 6" | BDL | 50002 | B4S1 | N | 0 | PR50012 | BDL51009 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.35 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51009 |  | 32 | 6" | BDL | 51009 | B4S1 | ST | 30 | BDL50002 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51015 |  | 32 | 6" | BDL | 51015 | B4S1 | ST | 30 | BDL51009 | FL60001 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51017 | 08 | 32 | 2" | BDL | 51017 | B4S1 | N | 0 | PW51013 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51018 |  | 32 | 3" | BDL | 51018 | B4S1 | ST | 30 | PW51014 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51020 |  | 32 | 1-1/2" | BDL | 51020 | B4S1 | ST | 30 | 32-D-5104 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL51021 |  | 32 | 1" | BDL | 51021 | B4S1 | ST | 30 | 32-D-5104 | ACW | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
FW68C12 | 08 | 32 | 3/4" | FW | 68C12 | B-13 | N | 0 | 32-XV-6801A | FW68C11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68C13 | 08 | 32 | 3/4" | FW | 68C13 | B-13 | N | 0 | 32-XV-6802A | FW68C11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68D01 | 08 | 45 | 4" | FW | 68D01 | B-7 | N | 0 | FW68D09 | 45-XV-6815A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D02 | 08 | 45 | 1/2" | FW | 68D02 | B-7 | N | 0 | FW68D09 | 45-XV-6816A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D03 | 08 | 45 | 1/2" | FW | 68D03 | B-7 | N | 0 | FW68D09 | 45-XV-6817A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D04 | 08 | 45 | 4" | FW | 68D04 | B-7 | N | 0 | FW68D09 | 45-XV-6818A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D05 | 08 | 45 | 4" | FW | 68D05 | B-13 | N | 0 | 45-XV-6818A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68D06 | 08 | 45 | 4" | FW | 68D06 | B-13 | N | 0 | 45-XV-6817A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68D07 | 08 | 45 | 4" | FW | 68D07 | B-13 | N | 0 | 45-XV-6816A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68D09 | 08 | 45 | 3/4" | FW | 68D09 | B-7 | N | 0 | FW68A56 | FW68D01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D09 | 08 | 45 | 8" | FW | 68D09 | B-7 | N | 0 | FW68A56 | FW68D01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D10 | 08 | 45 | 1" | FW | 68D10 | B-13 | N | 0 | HEADER | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68E02 | 08 | 32 | 3/4" | FW | 68E02 | B-7 | N | 0 | FW68E01 | INSPECTOR TEST VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E03 | 08 | 32 | 1" | FW | 68E03 | B-7 | N | 0 | FW68E13 | AIR RELIEF VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E03 | 08 | 32 | 3" | FW | 68E03 | B-7 | N | 0 | FW68E13 | AIR RELIEF VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E04 | 08 | 32 | 3/4" | FW | 68E04 | B-7 | N | 0 | FW68E41 | FW68E03 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E05 | 08 | 32 | 2" | FW | 68E05 | B-7 | N | 0 | FW68E41 | FW68E13 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
IA62097 | 08 | 32 | 1-1/2" | IA | 62097 | B-13 | N | 0 | IA62076 | 20 LTR TANK | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62098 | 08 | 32 | 3/4" | IA | 62098 | B-13 | N | 0 | IA620A0 | IA810103 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62099 | 08 | 32 | 3/4" | IA | 62099 | B-13 | N | 0 | IA620A0 | 32-Z-8114/TP-051 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620A0 | 08 | 32 | 3/4" | IA | 620A0 | B-13 | N | 0 | IA89037 | 32-PK-8102 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620A0 | 08 | 32 | 1" | IA | 620A0 | B-13 | N | 0 | IA89037 | 32-PK-8102 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620AD | 08 | 32 | 3/4" | IA | 620AD | B-13 | N | 0 | IA62083 | 32-IAT-090 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AF | 08 | 32 | 3/4" | IA | 620AF | B-13 | N | 0 | IA62081 | 32-IAT-081 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AH | 08 | 32 | 3/4" | IA | 620AH | B-13 | N | 0 | IA62081 | 32-IAT-147 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AI | 08 | 32 | 3/4" | IA | 620AI | B-13 | N | 0 | IA62085 | 32-IAT-137 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AK | 08 | 32 | 3/4" | IA | 620AK | B-13 | N | 0 | IA620AX | 32-IAT-138 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AL | 08 | 32 | 3/4" | IA | 620AL | B-13 | N | 0 | IA620AX | 32-IAT-058 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AQ | 08 | 32 | 1-1/2" | IA | 620AQ | B-13 | N | 0 | IA62083 | 32-IAT-089 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AV | 08 | 32 | 3/4" | IA | 620AV | B-13 | N | 0 | IA620AQ | 32-IAT-083 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AW | 08 | 32 | 3/4" | IA | 620AW | B-13 | N | 0 | IA620AP | 32-IAT-065 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AX | 08 | 32 | 1-1/2" | IA | 620AX | B-13 | N | 0 | IA62085 | 32-IAT-137 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AZ | 08 | 32 | 3/4" | IA | 620AZ | B-13 | N | 0 | IA62081 | 32-IAT-063 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA68C02 | 08 | 32 | 1" | IA | 68C02 | B-13 | N | 0 | IA68C05 | AIR MAINTENANCE DEVICE | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-18 |  | - | N | 000 | - | 200
DO12034 | 08 | 32 | 1/2" | DO | 12034 | 1CS2 | N | 0 | 32-S-1200C | N12030 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12036 |  | 32 | 1" | DO | 12036 | 1CS2 | ET | 30 | 32-D-1200C | 32-S-1200C | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DW01001 | 08 | 32 | 3/4" | DW | 01001 | B-13 | IS | 50 | DW220003 OSBL LINE | DW69B05 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.2 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW01001 | 08 | 32 | 3" | DW | 01001 | B-13 | IS | 50 | DW220003 OSBL LINE | DW69B05 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.2 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69022 | 08 | 32 | 1-1/2" | DW | 69022 | B-13 | IS | 50 | DW01001 | DW69024 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69023 | 08 | 32 | 3/4" | DW | 69023 | B-13 | IS | 50 | DW69022 | TO RACKROOM | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A02 | 08 | 32 | 1-1/2" | DW | 69A02 | B-13 | IS | 50 | DW01001 | 32-ES-6908 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A03 | 08 | 32 | 1-1/2" | DW | 69A03 | B-13 | IS | 50 | DW01001 | 32-ES-6907 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A04 | 08 | 32 | 1-1/2" | DW | 69A04 | B-13 | IS | 50 | DW01001 | 32-ES-6906 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A06 | 08 | 32 | 1-1/2" | DW | 69A06 | B-13 | IS | 50 | DW01001 | 32-ES-6916 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A10 | 08 | 32 | 1-1/2" | DW | 69A10 | B-13 | IS | 50 | DW01001 | 32-ES-6902 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A12 | 08 | 32 | 1-1/2" | DW | 69A12 | B-13 | IS | 50 | DW01001 | 32-ES-6904 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B01 | 08 | 32 | 1-1/2" | DW | 69B01 | B-13 | N | 0 | DW69B02 | 32-ES-6912 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B07 | 08 | 32 | 1-1/2" | DW | 69B07 | B-13 | N | 0 | DW69B05 | 32-ES-6914 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B09 | 08 | 32 | 1-1/2" | DW | 69B09 | B-13 | N | 0 | DW69B05 | 32-ES-6915 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B13 | 08 | 32 | 2" | DW | 69B13 | B-13 | N | 0 | DW01001 | VZ92003 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
IA68N65 | 08 | 32 | 1" | IA | 68N65 | B-13 | N | 0 | IA68N06 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68O04 | 08 | 32 | 1" | IA | 68O04 | B-13 | N | 0 | IA68O03 | IA68O03 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68O07 | 08 | 32 | 1" | IA | 68O07 | B-13 | N | 0 | IA68C12 | FUSIBLE GAS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68O09 | 08 | 32 | 1" | IA | 68O09 | B-13 | N | 0 | IA68C12 | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68O12 | 08 | 32 | 1" | IA | 68O12 | B-13 | N | 0 | IA68O10 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
CHWS21006 |  | 32 | 3/4" | CHWS | 21006 | D3S1 | CF | 25 | CHWS61023 | 32-E-2100 | 55.0 | 150.0 | 4.0 | 2.0 |  | 82.51 | 153.15 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.12 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 1050
CHWS21006 |  | 32 | 6" | CHWS | 21006 | D3S1 | CF | 40 | CHWS61023 | 32-E-2100 | 55.0 | 150.0 | 4.0 | 2.0 |  | 82.51 | 153.15 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.12 | 2 | II | MOD.A2 | Y | 20 | Y | 32-U-023-01 |  | E | N | 010 | N | 1050
CHWS24002 |  | 32 | 3" | CHWS | 24002 | C42S1 | CF | 25 | CHWS61025 | 32-E-2404 | 42.0/42.0 | 150.0/-45.0 | 2.0 | 2.0 |  | 63.01 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.19 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-01 |  | M | N | 010 | N | 1053
CHWS43010 |  | 32 | 1" | CHWS | 43010 | C42S1 | CF | 25 | CHWS61029 | 32-E-4302 | 28.0/28.0 | 180.0/-45.0 | 2.0 | 2.0 |  | 42.12 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.33 | 2 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | M | N | 010 | N | 1051
CHWS43010 |  | 32 | 6" | CHWS | 43010 | C42S1 | CF | 40 | CHWS61029 | 32-E-4302 | 28.0/28.0 | 180.0/-45.0 | 2.0 | 2.0 |  | 42.12 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.33 | 2 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | M | N | 010 | N | 1051
CHWS61001 |  | 32 | 8" | CHWS | 61001 | B-1 | CF | 40 | 32-D-6100 | 32-P-6100A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61002 |  | 32 | 3/4" | CHWS | 61002 | B-1 | CF | 25 | 32-P-6100B | CHWS61015 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61002 |  | 32 | 3" | CHWS | 61002 | B-1 | CF | 25 | 32-P-6100B | CHWS61015 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61002 |  | 32 | 10" | CHWS | 61002 | B-1 | CF | 40 | 32-P-6100B | CHWS61015 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
FW68Z01 | 08 | 45 | 4" | FW | 68Z01 | B-13 | N | 0 | DELUGE VALVE | WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | Y | 000 | - | 74
FW68Z02 | 08 | 45 | 2" | FW | 68Z02 | B-13 | N | 0 | FW68Z01 | WC | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | Y | 000 | - | 74
FW68Z03 | 08 | 45 | 2" | FW | 68Z03 | B-13 | N | 0 | WC | FW68Z02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | Y | 000 | - | 74
HCM00001 | 08 | 45 | 1-1/2" | HCM | 00001 | B4S1 | N | 0 | FUEL TANK | FUEL TANK | 5.0 | 120.0 | 0.8 | 85.0 |  | 7.5 | 29.4 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.106 | 1 | I | MOD.A | Y | 1 | N | 45-U-002-01 |  | C | N | 141 | N | 383 | 10
HCM22003 |  | 32 | 6" | HCM | 22003 | D20S1 | P | 50 | PR33019 | P23027 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.13 | 1 | III | MOD.G | Y | 1 | Y | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM23003 |  | 32 | 4" | HCM | 23003 | C42S1 | HB | 40 | 32-S-2300 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
BDL01034 | 08 | 32 | 3/4" | BDL | 01034 | B32S1 | N | 0 | PR01002 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01034 | 08 | 32 | 1" | BDL | 01034 | B32S1 | N | 0 | PR01002 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01036 |  | 32 | 1" | BDL | 01036 | B4S1 | P | 50 | HD01001 | BDL01039 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL01037 |  | 32 | 3/4" | BDL | 01037 | B4S1 | P | 50 | VZ01003 | BDL24062 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL01037 |  | 32 | 1" | BDL | 01037 | B4S1 | P | 50 | VZ01003 | BDL24062 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL01039 | 08 | 32 | 2" | BDL | 01039 | B32S1 | N | 0 | BDL01003 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01042 | 08 | 32 | 2" | BDL | 01042 | B32S1 | N | 0 | BU01002 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01043 | 08 | 32 | 3/4" | BDL | 01043 | B32S1 | N | 0 | BDL01035 | BDL01042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01043 | 08 | 32 | 2" | BDL | 01043 | B32S1 | N | 0 | BDL01035 | BDL01042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01044 | 08 | 32 | 1/2" | BDL | 01044 | B32S1 | N | 0 | PR01001 | BDL01034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL14002 | 08 | 32 | 1" | BDL | 14002 | B4S1 | N | 0 | N14007 | BDL60023 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.8 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL20001 | 08 | 32 | 1" | BDL | 20001 | B32S1 | N | 0 | O20009 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.11 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL20002 | 08 | 32 | 1/2" | BDL | 20002 | B32S1 | N | 0 | O20008 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.11 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL20002 | 08 | 32 | 1" | BDL | 20002 | B32S1 | N | 0 | O20008 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.11 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL21008 | 08 | 32 | 3/4" | BDL | 21008 | B32S1 | N | 0 | PR22012 | BDL24073 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL21009 | 08 | 32 | 3/4" | BDL | 21009 | B32S1 | N | 0 | PR21010 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24090 | 08 | 32 | 3/4" | BDL | 24090 | B32S1 | N | 0 | PR24037 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24090 | 08 | 32 | 1" | BDL | 24090 | B32S1 | N | 0 | PR24037 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24091 | 08 | 32 | 3/4" | BDL | 24091 | B32S1 | N | 0 | PR24040 | BDL24092 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24091 | 08 | 32 | 1" | BDL | 24091 | B32S1 | N | 0 | PR24040 | BDL24092 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24092 | 08 | 32 | 1" | BDL | 24092 | B32S1 | N | 0 | BDL24091 | BDL23055 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24093 | 08 | 32 | 3/4" | BDL | 24093 | B32S1 | N | 0 | PR24044 | BDL24092 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24095 | 08 | 32 | 1" | BDL | 24095 | B32S1 | N | 0 | BDL22020 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
N50002 | 08 | 32 | 2" | N | 50002 | B-1 | N | 0 | N67052 | PR50010 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N50003 | 08 | 32 | 1-1/2" | N | 50003 | B-1 | N | 0 | N67052 | VZ50008 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N50003 | 08 | 32 | 3" | N | 50003 | B-1 | N | 0 | N67052 | VZ50008 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N64001 | 08 | 32 | 1/2" | N | 64001 | B-1 | N | 0 | N67041 | 32-AFR-6401 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N65001 | 08 | 32 | 1/4" | N | 65001 | B-1 | N | 0 | N67078 | TUBING Ø1/4" | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-01 |  | E | N | 000 | N | 140
PR33004 |  | 32 | 1-1/2" | PR | 33004 | C42S1 | ST | 30 | PR33003 | TP-003 (PR530129) | 25.0/25.0 | -45.0/120.0 | 3.0 | 20.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 20 | sh.25 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 371 | 10
PR33005 |  | 32 | 1" | PR | 33005 | C42S1 | HB | 30 | PR33002 | SL21002 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33006 |  | 32 | 3/4" | PR | 33006 | C42S1 | HB | 30 | 32-D-3300 | BDL33007 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
JWS32001 | 08 | 32 | 2" | JWS | 32001 | C3S1 | N | 0 | JWS64019 | 32-E-3200 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS32001 | 08 | 32 | 4" | JWS | 32001 | C3S1 | N | 0 | JWS64019 | 32-E-3200 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS32002 | 08 | 32 | 1" | JWS | 32002 | B-1 | N | 0 | JWS64021 | TP-21A, JWS320116, JWS320316 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS33001 | 08 | 32 | 3" | JWS | 33001 | C3S1 | N | 0 | JWS64022 | 32-E-3300 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS43001 | 08 | 32 | 3/4" | JWS | 43001 | C3S1 | N | 0 | JWS64027 | 32-E-4301 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.33 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS50001 | 08 | 32 | 3/4" | JWS | 50001 | B-1 | N | 0 | JWS52001 | COOLING DRUM | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS50001 | 08 | 32 | 1-1/2" | JWS | 50001 | B-1 | N | 0 | JWS52001 | COOLING DRUM | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS52001 | 08 | 32 | 3/4" | JWS | 52001 | B-1 | N | 0 | JWS64054 | Seal Pot | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
N80015 | 08 | 32 | 1/2" | N | 80015 | 1CS2 | N | 0 | N67077 | 32-S-8000 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80020 | 08 | 32 | 1/2" | N | 80020 | 1CS2 | N | 0 | N67074 | 32-V-8000A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80021 | 08 | 32 | 1/2" | N | 80021 | 1CS2 | N | 0 | N67076 | 32-V-8000B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80022 | 08 | 32 | 1/2" | N | 80022 | 1CS2 | N | 0 | N67079 | 32-V-8001B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80022 | 08 | 32 | 1-1/2" | N | 80022 | 1CS2 | N | 0 | N67079 | 32-V-8001B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80023 | 08 | 32 | 1/2" | N | 80023 | 1CS2 | N | 0 | N67075 | 32-V-8001A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80023 | 08 | 32 | 1-1/2" | N | 80023 | 1CS2 | N | 0 | N67075 | 32-V-8001A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80024 | 08 | 32 | 2" | N | 80024 | 1CS2 | N | 0 | N80018 | TP-005 (N81030) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N80026 | 08 | 32 | 2" | N | 80026 | B-1 | N | 0 | 32-D-8001 | 32-AT-5212 | 4.5/-0.5 | 110.0/110.0 | 2.75 | 60.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 60 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-060-01 |  | E | N | 000 | N | 149
N81014 | 08 | 32 | 1/2" | N | 81014 | 1CS2 | N | 0 | N89005 | 32-PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.62 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
LA23007 |  | 32 | 1/2" | LA | 23007 | 1FS4 | ET | 30 | LA31001 | HCM24095 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.15 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA84008 |  | 32 | 1/2" | LA | 84008 | 4CS2 | ET | 30 | 32-S-8402A | TP-N11216 (32-H-8901) | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84010 |  | 32 | 3/4" | LA | 84010 | 4CS2 | ET | 30 | 32-P-8402A | 32-S-8402A | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84011 |  | 32 | 1/2" | LA | 84011 | 4CS2 | ET | 30 | 32-D-8402 | 32-P-8402A | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 601
LA84012 |  | 32 | 1" | LA | 84012 | 4CS2 | ET | 30 | DRUM | 32-P-8403 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84013 |  | 32 | 1/2" | LA | 84013 | 4CS2 | ET | 30 | 32-P-8403 | 32-D-8402 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84013 |  | 32 | 1" | LA | 84013 | 4CS2 | ET | 30 | 32-P-8403 | 32-D-8402 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84032 |  | 32 | 1/2" | LA | 84032 | 4CS2 | ET | 30 | LA84011 | 32-P-8402B | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 601
LA84032 |  | 32 | 3/4" | LA | 84032 | 4CS2 | ET | 30 | LA84011 | 32-P-8402B | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 601
LA84033 |  | 32 | 1" | LA | 84033 | 4CS2 | ET | 30 | LA84013 | LA84034 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
BDL51021 | 08 | 32 | 2" | BDL | 51021 | B4S1 | N | 0 | 32-D-5104 | ACW | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 1 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL51022 | 08 | 32 | 1/2" | BDL | 51022 | B4S1 | N | 0 | PR51018 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51023 | 08 | 32 | 1" | BDL | 51023 | B4S1 | N | 0 | PR51017 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.28A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53001 | 08 | 32 | 3" | BDL | 53001 | B4S1 | ST | 30 | TP-006, PR530117 | BDL51020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53002 | 08 | 32 | 1/2" | BDL | 53002 | B4S1 | N | 0 | PR53002 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53003 | 08 | 32 | 1/2" | BDL | 53003 | B4S1 | N | 0 | PR53006 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53003 | 08 | 32 | 1-1/2" | BDL | 53003 | B4S1 | N | 0 | PR53006 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53004 | 08 | 32 | 1" | BDL | 53004 | B4S1 | N | 0 | PR53004 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53005 | 08 | 32 | 3/4" | BDL | 53005 | B4S1 | N | 0 | PR53005 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL53005 | 08 | 32 | 1" | BDL | 53005 | B4S1 | N | 0 | PR53005 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL60001 |  | 32 | 4" | BDL | 60001 | B32S1 | ST | 30 | 32-D-6002 | CANTAINER | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.41 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60002 | 08 | 32 | 10" | BDL | 60002 | B32S1 | N | 0 | BDL60029 | FL60001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60002 | 08 | 32 | 24" | BDL | 60002 | B32S1 | N | 0 | BDL60029 | FL60001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60020 | 08 | 32 | 16" | BDL | 60020 | B32S1 | N | 0 | BDL33002 | FL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL60026 | 08 | 32 | 12" | BDL | 60026 | B32S1 | N | 0 | HEADER | BDL60029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60028 | 08 | 32 | 2" | BDL | 60028 | B32S1 | N | 0 | BDL20001 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60029 | 08 | 32 | 16" | BDL | 60029 | B32S1 | N | 0 | HEADER | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60029 | 08 | 32 | 18" | BDL | 60029 | B32S1 | N | 0 | HEADER | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60030 | 08 | 32 | 10" | BDL | 60030 | B32S1 | N | 0 | BDL32029 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FW68E06 | 08 | 32 | 3/4" | FW | 68E06 | B-7 | N | 0 | FW68E41 | FW68E13 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E08 | 08 | 32 | 2" | FW | 68E08 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E09 | 08 | 32 | 3/4" | FW | 68E09 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E10 | 08 | 32 | 3/4" | FW | 68E10 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E11 | 08 | 32 | 2" | FW | 68E11 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E12 | 08 | 32 | 3/4" | FW | 68E12 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E13 | 08 | 32 | 4" | FW | 68E13 | B-7 | N | 0 | FW68E02 | FW68E03 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E17 | 08 | 32 | 3/4" | FW | 68E17 | B-7 | N | 0 | FW68E26 | FW68E27 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E18 | 08 | 32 | 3/4" | FW | 68E18 | B-7 | N | 0 | FW68E27 | FW68E26 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E19 | 08 | 32 | 3/4" | FW | 68E19 | B-7 | N | 0 | FW68E27 | FW68E26 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E20 | 08 | 32 | 3" | FW | 68E20 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E21 | 08 | 32 | 2" | FW | 68E21 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E22 | 08 | 32 | 2" | FW | 68E22 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E23 | 08 | 32 | 3/4" | FW | 68E23 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E24 | 08 | 32 | 3/4" | FW | 68E24 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E26 | 08 | 32 | 4" | FW | 68E26 | B-7 | N | 0 | FW68E28 | FW68E17 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E27 | 08 | 32 | 4" | FW | 68E27 | B-7 | N | 0 | FW68E17 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E28 | 08 | 32 | 3/4" | FW | 68E28 | B-7 | N | 0 | FW68E27 | FW68E26 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E41 | 08 | 32 | 4" | FW | 68E41 | B-7 | N | 0 | FW68E03 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68F02 | 08 | 32 | 1-1/2" | FW | 68F02 | B-13 | N | 0 | FW68R06 | FW68R06 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
IA68C09 | 08 | 32 | 1/2" | IA | 68C09 | B-13 | N | 0 | 32-XV-6801A | IA68H12 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68C10 | 08 | 32 | 1/2" | IA | 68C10 | B-13 | N | 0 | 32-XV-6802A | IA68I20 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68C11 | 08 | 32 | 1" | IA | 68C11 | B-13 | N | 0 | 32-XV-6810A | IA68Q06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68C12 | 08 | 32 | 1" | IA | 68C12 | B-13 | N | 0 | 32-XV-6808A | IA68O07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68D02 | 08 | 45 | 1" | IA | 68D02 | B-13 | N | 0 | IA68D05 | IA68D07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68D04 | 08 | 45 | 1" | IA | 68D04 | B-13 | N | 0 | IA68D05 | To Air Maintenance Device | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68D05 | 08 | 45 | 3/4" | IA | 68D05 | B-13 | N | 0 | 20 LTR TANK | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
BDL73047 | 08 | 32 | 3" | BDL | 73047 | B4S1 | N | 0 | BU73042 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73048 | 08 | 32 | 3" | BDL | 73048 | B4S1 | N | 0 | BU73081 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73049 | 08 | 32 | 1" | BDL | 73049 | B4S1 | N | 0 | BU73086 | BDL60024 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73050 | 08 | 32 | 1/2" | BDL | 73050 | B4S1 | N | 0 | BU73084 | BDL60024 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73050 | 08 | 32 | 1" | BDL | 73050 | B4S1 | N | 0 | BU73084 | BDL60024 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73074 | 08 | 32 | 1/2" | BDL | 73074 | B4S1 | N | 0 | BU73088 | BDL73044 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73077 | 08 | 32 | 1/2" | BDL | 73077 | B4S1 | N | 0 | BU73049 | BDL73044 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73078 | 08 | 32 | 3" | BDL | 73078 | B4S1 | N | 0 | BU73043 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73078 | 08 | 32 | 6" | BDL | 73078 | B4S1 | N | 0 | BU73043 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BU01001 | 08 | 32 | 1/2" | BU | 01001 | B32S1 | N | 0 | BU01003 | 32-S-7302B | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.1 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-01 |  | F | N | 140 | N | 731 | 15
DW69B14 | 08 | 32 | 2" | DW | 69B14 | B-13 | N | 0 | DW01001 | 32-ES-6910 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
IA68O15 | 08 | 32 | 1" | IA | 68O15 | B-13 | N | 0 | IA68O18 | IA68O17 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68O18 | 08 | 32 | 1" | IA | 68O18 | B-13 | N | 0 | IA68O09 | IA68O15 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68P03 | 08 | 32 | 1/2" | IA | 68P03 | B-13 | N | 0 | IA68P02 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P06 | 08 | 32 | 1" | IA | 68P06 | B-13 | N | 0 | IA68K09 | IA68P07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P07 | 08 | 32 | 1/2" | IA | 68P07 | B-13 | N | 0 | IA68P06 | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P08 | 08 | 32 | 1/2" | IA | 68P08 | B-13 | N | 0 | IA68P06 | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P09 | 08 | 32 | 1/2" | IA | 68P09 | B-13 | N | 0 | IA68P06 | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P10 | 08 | 32 | 1" | IA | 68P10 | B-13 | N | 0 | IA68P11 | IA68P11 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P12 | 08 | 32 | 1" | IA | 68P12 | B-13 | N | 0 | IA68P13 | IA68P13 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P13 | 08 | 32 | 1/2" | IA | 68P13 | B-13 | N | 0 | IA68P12 | IA68P12 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Q01 | 08 | 32 | 1" | IA | 68Q01 | B-13 | N | 0 | IA68Q05 | IA68Q04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68Q03 | 08 | 32 | 1" | IA | 68Q03 | B-13 | N | 0 | IA68Q04 | IA68Q04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68Q06 | 08 | 32 | 1" | IA | 68Q06 | B-13 | N | 0 | IA68C11 | IA68Q08 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68Q10 | 08 | 32 | 1" | IA | 68Q10 | B-13 | N | 0 | IA68Q08 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68R02 | 08 | 45 | 1-1/2" | IA | 68R02 | B-13 | N | 0 | 20 LTR TANK | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
IA68R03 | 08 | 45 | 1" | IA | 68R03 | B-13 | N | 0 | 45-XV-6821A | IA68F07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-14 |  | - | N | 000 | - | 200
IA68R05 | 08 | 45 | 1" | IA | 68R05 | B-13 | N | 0 | IA68R02 | To Air Maintenance Device | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
IA68R07 | 08 | 45 | 1/2" | IA | 68R07 | B-13 | N | 0 | From Air Maintenance Device | 45-XV-6822A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
IA68R10 | 08 | 45 | 1" | IA | 68R10 | B-13 | N | 0 | 45-XV-6820A | IA68F02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | N | 000 | - | 200
ET71035 | 08 | 32 | 1" | ET | 71035 | D1S1 | N | 0 | ET710135 | ET71036 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 153.15 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 325 | ,10
ET71035 | 08 | 32 | 2" | ET | 71035 | D1S1 | N | 0 | ET710135 | ET71036 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 153.15 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-03 |  | C | N | 041 | N | 325 | ,10
ET71036 | 08 | 32 | 1" | ET | 71036 | D1S1 | ST | 30 | ET71035 | ET71037 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 153.15 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 20 | N | 32-P-006-03 |  | C | N | 041 | N | 325 | ,10
ET71037 | 08 | 32 | 3/4" | ET | 71037 | C3S1 | N | 0 | ET71036 | ET71064 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71037 | 08 | 32 | 2" | ET | 71037 | C3S1 | N | 0 | ET71036 | ET71064 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71038 | 08 | 32 | 2" | ET | 71038 | C3S1 | N | 0 | ET71037 | ET710138 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71039 | 08 | 32 | 3/4" | ET | 71039 | C3S1 | N | 0 | 32-S-7100A | ET40007 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71039 | 08 | 32 | 1" | ET | 71039 | C3S1 | N | 0 | 32-S-7100A | ET40007 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71039 | 08 | 32 | 1-1/2" | ET | 71039 | C3S1 | N | 0 | 32-S-7100A | ET40007 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71039 | 08 | 32 | 3" | ET | 71039 | C3S1 | N | 0 | 32-S-7100A | ET40007 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71039 | 08 | 32 | 4" | ET | 71039 | C3S1 | N | 0 | 32-S-7100A | ET40007 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71042 | 7A | 32 | 3" | ET | 71042 | C3S1 | HA | 70 | ET71079 | 32-T-7110B | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
HCM23003 |  | 32 | 12" | HCM | 23003 | C42S1 | HB | 40 | 32-S-2300 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23004 |  | 32 | 3/4" | HCM | 23004 | C42S1 | HB | 30 | HCM23003 | 32-Z-2300A | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23004 |  | 32 | 6" | HCM | 23004 | C42S1 | HB | 40 | HCM23003 | 32-Z-2300A | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23018 |  | 32 | 3/4" | HCM | 23018 | C42S1 | ST | 30 | HN23007 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23018 |  | 32 | 1-1/2" | HCM | 23018 | C42S1 | ST | 30 | HN23007 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23035 |  | 32 | 3/4" | HCM | 23035 | C42S1 | ST | 30 | HCM23018 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23043 |  | 32 | 1/2" | HCM | 23043 | C42S1 | HB | 30 | HCM23003 | HCM24084 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23044 |  | 32 | 1-1/2" | HCM | 23044 | C42S1 | HB | 30 | HCM32019 | HCM23045 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM23045 |  | 32 | 1-1/2" | HCM | 23045 | 1FS4 | ST | 30 | HCM23044 | HCM23048 | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-047-04 |  | G | N | 141 | N | 332 | 10
HCM23046 |  | 32 | 1" | HCM | 23046 | C42S1 | HB | 30 | HCM24059 | HCM23058 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23046 |  | 32 | 4" | HCM | 23046 | C42S1 | HB | 40 | HCM24059 | HCM23058 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23047 |  | 32 | 1" | HCM | 23047 | 1FS4 | ST | 30 | HCM23045 | HCM23046 | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-008-01 |  | G | N | 141 | N | 332 | 10
HCM23048 |  | 32 | 1" | HCM | 23048 | 1FS4 | JP | 0 | JLS23008 | JLS23008 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23048 | 08 | 32 | 1-1/2" | HCM | 23048 | 1FS4 | N | 0 | JLS23008 | JLS23008 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 5 | Y | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23050 | 08 | 32 | 1/2" | HCM | 23050 | 1FS4 | N | 0 | HCM23049 | HCM23052 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23050 | 08 | 32 | 1-1/2" | HCM | 23050 | 1FS4 | N | 0 | HCM23049 | HCM23052 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 5 | Y | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
FL60001 |  | 32 | 1" | FL | 60001 | B32S1 | HB | 30 | BDL60002 | 32-D-6001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | III | MOD.G | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 490 | 10
FL60001 |  | 32 | 24" | FL | 60001 | B32S1 | HB | 40 | BDL60002 | 32-D-6001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | III | MOD.G | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 490 | 10
FL60002 | 08 | 32 | 24" | FL | 60002 | B32S1 | N | 0 | 32-D-6001 | FL01001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
HCM24097 |  | 32 | 2" | HCM | 24097 | D20S1 | P | 50 | 32-T-2400 | HCM24089 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24097 |  | 32 | 6" | HCM | 24097 | D20S1 | P | 50 | 32-T-2400 | HCM24089 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24098 | 08 | 32 | 1" | HCM | 24098 | 3FS4 | HB | 30 | HCM24061 | HCM24065 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM24099 |  | 32 | 3/4" | HCM | 24099 | D20S1 | ST | 30 | 32-T-2400 | BDL24098 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24099 |  | 32 | 2" | HCM | 24099 | D20S1 | ST | 30 | 32-T-2400 | BDL24098 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
BDL24096 | 08 | 32 | 1" | BDL | 24096 | B32S1 | N | 0 | HCM24083 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24097 | 08 | 32 | 3/4" | BDL | 24097 | B32S1 | N | 0 | HCM24095 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24098 |  | 32 | 6" | BDL | 24098 | B32S1 | ST | 30 | HCM24099 | FL60001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24099 | 08 | 32 | 3/4" | BDL | 24099 | B32S1 | N | 0 | HCM24099 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL26003 | 08 | 32 | 1/2" | BDL | 26003 | B32S1 | N | 0 | BDL26004 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL26003 | 08 | 32 | 1" | BDL | 26003 | B32S1 | N | 0 | BDL26004 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL26004 | 08 | 32 | 1" | BDL | 26004 | B32S1 | N | 0 | CO26029 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.22 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31004 | 08 | 32 | 3/4" | BDL | 31004 | B32S1 | N | 0 | HCM31012 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31004 | 08 | 32 | 1" | BDL | 31004 | B32S1 | N | 0 | HCM31012 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31022 | 08 | 32 | 3/4" | BDL | 31022 | B32S1 | N | 0 | P31008 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31022 | 08 | 32 | 1" | BDL | 31022 | B32S1 | N | 0 | P31008 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31023 | 08 | 32 | 8" | BDL | 31023 | B32S1 | N | 0 | 32-S-3100 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31023 | 08 | 32 | 14" | BDL | 31023 | B32S1 | N | 0 | 32-S-3100 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31024 | 08 | 32 | 1" | BDL | 31024 | B32S1 | N | 0 | PR31015 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31025 | 08 | 32 | 3" | BDL | 31025 | B32S1 | N | 0 | PR24032 | BDL31031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31026 | 08 | 32 | 1" | BDL | 31026 | B32S1 | N | 0 | BDL43015 | BDL34016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31027 | 08 | 32 | 1" | BDL | 31027 | B32S1 | N | 0 | P31012 | BDL34016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31028 | 08 | 32 | 1/2" | BDL | 31028 | B32S1 | N | 0 | CO31001 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
N66001 | 08 | 32 | 3/4" | N | 66001 | 1CS2 | N | 0 | N67070 | 32-D-6600 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.46 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-03 |  | M | N | 000 | N | 166
N66002 | 08 | 32 | 1/2" | N | 66002 | B-1 | N | 0 | N67070 | N66003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.46 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N66003 | 08 | 32 | 1/2" | N | 66003 | 1CS2 | N | 0 | N66002 | VA66002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.46 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-03 |  | M | N | 000 | N | 166
N67000 | 08 | 32 | 1/2" | N | 67000 | B-1 | N | 0 | N67003 | N33003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67002 | 08 | 32 | 1/2" | N | 67002 | B-1 | N | 0 | N67055 | N16003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67002 | 08 | 32 | 1" | N | 67002 | B-1 | N | 0 | N67055 | N16003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67003 | 08 | 32 | 2" | N | 67003 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N6700A | 08 | 32 | 1" | N | 6700A | B-1 | N | 0 | N01001 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700D | 08 | 32 | 3/4" | N | 6700D | B-1 | N | 0 | N6700C | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700E | 08 | 32 | 3/4" | N | 6700E | B-1 | N | 0 | N6700C | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700H | 08 | 32 | 1" | N | 6700H | B-1 | N | 0 | N01001 | TP-001 (N610250) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700L | 08 | 32 | 1/2" | N | 6700L | B-1 | N | 0 | N89098 | TP-N60246 (32-D-8908) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N6700M | 08 | 32 | 1" | N | 6700M | B-1 | N | 0 | N01001 | 32-AH-0001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700N | 08 | 32 | 1/2" | N | 6700N | B-1 | N | 0 | 32-AFR-7201 | N67003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.51 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N6700P | 08 | 32 | 1/2" | N | 6700P | B-1 | N | 0 | N67046 | FLANGE | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700Q | 08 | 32 | 1/2" | N | 6700Q | B-1 | N | 0 | N67017 | 32-AFR-5101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700V | 08 | 32 | 3/4" | N | 6700V | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N6700W | 08 | 32 | 3/4" | N | 6700W | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N6700X | 08 | 32 | 3/4" | N | 6700X | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
JWS52001 | 08 | 32 | 1-1/2" | JWS | 52001 | B-1 | N | 0 | JWS64054 | Seal Pot | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS52002 | 08 | 32 | 3/4" | JWS | 52002 | B-1 | N | 0 | JWS52001 | Seal Pot | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS52003 | 08 | 32 | 1-1/2" | JWS | 52003 | B-1 | N | 0 | JWS64059 | 32-E-5252A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS52004 | 08 | 32 | 1-1/2" | JWS | 52004 | B-1 | N | 0 | JWS52003 | 32-E-5252B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS61001 | 08 | 32 | 1-1/2" | JWS | 61001 | C3S1 | N | 0 | JWS64061 | TI-6176 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.42D | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS63004 | 08 | 32 | 2" | JWS | 63004 | B-1 | N | 0 | JWS64056 | JWS63003 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64001 | 08 | 32 | 3/4" | JWS | 64001 | B-1 | N | 0 | 32-E-6400A | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64001 | 08 | 32 | 20" | JWS | 64001 | B-1 | N | 0 | 32-E-6400A | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64003 | 08 | 32 | 1-1/2" | JWS | 64003 | B-1 | N | 0 | 32-E-6400C | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64004 | 08 | 32 | 3" | JWS | 64004 | UGB-1PE | N | 0 | JWS64001 | JWS64073 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
JWS64004 | 08 | 32 | 32" | JWS | 64004 | UGB-1PE | N | 0 | JWS64001 | JWS64073 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
JWS64005 | 08 | 32 | 1" | JWS | 64005 | B-1 | N | 0 | 32-Z-6400 | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64007 | 08 | 32 | 20" | JWS | 64007 | B-1 | N | 0 | JWS64004 | 32-P-6400B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
N81017 | 08 | 32 | 1/2" | N | 81017 | 1CS2 | N | 0 | N89009 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81030 | 08 | 32 | 4" | N | 81030 | 1CS2 | N | 0 | TP-001 (N80024) | 32-D-8002A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | I | MOD.A | Y | 5 | N | 32-P-060-01_B |  | M | N | 000 | N | 166
N81040 | 08 | 32 | 1/2" | N | 81040 | 1CS2 | N | 0 | N89057 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81043 | 08 | 32 | 3/4" | N | 81043 | 1CS2 | N | 0 | N89059 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81044 | 08 | 32 | 3/4" | N | 81044 | 1CS2 | N | 0 | N89055 | 32-PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60A | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81048 | 08 | 32 | 1/2" | N | 81048 | 1CS2 | N | 0 | N89051 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-03 |  | M | N | 000 | N | 166
N81050 | 08 | 32 | 1/2" | N | 81050 | 1CS2 | N | 0 | N89050 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-03 |  | M | N | 000 | N | 166
N81053 | 08 | 32 | 1/2" | N | 81053 | 1CS2 | N | 0 | N89065 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-03 |  | M | N | 000 | N | 166
PR53003 | 08 | 32 | 3" | PR | 53003 | B4S1 | N | 0 | PR51015 | PR53004 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
PR53004 | 08 | 32 | 2" | PR | 53004 | B4S1 | P | 50 | TP-002 (PR530113) | PR53005 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
PR53005 | 08 | 32 | 3/4" | PR | 53005 | B4S1 | N | 0 | PR53004 | OG53003 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
PR53005 | 08 | 32 | 3" | PR | 53005 | B4S1 | N | 0 | PR53004 | OG53003 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
LA84034 |  | 32 | 2" | LA | 84034 | 4CS2 | ET | 30 | LA84033 | LA84012 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84035 |  | 32 | 3/4" | LA | 84035 | 4CS2 | ET | 30 | LA84010 | LA84036 | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84037 |  | 32 | 3/4" | LA | 84037 | 4CS2 | ET | 30 | LA84039 | LA84038 | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84039 |  | 32 | 1" | LA | 84039 | 4CS2 | ET | 30 | 32-P-8402B | 32-Z-8402B | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LC00C01 |  | 32 | 3/4" | LC | 00C01 | B-5 | P | 50 | LC63034 | LC91B01 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 19-U-002-01 |  | E | N | 000 | N | 136
LC00C01 |  | 32 | 1" | LC | 00C01 | B-5 | P | 50 | LC63034 | LC91B01 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 19-U-002-01 |  | E | N | 000 | N | 136
LC00C01 |  | 32 | 2" | LC | 00C01 | B-5 | P | 50 | LC63034 | LC91B01 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 19-U-002-01 |  | E | N | 000 | N | 136
LC02001 |  | 32 | 2" | LC | 02001 | B-5 | HB | 40 | LC72002 | LC63059 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS23014 |  | 32 | 1/2" | LS | 23014 | B-5 | HB | 60 | 32-D-2300 | LC23033 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.17 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23014 |  | 32 | 1-1/2" | LS | 23014 | B-5 | HB | 70 | 32-D-2300 | LC23033 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.17 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23018 |  | 32 | 1" | LS | 23018 | B-5 | HB | 70 | 32-E-2301 | LC23017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.18 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23018 |  | 32 | 2" | LS | 23018 | B-5 | HB | 80 | 32-E-2301 | LC23017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.18 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23020 |  | 32 | 3/4" | LS | 23020 | B-5 | HB | 60 | JLS23009 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
FW68A01 | 08 | 45 | 20" | FW | 68A01 | PEB-69 | N | 0 | FW68A17 | IP-TCM/OFF-PIP-005 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | TP-FW-01 |  | - | N | 000 | - | 73 | 76
FW68A03 | 08 | 45 | 18" | FW | 68A03 | PEB-69 | N | 0 | FW68A10 | FW68A10 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A04 | 08 | 45 | 6" | FW | 68A04 | PEB-69 | N | 0 | FW68A03 | FW68A90 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A08 | 08 | 45 | 6" | FW | 68A08 | PEB-69 | N | 0 | FW68A03 | FW68A92 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A0C | 08 | 45 | 6" | FW | 68A0C | UGB-1PE | N | 0 | FW68A61 | FW68A0D | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0D | 08 | 45 | 6" | FW | 68A0D | B-7 | N | 0 | FW68A0C | FW68A0W | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A0E | 08 | 45 | 6" | FW | 68A0E | UGB-1PE | N | 0 | FW68A59 | 45-HM-6803 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0F | 08 | 45 | 6" | FW | 68A0F | UGB-1PE | N | 0 | FW68A38 | FW68A39 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0I | 08 | 45 | 16" | FW | 68A0I | UGB-1PE | N | 0 | FW68A67 | FW68A68 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0J | 08 | 45 | 6" | FW | 68A0J | UGB-1PE | N | 0 | FW68A49 | 45-HM-6804 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0L | 08 | 45 | 6" | FW | 68A0L | UGB-1PE | N | 0 | FW68A51 | 45-HM-6806 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0M | 08 | 45 | 12" | FW | 68A0M | UGB-1PE | N | 0 | FW68A85 | FW68A86 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0N | 08 | 45 | 12" | FW | 68A0N | UGB-1PE | N | 0 | FW68A83 | FW68A84 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0P | 08 | 45 | 6" | FW | 68A0P | UGB-1PE | N | 0 | FW68A69 | 45-HM-6808 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0Q | 08 | 45 | 6" | FW | 68A0Q | UGB-1PE | N | 0 | FW68A37 | FW68A38 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0S | 08 | 45 | 6" | FW | 68A0S | UGB-1PE | N | 0 | FW68A87 | 45-HY-6804 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
BDL60031 | 08 | 32 | 6" | BDL | 60031 | B32S1 | N | 0 | HEADER | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60036 | 08 | 32 | 2" | BDL | 60036 | B32S1 | N | 0 | HEADER | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60037 | 08 | 32 | 10" | BDL | 60037 | B32S1 | N | 0 | BDL43018 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60038 | 08 | 32 | 3" | BDL | 60038 | B32S1 | N | 0 | BDL65003 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60040 | 08 | 32 | 1" | BDL | 60040 | B32S1 | N | 0 | N67091 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60043 | 08 | 32 | 1" | BDL | 60043 | B32S1 | N | 0 | N67094 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60045 | 08 | 32 | 1" | BDL | 60045 | B32S1 | N | 0 | N67099 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60046 | 08 | 32 | 1" | BDL | 60046 | B32S1 | N | 0 | N67096 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60047 | 08 | 32 | 1" | BDL | 60047 | B32S1 | N | 0 | N67106 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FW68F03 | 08 | 32 | 1" | FW | 68F03 | B-13 | N | 0 | FW68R06 | FW68F02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
FW68F04 | 08 | 32 | 1-1/2" | FW | 68F04 | B-13 | N | 0 | FW68R04 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
FW68F16 | 08 | 32 | 3/4" | FW | 68F16 | B-13 | N | 0 | FW68F30 | ARV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F16 | 08 | 32 | 2" | FW | 68F16 | B-13 | N | 0 | FW68F30 | ARV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F17 | 08 | 32 | 2" | FW | 68F17 | B-13 | N | 0 | FW68F16 | FW68F16 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F18 | 08 | 32 | 2" | FW | 68F18 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F19 | 08 | 32 | 2" | FW | 68F19 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F20 | 08 | 32 | 3" | FW | 68F20 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F21 | 08 | 32 | 2" | FW | 68F21 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F22 | 08 | 32 | 3/4" | FW | 68F22 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F23 | 08 | 32 | 2" | FW | 68F23 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F24 | 08 | 32 | 2" | FW | 68F24 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F26 | 08 | 32 | 2" | FW | 68F26 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F27 | 08 | 32 | 2" | FW | 68F27 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F30 | 08 | 32 | 1" | FW | 68F30 | B-13 | N | 0 | FW68R08 | DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
BU01001 | 08 | 32 | 1" | BU | 01001 | B32S1 | N | 0 | BU01003 | 32-S-7302B | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.1 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-01 |  | F | N | 140 | N | 731 | 15
BU01001 | 08 | 32 | 2" | BU | 01001 | B32S1 | N | 0 | BU01003 | 32-S-7302B | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.1 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-01 |  | F | N | 140 | N | 731 | 15
BU01001 | 08 | 32 | 4" | BU | 01001 | B32S1 | N | 0 | BU01003 | 32-S-7302B | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.1 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-01 |  | F | N | 140 | N | 731 | 15
BU01002 | 08 | 32 | 1" | BU | 01002 | B32S1 | N | 0 | BU01001 | BDL01042 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-01 |  | F | N | 140 | N | 731 | 15
FW68N01 | 08 | 32 | 1-1/2" | FW | 68N01 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N04 | 08 | 32 | 1" | FW | 68N04 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N06 | 08 | 32 | 1-1/2" | FW | 68N06 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N09 | 08 | 32 | 4" | FW | 68N09 | B-13 | N | 0 | FW68K05 | FW68N10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N10 | 08 | 32 | 1-1/2" | FW | 68N10 | B-13 | N | 0 | FW68N09 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N21 | 08 | 32 | 1" | FW | 68N21 | B-13 | N | 0 | FW68K05 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N34 | 08 | 32 | 1" | FW | 68N34 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N34 | 08 | 32 | 3" | FW | 68N34 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N38 | 08 | 32 | 1-1/2" | FW | 68N38 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N41 | 08 | 32 | 2" | FW | 68N41 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N42 | 08 | 32 | 1" | FW | 68N42 | B-13 | N | 0 | FW68N46 | FW68N44 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N43 | 08 | 32 | 1" | FW | 68N43 | B-13 | N | 0 | SWIVEL JOINT | FW68N42 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N44 | 08 | 32 | 1" | FW | 68N44 | B-13 | N | 0 | FW68N42 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N46 | 08 | 32 | 4" | FW | 68N46 | B-13 | N | 0 | FW68N51 | FW68K05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N47 | 08 | 32 | 1-1/2" | FW | 68N47 | B-13 | N | 0 | SWIVEL JOINT | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N48 | 08 | 32 | 1-1/2" | FW | 68N48 | B-13 | N | 0 | FW68N47 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
ET71049 | 7A | 32 | 1/2" | ET | 71049 | C3S1 | HB | 50 | 32-T-7110B | BDL71025 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71049 | 7A | 32 | 1" | ET | 71049 | C3S1 | HB | 60 | 32-T-7110B | BDL71025 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71051 | 08 | 32 | 3/4" | ET | 71051 | C3S1 | N | 0 | 32-E-7102 | 32-S-7100A | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.48 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-02 |  | C | N | 041 | N | 323 | ,10
ET71058 | 08 | 32 | 1" | ET | 71058 | C3S1 | N | 0 | 32-S-7100A | BDL71035 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71064 | 08 | 32 | 1" | ET | 71064 | C3S1 | N | 0 | ET71037 | BDL71036 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71074 | 7A | 32 | 3/4" | ET | 71074 | C3S1 | HA | 60 | ET71042 | BDL71033 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71076 | 7A | 32 | 2" | ET | 71076 | C3S1 | HA | 70 | ET71042 | BDL71026 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71077 | 08 | 32 | 3/4" | ET | 71077 | C3S1 | N | 0 | ET71051 | BDL71027 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.48 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-006-02 |  | C | N | 041 | N | 323 | ,10
ET71078 | 08 | 32 | 3/4" | ET | 71078 | C3S1 | N | 0 | ET71079 | BDL71030 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | Art 4.3 | NA | N | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71079 | 7A | 32 | 1/2" | ET | 71079 | C3S1 | HB | 50 | 32-E-7101 | ET71042 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71079 | 7A | 32 | 4" | ET | 71079 | C3S1 | HB | 70 | 32-E-7101 | ET71042 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | Y | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
HCM31019 |  | 32 | 3/4" | HCM | 31019 | C42S1 | HB | 30 | 32-S-3101B | 32-E-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31019 |  | 32 | 6" | HCM | 31019 | C42S1 | HB | 30 | 32-S-3101B | 32-E-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31020 | 08 | 32 | 3/4" | HCM | 31020 | C42S1 | N | 0 | CD31005 | BDL31040 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31022 |  | 32 | 3/4" | HCM | 31022 | C42S1 | HB | 30 | 32-S-3101A | BDL31038 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM24099 |  | 32 | 4" | HCM | 24099 | D20S1 | ST | 30 | 32-T-2400 | BDL24098 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM31012 |  | 32 | 3/4" | HCM | 31012 | C42S1 | HB | 30 | 32-S-3100 | 32-S-3101A | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31012 |  | 32 | 4" | HCM | 31012 | C42S1 | HB | 30 | 32-S-3100 | 32-S-3101A | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31012 |  | 32 | 10" | HCM | 31012 | C42S1 | HB | 40 | 32-S-3100 | 32-S-3101A | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31013 |  | 32 | 3/4" | HCM | 31013 | C42S1 | ST | 30 | 32-S-3100 | 32-PDT-3102 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31014 |  | 32 | 3/4" | HCM | 31014 | C42S1 | ST | 30 | HN31001 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31014 |  | 32 | 1-1/2" | HCM | 31014 | C42S1 | ST | 30 | HN31001 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31015 |  | 32 | 3/4" | HCM | 31015 | C42S1 | ST | 30 | 32-D-3100 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31015 |  | 32 | 1-1/2" | HCM | 31015 | C42S1 | ST | 30 | 32-D-3100 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31015 |  | 32 | 4" | HCM | 31015 | C42S1 | ST | 40 | 32-D-3100 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31016 | 08 | 32 | 1" | HCM | 31016 | C42S1 | N | 0 | 32-D-3100 | BDL31030 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31017 |  | 32 | 3/4" | HCM | 31017 | C42S1 | ST | 30 | PR31022 | 32-D-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31017 |  | 32 | 1-1/2" | HCM | 31017 | C42S1 | ST | 30 | PR31022 | 32-D-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31018 |  | 32 | 3/4" | HCM | 31018 | C42S1 | HB | 30 | HCM31012 | 32-S-3101B | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
BDL31028 | 08 | 32 | 1" | BDL | 31028 | B32S1 | N | 0 | CO31001 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31029 | 08 | 32 | 3/4" | BDL | 31029 | B32S1 | N | 0 | PR31022 | BDL31022 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31030 | 08 | 32 | 2" | BDL | 31030 | B32S1 | N | 0 | HCM31016 | BDL34014 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31030 | 08 | 32 | 3" | BDL | 31030 | B32S1 | N | 0 | HCM31016 | BDL34014 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31031 | 08 | 32 | 4" | BDL | 31031 | B32S1 | N | 0 | BDL31025 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31032 |  | 32 | 10" | BDL | 31032 | B32S1 | SB | 100 | HCM31012 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31034 | 08 | 32 | 2" | BDL | 31034 | B32S1 | N | 0 | BDL31038 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31035 | 08 | 32 | 1" | BDL | 31035 | B32S1 | N | 0 | HCM31019 | BDL31034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31036 | 08 | 32 | 1" | BDL | 31036 | B32S1 | N | 0 | 32-S-3101A | BDL31034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31038 | 08 | 32 | 1" | BDL | 31038 | B32S1 | N | 0 | BDL31039 | BDL31034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31039 | 08 | 32 | 1" | BDL | 31039 | B32S1 | N | 0 | HCM31012 | BDL31038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31040 | 08 | 32 | 1/2" | BDL | 31040 | B32S1 | N | 0 | HCM31020 | BDL31034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31042 |  | 32 | 1" | BDL | 31042 | B32S1 | ST | 30 | HCM31014 | BDL31023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32016 | 08 | 32 | 4" | BDL | 32016 | B32S1 | N | 0 | HCM32034 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32017 | 08 | 32 | 1" | BDL | 32017 | B32S1 | N | 0 | HCM32025 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32018 | 08 | 32 | 1" | BDL | 32018 | B32S1 | N | 0 | HCM32024 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32019 | 08 | 32 | 1" | BDL | 32019 | B32S1 | N | 0 | HCM32019 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32020 | 08 | 32 | 1" | BDL | 32020 | B32S1 | N | 0 | HCM32023 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
PG61001 | 08 | 32 | 1" | PG | 61001 | 1CS2 | N | 0 | 32-P-6101 | 32-D-6100 | 10.0 | 60.0 | 5.0 | 20.0 |  | 15 | 28.5 | H | PROPYLENE GLYCOL | L | - | - | <1.5 | 20 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-023-01 |  | M | N | 010 | N | 80
PJW23004 |  | 32 | 3/4" | PJW | 23004 | B-1 | HB | 30 | 32-E-2300 | 32-P-2300 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.16 | 2 | III | MOD.G | Y | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PJW23004 |  | 32 | 6" | PJW | 23004 | B-1 | HB | 30 | 32-E-2300 | 32-P-2300 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.16 | 2 | III | MOD.G | Y | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PJW23005 |  | 32 | 6" | PJW | 23005 | B-1 | HB | 30 | 32-P-2300 | 32-E-2301 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | I | MOD.A | Y | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
PJW23006 |  | 32 | 6" | PJW | 23006 | B-1 | HB | 30 | 32-E-2301 | PJW23007 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | I | MOD.A | Y | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
PJW23008 |  | 32 | 2" | PJW | 23008 | B-1 | HB | 30 | PJW23006 | JWS32001 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
PJW23009 |  | 32 | 6" | PJW | 23009 | B-1 | HB | 30 | PJW23006 | JWS64025 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | I | MOD.A | Y | 20 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW32002 |  | 32 | 2" | PJW | 32002 | B-1 | HB | 30 | JWR32001 | PJW23004 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
PJW40001 |  | 32 | 6" | PJW | 40001 | B-1 | HB | 30 | JWR40003 | PJW23004 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.30 | 2 | I | MOD.A | Y | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
N6700Y | 08 | 32 | 1/2" | N | 6700Y | B-1 | N | 0 | N01001 | BDL60063 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67010 | 08 | 32 | 3/4" | N | 67010 | B-1 | N | 0 | N67028 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67011 | 08 | 32 | 3/4" | N | 67011 | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67015 | 08 | 32 | 3/4" | N | 67015 | B-1 | N | 0 | N67017 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67016 | 08 | 32 | 1/2" | N | 67016 | B-1 | N | 0 | N67041 | N61004 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67018 | 08 | 32 | 3/4" | N | 67018 | B-1 | N | 0 | N67028 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67020 | 08 | 32 | 2" | N | 67020 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67025 | 08 | 32 | 1/2" | N | 67025 | B-1 | N | 0 | N67017 | LS63046 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67027 | 08 | 32 | 3/4" | N | 67027 | B-1 | N | 0 | N67028 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67028 | 08 | 32 | 2" | N | 67028 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67029 | 08 | 32 | 3" | N | 67029 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67031 | 08 | 32 | 1/2" | N | 67031 | B-1 | N | 0 | N67005 | 32-D-1301 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67032 | 08 | 32 | 1/2" | N | 67032 | B-1 | N | 0 | N67005 | 32-D-1300 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67032 | 08 | 32 | 1" | N | 67032 | B-1 | N | 0 | N67005 | 32-D-1300 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67033 | 08 | 32 | 3/4" | N | 67033 | B-1 | N | 0 | N67039 | N14006 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N67034 | 08 | 32 | 1" | N | 67034 | B-1 | N | 0 | N67039 | N14021 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N67035 | 08 | 32 | 1/2" | N | 67035 | B-1 | N | 0 | N67055 | N15005 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04,32-P-024-01 |  | E | N | 000 | N | 140
N67036 | 08 | 32 | 1/2" | N | 67036 | B-1 | N | 0 | N67055 | N16001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67037 | 08 | 32 | 3/4" | N | 67037 | B-1 | N | 0 | N67017 | LS63047 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-052-01 |  | E | N | 000 | N | 140
N67037 | 08 | 32 | 1-1/2" | N | 67037 | B-1 | N | 0 | N67017 | LS63047 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-052-01 |  | E | N | 000 | N | 140
JWS64008 | 08 | 32 | 20" | JWS | 64008 | UGB-1PE | N | 0 | JWS64009 | JWS64054 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
JWS64008 | 08 | 32 | 32" | JWS | 64008 | UGB-1PE | N | 0 | JWS64009 | JWS64054 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
LPN01001 | 08 | 32 | 2" | LPN | 01001 | 1C13 | N | 0 | N01008 | SP-0105 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02001 | 08 | 32 | 3/4" | LPN | 02001 | 1C13 | N | 0 | LPN01001 | LPN10016 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02001 | 08 | 32 | 2" | LPN | 02001 | 1C13 | N | 0 | LPN01001 | LPN10016 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02002 | 08 | 32 | 1" | LPN | 02002 | 1C13 | N | 0 | LPN01001 | LPN11010 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02003 | 08 | 32 | 3/4" | LPN | 02003 | 1C13 | N | 0 | LPN01001 | VA11006 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02003 | 08 | 32 | 1" | LPN | 02003 | 1C13 | N | 0 | LPN01001 | VA11006 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02004 | 08 | 32 | 1" | LPN | 02004 | 1C13 | N | 0 | LPN01001 | LPN11011 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN10001 | 08 | 32 | 3/4" | LPN | 10001 | 1CS2 | N | 0 | LPN02001 | LPN10014 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN10003 | 08 | 32 | 1/2" | LPN | 10003 | 3DS3 | N | 0 | LPN10001 | LPN10006 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10005 | 08 | 32 | 1/2" | LPN | 10005 | 3DS3 | N | 0 | N10006 | PK-1001 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10006 | 08 | 32 | 1" | LPN | 10006 | 3DS3 | N | 0 | N10005 | LPN11004 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10007 | 08 | 32 | 1/2" | LPN | 10007 | 3DS3 | N | 0 | LPN10001 | 32--674 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10008 | 08 | 32 | 3/4" | LPN | 10008 | 1CS2 | N | 0 | LPN02005 | HOSE CONNECTION | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN10009 | 08 | 32 | 2" | LPN | 10009 | 3DS3 | N | 0 | PK-1001 | TEAL CYLINDER | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10014 | 08 | 32 | 3/4" | LPN | 10014 | 1CS2 | N | 0 | LPN10001 | LPN15A11 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN10014 | 08 | 32 | 1" | LPN | 10014 | 1CS2 | N | 0 | LPN10001 | LPN15A11 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN10015 | 08 | 32 | 1-1/2" | LPN | 10015 | 3DS3 | N | 0 | LPN10001 | 32-D-1001 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
PR61003 | 08 | 32 | 3" | PR | 61003 | C42S1 | N | 0 | TP-005 (32-D-6109) | TP-017 (32-PSV-6169) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42C | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61004 | 08 | 32 | 1-1/2" | PR | 61004 | C42S1 | N | 0 | TP-008 (32-E-6101) | TP-019 (32-PSV-6177) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61005 | 08 | 32 | 2" | PR | 61005 | C42S1 | N | 0 | TP-015 (32-D-6108) | TP-021 (32-PSV-6180) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61006 | 08 | 32 | 1" | PR | 61006 | C42S1 | CF | 40 | TP-012 (E-6102) | BDL61023 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 4.1 | -4.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | -4 | sh.42E | 1 | II | MOD.A2 | Y | 20 | N | 32-P-055-03 |  | F | N | 141 | N | 396 | 15
LS23021 |  | 32 | 1/2" | LS | 23021 | B-5 | HB | 60 | JLS23008 | LC23020 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23022 |  | 32 | 1" | LS | 23022 | B-5 | HB | 70 | JLS23010 | LC23021 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23023 |  | 32 | 1/2" | LS | 23023 | B-5 | HB | 60 | JLS23014 | LC23036 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23025 |  | 32 | 1/2" | LS | 23025 | B-5 | HB | 60 | JLS23011 | LC23044 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.15 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23026 |  | 32 | 1/2" | LS | 23026 | B-5 | HB | 60 | JLS23012 | LC23035 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23029 |  | 32 | 1/2" | LS | 23029 | B-5 | HB | 60 | JLS23018 | LC23039 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23032 |  | 32 | 1/2" | LS | 23032 | B-5 | HB | 60 | JLS23013 | LC23037 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23033 |  | 32 | 1/2" | LS | 23033 | B-5 | HB | 60 | JLS23021 | LC23047 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.15 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23037 |  | 32 | 3/4" | LS | 23037 | B-5 | HB | 60 | HCM23057 | LC23055 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23039 |  | 32 | 1" | LS | 23039 | B-5 | HB | 70 | LS63193 | JLS23010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23040 |  | 32 | 1" | LS | 23040 | B-5 | HB | 70 | JLS23010 | LC23059 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS24010 |  | 32 | 3/4" | LS | 24010 | B-5 | HB | 60 | JLS24001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS24011 |  | 32 | 3/4" | LS | 24011 | B-5 | HB | 60 | LS63073 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS24011 |  | 32 | 2" | LS | 24011 | B-5 | HB | 80 | LS63073 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS24011 |  | 32 | 4" | LS | 24011 | B-5 | HB | 90 | LS63073 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS24012 |  | 32 | 4" | LS | 24012 | D1S1 | HB | 70 | LS63073 | 32-E-2402 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | E | N | 041 | N | 1090
LS24013 |  | 32 | 1-1/2" | LS | 24013 | D1S1 | HB | 50 | 32-E-2402 | LS24014 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | E | N | 041 | N | 1090
FW68A0V | 08 | 45 | 6" | FW | 68A0V | UGB-1PE | N | 0 | FW68A15 | 45-HY-6807 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0X | 08 | 45 | 6" | FW | 68A0X | B-13 | N | 0 | FW68A0B | 45-EM-6801 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68A11 | 08 | 45 | 6" | FW | 68A11 | PEB-69 | N | 0 | FW68A03 | FW68A0T | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A13 | 08 | 45 | 6" | FW | 68A13 | PEB-69 | N | 0 | FW68A03 | FW68A0U | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
HN21003 | 08 | 32 | 1" | HN | 21003 | C6S1 | N | 0 | NITROGEN CONNECTION | PR21013 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.12 | 2 | I | MOD.A | Y | 1 | N | 32-P-042-01 |  | E | N | 000 | N | 170
HN21005 | 08 | 32 | 1" | HN | 21005 | C6S1 | N | 0 | NITROGEN CONNECTION | BDH21005 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.12 | 2 | I | MOD.A | Y | 1 | N | 32-U-031-02 |  | E | N | 000 | N | 170
HN21006 | 08 | 32 | 1" | HN | 21006 | C6S1 | N | 0 | NITROGEN CONNECTION | PR21012 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.12 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-02 |  | E | N | 000 | N | 170
HN22001 | 08 | 32 | 1" | HN | 22001 | C6S1 | N | 0 | HN | ET22010 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.13 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN22002 | 08 | 32 | 1" | HN | 22002 | C6S1 | N | 0 | HN | ET22008 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.13 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN23004 | 08 | 32 | 1" | HN | 23004 | C6S1 | N | 0 | NITROGEN CONNECTION | P23027 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.16 | 2 | I | MOD.A | Y | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 170
HN23007 | 08 | 32 | 1" | HN | 23007 | C6S1 | N | 0 | CD, N, HN | HCM23018 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.17 | 2 | I | MOD.A | Y | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 170
HN23009 | 08 | 32 | 1-1/2" | HN | 23009 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM23052 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.16 | 2 | I | MOD.A | Y | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 170
HN24002 | 08 | 32 | 1" | HN | 24002 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24063 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.19 | 2 | I | MOD.A | Y | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 170
HN24003 | 08 | 32 | 1-1/2" | HN | 24003 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24092 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.19 | 2 | I | MOD.A | Y | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 170
HN24005 | 08 | 32 | 1" | HN | 24005 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24073 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.20 | 2 | I | MOD.A | Y | 1 | N | 32-P-046-01 |  | E | N | 000 | N | 170
CWS60413 | 08 | 32 | 3" | CWS | 60413 | B-1 | N | 0 | CWS64006 | 32-E-9004 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS60413 | 08 | 32 | 4" | CWS | 60413 | B-1 | N | 0 | CWS64006 | 32-E-9004 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64001 | 08 | 32 | 14" | CWS | 64001 | B-1 | N | 0 | CWS01010 | 32-E-6400A | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64002 | 08 | 32 | 1-1/2" | CWS | 64002 | B-1 | N | 0 | CWS01010 | 32-E-6400B | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64002 | 08 | 32 | 20" | CWS | 64002 | B-1 | N | 0 | CWS01010 | 32-E-6400B | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64003 | 08 | 32 | 14" | CWS | 64003 | B-1 | N | 0 | CWS01010 | 32-E-6400C | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64005 | 08 | 32 | 3/4" | CWS | 64005 | B-1 | N | 0 | CWS64004 | 32-E-8000 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64005 | 08 | 32 | 4" | CWS | 64005 | B-1 | N | 0 | CWS64004 | 32-E-8000 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
FW68N49 | 08 | 32 | 1-1/2" | FW | 68N49 | B-13 | N | 0 | FW68N52 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N51 | 08 | 32 | 1-1/2" | FW | 68N51 | B-13 | N | 0 | FW68N52 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N52 | 08 | 32 | 1-1/2" | FW | 68N52 | B-13 | N | 0 | FW68N47 | FW68N51 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N57 | 08 | 32 | 1-1/2" | FW | 68N57 | B-13 | N | 0 | FW68N34 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N58 | 08 | 32 | 1-1/2" | FW | 68N58 | B-13 | N | 0 | FW68N34 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N59 | 08 | 32 | 1-1/2" | FW | 68N59 | B-13 | N | 0 | FW68N34 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N60 | 08 | 32 | 1" | FW | 68N60 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N61 | 08 | 32 | 1-1/2" | FW | 68N61 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N70 | 08 | 32 | 1/2" | FW | 68N70 | B-13 | N | 0 | FW68N51 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N70 | 08 | 32 | 1-1/2" | FW | 68N70 | B-13 | N | 0 | FW68N51 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68O01 | 08 | 32 | 1-1/2" | FW | 68O01 | B-13 | N | 0 | FW68O04 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O08 | 08 | 32 | 1" | FW | 68O08 | B-13 | N | 0 | FW68O06 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O13 | 08 | 32 | 3" | FW | 68O13 | B-13 | N | 0 | FW68O14 | FW68O15 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O15 | 08 | 32 | 2" | FW | 68O15 | B-13 | N | 0 | FW68O13 | FW68O17 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O17 | 08 | 32 | 1-1/2" | FW | 68O17 | B-13 | N | 0 | FW68O15 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O19 | 08 | 32 | 1" | FW | 68O19 | B-13 | N | 0 | FW68O16 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O22 | 08 | 32 | 1" | FW | 68O22 | B-13 | N | 0 | FW68O12 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68P01 | 08 | 32 | 1/2" | FW | 68P01 | B-13 | N | 0 | FW68P18 | FW68P18 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P02 | 08 | 32 | 1/2" | FW | 68P02 | B-13 | N | 0 | FW68P01 | FW68P01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
CHWR61002 |  | 32 | 3" | CHWR | 61002 | B-1 | CF | 25 | CHWR43011 | CHWR61014 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CO42003 | 08 | 32 | 1/2" | CO | 42003 | 1IS5 | N | 0 | CO42017 | 32-R-4001 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42003 | 08 | 32 | 1" | CO | 42003 | 1IS5 | N | 0 | CO42017 | 32-R-4001 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42016 | 08 | 32 | 1/2" | CO | 42016 | 1IS5 | N | 0 | CO42003 | 32-R-4001 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42017 | 08 | 32 | 1/2" | CO | 42017 | 1IS5 | N | 0 | CO42018 | CO42003 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42019 | 08 | 32 | 1/2" | CO | 42019 | 1IS5 | N | 0 | REACTOR EMERGENCY KILLER | CO42018 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
HCM31023 | 08 | 32 | 1/2" | HCM | 31023 | C42S1 | N | 0 | CD31006 | BDL31037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31023 | 08 | 32 | 1" | HCM | 31023 | C42S1 | N | 0 | CD31006 | BDL31037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32017 |  | 32 | 1" | HCM | 32017 | C42S1 | HB | 30 | VZ32002 | FO35015 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32018 |  | 32 | 4" | HCM | 32018 | C42S1 | HB | 40 | HCM32019 | HCM32033 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 351 | 10
HCM32019 | 08 | 32 | 3/4" | HCM | 32019 | C42S1 | HB | 30 | TP-06A (32-D-3202A) | HCM23046 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-04 |  | G | Y | 141 | N | 351 | 10
HCM32019 | 08 | 32 | 3" | HCM | 32019 | C42S1 | HB | 40 | TP-06A (32-D-3202A) | HCM23046 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-04 |  | G | Y | 141 | N | 351 | 10
HCM32019 | 08 | 32 | 4" | HCM | 32019 | C42S1 | HB | 40 | TP-06A (32-D-3202A) | HCM23046 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-04 |  | G | Y | 141 | N | 351 | 10
HCM32021 |  | 32 | 1" | HCM | 32021 | C42S1 | HB | 30 | HCM32019 | HCM32023 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM32023 |  | 32 | 3/4" | HCM | 32023 | C42S1 | P | 50 | HCM32021 | BDL32020 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM32024 |  | 32 | 1" | HCM | 32024 | C42S1 | HB | 30 | 32-D-3200 | TP-01A (32-D-3201A) | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32024 |  | 32 | 6" | HCM | 32024 | C42S1 | HB | 30 | 32-D-3200 | TP-01A (32-D-3201A) | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32026 |  | 32 | 1" | HCM | 32026 | C42S1 | HB | 30 | 32-E-3200 | 32-D-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32026 |  | 32 | 4" | HCM | 32026 | C42S1 | HB | 30 | 32-E-3200 | 32-D-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32026 |  | 32 | 8" | HCM | 32026 | C42S1 | HB | 40 | 32-E-3200 | 32-D-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32027 |  | 32 | 1/2" | HCM | 32027 | C42S1 | HB | 30 | 32-E-3200 | HCM32029 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32027 |  | 32 | 1" | HCM | 32027 | C42S1 | HB | 30 | 32-E-3200 | HCM32029 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32027 |  | 32 | 2" | HCM | 32027 | C42S1 | HB | 30 | 32-E-3200 | HCM32029 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32028 | 08 | 32 | 1" | HCM | 32028 | QXC25S1 | N | 0 | JLS32002 | HCM31019 | 25.0/25.0 | -40.0/200.0 | 18.0 | 85.0 |  | 40.08 | 74.4 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-047-01 |  | A | N | 141 | N | 343 | 10
BDL32021 | 08 | 32 | 3/4" | BDL | 32021 | B32S1 | N | 0 | HCM32023 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32021 | 08 | 32 | 1" | BDL | 32021 | B32S1 | N | 0 | HCM32023 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32022 | 08 | 32 | 3/4" | BDL | 32022 | B32S1 | N | 0 | HCM32030 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32022 | 08 | 32 | 1" | BDL | 32022 | B32S1 | N | 0 | HCM32030 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32023 | 08 | 32 | 3/4" | BDL | 32023 | B32S1 | N | 0 | HCM32027 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32024 | 08 | 32 | 1/2" | BDL | 32024 | B32S1 | N | 0 | HCM32027 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32025 | 08 | 32 | 1/2" | BDL | 32025 | B32S1 | N | 0 | VZ32002 | BDL32018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32026 | 08 | 32 | 1" | BDL | 32026 | B32S1 | N | 0 | HCM32019 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
JWR24001 |  | 32 | 6" | JWR | 24001 | B-1 | HB | 30 | JWR24003 | JWR64003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.19 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR24002 | 08 | 32 | 1" | JWR | 24002 | B-1 | N | 0 | TP-13 (JWR240115) | JWR64047 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR24003 | 08 | 32 | 1-1/2" | JWR | 24003 | B-1 | N | 0 | 32-E-2401 | JWR24001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.19 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR24003 | 08 | 32 | 12" | JWR | 24003 | B-1 | N | 0 | 32-E-2401 | JWR24001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.19 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR24005 | 08 | 32 | 6" | JWR | 24005 | B-1 | N | 0 | JWR24008 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR24006 | 08 | 32 | 1" | JWR | 24006 | D20S1 | N | 0 | 32-E-2400 | JWR24005 | 49.0/49.0 | -45.0/150.0 | 5.0 | 40.0 |  | 73.51 | 128.56 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 000 | N | 1021
JWR24007 | 08 | 32 | 1" | JWR | 24007 | D20S1 | N | 0 | 32-E-2403 | JWR24008 | 49.0/49.0 | -45.0/150.0 | 5.0 | 40.0 |  | 73.51 | 128.56 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 000 | N | 1021
JWR24008 | 08 | 32 | 6" | JWR | 24008 | B-1 | N | 0 | JWR24007 | JWR24005 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.20 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR32001 | 08 | 32 | 3/4" | JWR | 32001 | C3S1 | N | 0 | 32-E-3200 | JWR32002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR32001 | 08 | 32 | 4" | JWR | 32001 | C3S1 | N | 0 | 32-E-3200 | JWR32002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR32002 | 08 | 32 | 4" | JWR | 32002 | B-1 | N | 0 | JWR32001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.24 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR32003 | 08 | 32 | 2" | JWR | 32003 | B-1 | N | 0 | TP-24B, JWR320124, JWR320324 | JWR64047 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR32004 | 08 | 32 | 2" | JWR | 32004 | B-1 | N | 0 | TP-24A, JWR320124, JWR320324 | JWR64047 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PR01001 | 08 | 32 | 8" | PR | 01001 | C42S1 | N | 0 | PR01002 | 32-D-7200 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
PR01002 | 08 | 32 | 1" | PR | 01002 | C42S1 | N | 0 | PR80001 | PR01001 | 43.7/43.7 | 80.0/-46.0 | 31.1/31.1 | 42.0/0.0 |  | 65.55 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-01 |  | F | N | 141 | N | 360 | ,15
PR01004 | 08 | 32 | 4" | PR | 01004 | C42S1 | N | 0 | PR24007 | PR01001 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
PR21009 |  | 32 | 1/2" | PR | 21009 | 1FS4 | CF | 25 | PR21010 | 32-AE-2101 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | II | MOD.A2 | Y | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21009 |  | 32 | 1" | PR | 21009 | 1FS4 | CF | 25 | PR21010 | 32-AE-2101 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | II | MOD.A2 | Y | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21009 |  | 32 | 2" | PR | 21009 | 1FS4 | CF | 25 | PR21010 | 32-AE-2101 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21010 |  | 32 | 3/4" | PR | 21010 | D20S1 | HB | 30 | 32-E-2100 | PR21011 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR21010 |  | 32 | 2" | PR | 21010 | D20S1 | HB | 30 | 32-E-2100 | PR21011 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR21010 |  | 32 | 4" | PR | 21010 | D20S1 | HB | 30 | 32-E-2100 | PR21011 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR21011 | 7A | 32 | 3" | PR | 21011 | 1FS4 | HB | 30 | PR21010 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.12 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-045-01 |  | G | N | 141 | N | 337 | 10
PR21012 |  | 32 | 1" | PR | 21012 | 1FS4 | CF | 25 | HN21006 | PR21014 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | Art 4.3 | NA | N | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21013 | 08 | 32 | 1" | PR | 21013 | D20S1 | N | 0 | HN21003 | 32-R-2100 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-042-01 |  | F | N | 141 | N | 330 | 15
PR21015 |  | 32 | 1/2" | PR | 21015 | 1FS4 | CF | 25 | PR21009 | BDL21011 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | Art 4.3 | NA | N | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR22011 | 08 | 32 | 2" | PR | 22011 | D20S1 | N | 0 | PR33019 | PR31015 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22012 | 08 | 32 | 1" | PR | 22012 | D20S1 | N | 0 | PR33019 | 32-E-2100 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22013 | 08 | 32 | 1" | PR | 22013 | D20S1 | N | 0 | PR22012 | SL21001 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR22014 | 08 | 32 | 2" | PR | 22014 | D20S1 | N | 0 | PR22016 | HCM24006 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22015 | 08 | 32 | 1/2" | PR | 22015 | D20S1 | N | 0 | PR22016 | PR23012 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22015 | 08 | 32 | 3" | PR | 22015 | D20S1 | N | 0 | PR22016 | PR23012 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
LPN11002 | 08 | 32 | 1/2" | LPN | 11002 | 3DS3 | N | 0 | LPN11010 | 32-D-1100 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN11003 | 08 | 32 | 2" | LPN | 11003 | 3DS3 | N | 0 | LPN11010 | 32-D-1100 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN11004 | 08 | 32 | 1/2" | LPN | 11004 | 3DS3 | N | 0 | LPN11003 | 32-Z-1100 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN11010 | 08 | 32 | 1" | LPN | 11010 | 1CS2 | N | 0 | LPN02002 | LPN11003 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN11011 | 08 | 32 | 1" | LPN | 11011 | 1CS2 | N | 0 | LPN02004 | FO11003 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN11012 | 08 | 32 | 1" | LPN | 11012 | 3DS3 | N | 0 | 32-Z-1100 | 32-D-1102 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN11023 | 08 | 32 | 2" | LPN | 11023 | 3DS3 | N | 0 | 32-Z-1100 | 32-D-1102 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
JWS64063 | 08 | 32 | 1-1/2" | JWS | 64063 | B-1 | N | 0 | JWS64062 | 32-Z-2400B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64064 | 08 | 32 | 3/4" | JWS | 64064 | B-1 | N | 0 | JWS64065 | 32-Z-3300A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64065 | 08 | 32 | 1-1/2" | JWS | 64065 | B-1 | N | 0 | JWS64056 | 32-Z-3300B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64067 | 08 | 32 | 3/4" | JWS | 64067 | B-1 | N | 0 | JWS64026 | 32-Z-4300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64067 | 08 | 32 | 1-1/2" | JWS | 64067 | B-1 | N | 0 | JWS64026 | 32-Z-4300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64069 | 08 | 32 | 1-1/2" | JWS | 64069 | B-1 | N | 0 | JWS64056 | 32-Z-7300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64072 | 08 | 32 | 4" | JWS | 64072 | B-1 | N | 0 | JWS64054 | JWS64048 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64073 | 08 | 32 | 20" | JWS | 64073 | B-1 | N | 0 | JWS64004 | 32-P-6400A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.9 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64074 | 08 | 32 | 20" | JWS | 64074 | B-1 | N | 0 | JWS64004 | 32-P-6400C | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64075 | 08 | 32 | 3/4" | JWS | 64075 | B-1 | N | 0 | JWS64054 | 32-E-1451 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-01 |  | E | N | 000 | N | 10
JWS64075 | 08 | 32 | 1" | JWS | 64075 | B-1 | N | 0 | JWS64054 | 32-E-1451 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-01 |  | E | N | 000 | N | 10
JWS64076 | 08 | 32 | 1" | JWS | 64076 | B-1 | N | 0 | JWS64054 | 32-E-1450A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-01 |  | E | N | 000 | N | 10
JWS64077 | 08 | 32 | 1" | JWS | 64077 | B-1 | N | 0 | JWS64054 | 32-E-1450B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-01 |  | E | N | 000 | N | 10
JWS64078 | 08 | 32 | 2" | JWS | 64078 | B-1 | N | 0 | JWS64023 | TP-147 (JWS360137) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64079 | 08 | 32 | 2" | JWS | 64079 | B-1 | N | 0 | JWS64023 | TP-145 (JWS360129) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64084 | 08 | 32 | 1" | JWS | 64084 | B-1 | N | 0 | JWS64020 | TP 21B, (JWS320116) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS71001 | 08 | 32 | 3/4" | JWS | 71001 | C3S1 | N | 0 | JWS64033 | 32-E-7102 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
LS24014 |  | 32 | 3/4" | LS | 24014 | B-5 | HB | 60 | LS24013 | LC24011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS24014 |  | 32 | 1-1/2" | LS | 24014 | B-5 | HB | 70 | LS24013 | LC24011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS24016 |  | 32 | 1" | LS | 24016 | B-5 | HB | 70 | PR24032 | LC24013 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31006 |  | 32 | 1" | LS | 31006 | B-5 | HB | 70 | LS63199 | PR31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31017 | 08 | 32 | 3/4" | LS | 31017 | B-5 | HB | 60 | PR31015 | LC31010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.68N | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31018 | 08 | 32 | 3/4" | LS | 31018 | B-5 | HB | 60 | JLS31006 | LC31011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31020 |  | 32 | 1" | LS | 31020 | B-5 | HB | 70 | LS63039 | JLS31007 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31021 | 08 | 32 | 3/4" | LS | 31021 | B-5 | HB | 60 | PR31015 | LC31016 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31022 |  | 32 | 3/4" | LS | 31022 | B-5 | HB | 60 | JLS31009 | LC31017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31023 | 08 | 32 | 3/4" | LS | 31023 | B-5 | HB | 60 | PR31015 | LC31018 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31024 |  | 32 | 1" | LS | 31024 | B-5 | HB | 70 | JLS31007 | LC31019 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31025 |  | 32 | 3/4" | LS | 31025 | B-5 | HB | 60 | 32-S-3100 | LC31013 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31026 |  | 32 | 1/2" | LS | 31026 | B-5 | HB | 60 | 32-D-3100 | LC31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31026 |  | 32 | 1" | LS | 31026 | B-5 | HB | 70 | 32-D-3100 | LC31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31027 |  | 32 | 1" | LS | 31027 | B-5 | HB | 70 | LS63041 | JLS31012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31028 |  | 32 | 3/4" | LS | 31028 | B-5 | HB | 60 | JLS31012 | LC31021 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31030 |  | 32 | 3/4" | LS | 31030 | B-5 | HB | 60 | PR31016 | LC31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
HN31001 |  | 32 | 1" | HN | 31001 | C6S1 | ST | 30 | NITROGEN CONNECTION | HCM31014 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.23 | 2 | I | MOD.A | Y | 20 | N | 32-P-047-01 |  | E | N | 000 | N | 170
HN33001 | 08 | 32 | 1" | HN | 33001 | C6S1 | N | 0 | VZ33002 | SP-04-13300-03 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN40002 |  | 32 | 1" | HN | 40002 | C6S1 | ST | 30 | NITROGEN CONNECTION | PR40035 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.30 | 2 | I | MOD.A | Y | 20 | N | 32-P-047-03 |  | E | N | 000 | N | 170
HN62017 | 08 | 32 | 1" | HN | 62017 | C6S1 | N | 0 | HN | PR33019 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.13 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN67001 | 08 | 32 | 1-1/2" | HN | 67001 | C6S1 | N | 0 | HN67011 | HEADER | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67002 | 08 | 32 | 3/4" | HN | 67002 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67003 | 08 | 32 | 1-1/2" | HN | 67003 | C6S1 | N | 0 | HN67011 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67004 | 08 | 32 | 1-1/2" | HN | 67004 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67005 | 08 | 32 | 1-1/2" | HN | 67005 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67008 | 08 | 32 | 1-1/2" | HN | 67008 | C6S1 | N | 0 | HN67007 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67009 | 08 | 32 | 1-1/2" | HN | 67009 | C6S1 | N | 0 | HN67007 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67011 | 08 | 32 | 3" | HN | 67011 | C6S1 | N | 0 | D-6701C (PK6701) | HEADER | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.103 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67012 | 08 | 32 | 1-1/2" | HN | 67012 | C6S1 | N | 0 | HEADER | HN67011 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67014 | 08 | 32 | 1-1/2" | HN | 67014 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67015 | 08 | 32 | 1-1/2" | HN | 67015 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67016 | 08 | 32 | 1-1/2" | HN | 67016 | C6S1 | N | 0 | HN67002 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67017 | 08 | 32 | 1-1/2" | HN | 67017 | C6S1 | N | 0 | HN67002 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67019 | 08 | 32 | 1-1/2" | HN | 67019 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67021 | 08 | 32 | 3/4" | HN | 67021 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
CWS64007 | 08 | 32 | 3" | CWS | 64007 | B-1 | N | 0 | CWS64006 | 32-E-9001A | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64008 | 08 | 32 | 3/4" | CWS | 64008 | B-1 | N | 0 | CWS64006 | 32-E-9001B | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64008 | 08 | 32 | 3" | CWS | 64008 | B-1 | N | 0 | CWS64006 | 32-E-9001B | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64009 | 08 | 32 | 2" | CWS | 64009 | B-1 | N | 0 | CWS64006 | 32-E-8005 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64009 | 08 | 32 | 3" | CWS | 64009 | B-1 | N | 0 | CWS64006 | 32-E-8005 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64010 | 08 | 32 | 20" | CWS | 64010 | B-1 | N | 0 | CWS64006 | CWS89041 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64012 | 08 | 32 | 2" | CWS | 64012 | B-1 | N | 0 | CWS64006 | 32-E-9002 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64012 | 08 | 32 | 3" | CWS | 64012 | B-1 | N | 0 | CWS64006 | 32-E-9002 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86015 | 08 | 32 | 1/2" | CWS | 86015 | B-1 | N | 0 | CWS89042 | JCW86022 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86016 | 08 | 32 | 1" | CWS | 86016 | B-1 | N | 0 | CWS89042 | 32-D-8600 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86017 | 08 | 32 | 1/2" | CWS | 86017 | B-1 | N | 0 | CWS89042 | CWS86019 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86017 | 08 | 32 | 1" | CWS | 86017 | B-1 | N | 0 | CWS89042 | CWS86019 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86019 | 08 | 32 | 1/2" | CWS | 86019 | B-1 | N | 0 | CWS86017 | CWS86018 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
FW68B0U | 08 | 45 | 12" | FW | 68B0U | UGB-1PE | N | 0 | FW68B63 | FW68B64 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0V | 08 | 45 | 12" | FW | 68B0V | UGB-1PE | N | 0 | FW68B61 | FW68B62 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | 3LPE | N | TP-FW-02 |  | E | N | 000 | N | 76
FW68B0X | 08 | 45 | 6" | FW | 68B0X | UGB-1PE | N | 0 | FW68B67 | 45-HY-6819 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
HTF89006 | 08 | 32 | 1" | HTF | 89006 | C-2 | N | 0 | - | TP-N60221 (32-P-8918) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | DIATHERMIC OIL/HOT THERMAL FLUID | L | - | - | <1.5 | 280 | sh.68R | 2 | Art 4.3 | NA | N | 7 | N | 32-P-070-05 |  | E | N | 110 | N | 207
HTF89009 | 08 | 32 | 1" | HTF | 89009 | C-2 | HA | 80 | HOR89003 | COLLECTION DRUM | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | DIATHERMIC OIL/HOT THERMAL FLUID | L | - | - | <1.5 | 280 | sh.68R | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 207
BDL72028 | 08 | 32 | 1/2" | BDL | 72028 | B32S1 | N | 0 | PR72009 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72029 | 08 | 32 | 1-1/2" | BDL | 72029 | B32S1 | N | 0 | BDL72026 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72030 | 08 | 32 | 1" | BDL | 72030 | B32S1 | N | 0 | PR72027 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
DMW01001 | 08 | 32 | 3/4" | DMW | 01001 | SXB-48 | N | 0 | DMW220003 OSBL LINE | DMW64001 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.2 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DMW50001 | 08 | 32 | 1/2" | DMW | 50001 | SXB-48 | N | 0 | DMW63005 | DMW50002 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.34 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-050-01 |  | M | N | 000 | N | 26
DMW50001 | 08 | 32 | 1" | DMW | 50001 | SXB-48 | N | 0 | DMW63005 | DMW50002 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.34 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-050-01 |  | M | N | 000 | N | 26
DMW50003 | 08 | 32 | 1/2" | DMW | 50003 | SXB-48 | N | 0 | DMW50001 | LS50001 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.34 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-050-01 |  | M | N | 000 | N | 26
FW68P06 | 08 | 32 | 1-1/2" | FW | 68P06 | B-13 | N | 0 | FW68P08 | FW68P08 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P08 | 08 | 32 | 1" | FW | 68P08 | B-13 | N | 0 | FW68P06 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P10 | 08 | 32 | 1/2" | FW | 68P10 | B-13 | N | 0 | FW68P09 | FW68P11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P11 | 08 | 32 | 1-1/2" | FW | 68P11 | B-13 | N | 0 | FW68P10 | FW68P10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P12 | 08 | 32 | 1-1/2" | FW | 68P12 | B-13 | N | 0 | FW68P10 | FW68P10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P13 | 08 | 32 | 1/2" | FW | 68P13 | B-13 | N | 0 | FW68P10 | FW68P10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P14 | 08 | 32 | 1/2" | FW | 68P14 | B-13 | N | 0 | FW68P17 | FW68P17 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P15 | 08 | 32 | 1/2" | FW | 68P15 | B-13 | N | 0 | FW68P14 | FW68P14 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P17 | 08 | 32 | 3" | FW | 68P17 | B-13 | N | 0 | FW68P14 | FW68P14 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68Q01 | 08 | 32 | 3" | FW | 68Q01 | B-13 | N | 0 | FW68C09 | FW68Q10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q02 | 08 | 32 | 1" | FW | 68Q02 | B-13 | N | 0 | FW68C09 | FW68Q05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q03 | 08 | 32 | 1" | FW | 68Q03 | B-13 | N | 0 | FW68Q06 | FW68Q06 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q04 | 08 | 32 | 1" | FW | 68Q04 | B-13 | N | 0 | FW68Q06 | FW68Q02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q05 | 08 | 32 | 1" | FW | 68Q05 | B-13 | N | 0 | FW68Q02 | FW68Q02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q05 | 08 | 32 | 2" | FW | 68Q05 | B-13 | N | 0 | FW68Q02 | FW68Q02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q06 | 08 | 32 | 1" | FW | 68Q06 | B-13 | N | 0 | FW68Q02 | FW68C09 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
CHWR61005 | 08 | 32 | 10" | CHWR | 61005 | B-5 | N | 0 | CHWS61015 | CHWR61012 | 9.0 | 280.0 | 6.0/6.0 | 10.0/170.0 |  | 14.51 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 10 | sh.42 | 2 | I | MOD.A | Y | 6 | N | 32-U-023-02 |  | A | N | 010 | N | 54
CHWR61007 | 08 | 32 | 6" | CHWR | 61007 | B-1 | N | 0 | VENT | WW61001 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
CHWR61009 | 08 | 32 | 1/2" | CHWR | 61009 | B-1 | N | 0 | N67016 | 32-D-6101 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
CHWR61009 | 08 | 32 | 1" | CHWR | 61009 | B-1 | N | 0 | N67016 | 32-D-6101 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
CHWR61012 |  | 32 | 8" | CHWR | 61012 | B-1 | CF | 40 | CHWR61013 | TP-030 (CHWR61017) | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61013 |  | 32 | 1-1/2" | CHWR | 61013 | B-1 | CF | 25 | CHWR61002 | CHWR61012 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61014 |  | 32 | 6" | CHWR | 61014 | B-1 | CF | 40 | CHWR61002 | 32-D-6101 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61015 |  | 32 | 3" | CHWR | 61015 | B-1 | CF | 25 | CHWR51005 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61017 | 08 | 32 | 8" | CHWR | 61017 | C42S1 | CF | 40 | TP-031 (CHWR61012) | TP-009, E-6102 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 6.0 | 6.0 |  | 28.05 | 76.65 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 6 | sh.42E | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-02 |  | M | N | 010 | N | 1058
CHWR65003 |  | 32 | 3/4" | CHWR | 65003 | B-1 | CF | 25 | CHWR65001 | VA65001 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CT14001 |  | 32 | 2" | CT | 14001 | QXC25S1 | CF | 25 | 32-D-1400A | 32-S-1400A | 20.0 | 190.0 | 10.0/0.03 | 6.0/70.0 |  | 31.64 | 74.4 | H | DRY CATALYST | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-03 |  | M | N | 231 | N | 284
CT14002 |  | 32 | 1" | CT | 14002 | 3FS3 | JP | 0 | CT14010 | CT15003 | 20.0 | 190.0 | 10.0 | 6.0 |  | 31.64 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | A | N | 232 | N | 285 | 23,25
HCM32029 |  | 32 | 1" | HCM | 32029 | C42S1 | HB | 30 | HCM32027 | JLS32002 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32032 | 08 | 32 | 1" | HCM | 32032 | C42S1 | HB | 30 | HCM32043 | HCM32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24G | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32033 |  | 32 | 4" | HCM | 32033 | C42S1 | HB | 40 | HCM32018 | HCM31019 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G | Y | 141 | N | 351 | 10
HCM32034 |  | 32 | 1" | HCM | 32034 | C42S1 | HB | 30 | HCM32026 | BDL32016 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32034 |  | 32 | 4" | HCM | 32034 | C42S1 | HB | 30 | HCM32026 | BDL32016 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
BDL23068 | 08 | 32 | 3/4" | BDL | 23068 | B32S1 | N | 0 | P23030 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23069 | 08 | 32 | 3/4" | BDL | 23069 | B32S1 | N | 0 | P23032 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23070 | 08 | 32 | 3/4" | BDL | 23070 | B32S1 | N | 0 | P23026 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23071 | 08 | 32 | 3/4" | BDL | 23071 | B32S1 | N | 0 | P23029 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23075 | 08 | 32 | 1/2" | BDL | 23075 | B32S1 | N | 0 | BDL23078 | BDL60061 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL23075 | 08 | 32 | 1" | BDL | 23075 | B32S1 | N | 0 | BDL23078 | BDL60061 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL23078 | 08 | 32 | 3/4" | BDL | 23078 | B32S1 | N | 0 | HCM23065 | BDL23075 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
BDL24001 | 08 | 32 | 1" | BDL | 24001 | B32S1 | N | 0 | VZ24005 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 19-U-001-01 |  | G | N | 141 | N | 460 | 10
BDL24050 | 08 | 32 | 3/4" | BDL | 24050 | B32S1 | N | 0 | 32-P-2400A | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24057 | 08 | 32 | 2" | BDL | 24057 | B32S1 | N | 0 | TP-3 (FL240157) | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24058 | 08 | 32 | 3/4" | BDL | 24058 | B32S1 | N | 0 | HCM24058 | BDL31031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24058 | 08 | 32 | 1" | BDL | 24058 | B32S1 | N | 0 | HCM24058 | BDL31031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24059 | 08 | 32 | 3" | BDL | 24059 | B32S1 | N | 0 | HCM24063 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
JWR32005 | 08 | 32 | 1" | JWR | 32005 | C3S1 | N | 0 | JWR32001 | VA32002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR32006 | 08 | 32 | 1" | JWR | 32006 | B-1 | N | 0 | TP-22A, JWR320121, JWR320321 | JWR32004 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR32007 | 08 | 32 | 1" | JWR | 32007 | B-1 | N | 0 | TP 22B (JWR320121) | JWR32003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR33001 | 08 | 32 | 1-1/2" | JWR | 33001 | C3S1 | N | 0 | 32-E-3300 | JWR33002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR35001 | 08 | 32 | 3/4" | JWR | 35001 | B-1 | N | 0 | 32-E-3500 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.27 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR35001 | 08 | 32 | 3" | JWR | 35001 | B-1 | N | 0 | 32-E-3500 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.27 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37001 | 08 | 32 | 3/4" | JWR | 37001 | B-1 | N | 0 | 32-Z-2400A | JWR64045 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37001 | 08 | 32 | 1-1/2" | JWR | 37001 | B-1 | N | 0 | 32-Z-2400A | JWR64045 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37002 | 08 | 32 | 1-1/2" | JWR | 37002 | B-1 | N | 0 | 32-Z-2400B | JWR37001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37003 | 08 | 32 | 3/4" | JWR | 37003 | B-1 | N | 0 | 32-Z-3300A | JWR37004 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37003 | 08 | 32 | 1-1/2" | JWR | 37003 | B-1 | N | 0 | 32-Z-3300A | JWR37004 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PR22016 | 08 | 32 | 3" | PR | 22016 | D20S1 | N | 0 | PR33019 | PR22014 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR23005 |  | 32 | 3/4" | PR | 23005 | D20S1 | ST | 30 | 32-D-2300 | 32-S-2300 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23005 |  | 32 | 2" | PR | 23005 | D20S1 | ST | 40 | 32-D-2300 | 32-S-2300 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23008 | 7A | 32 | 4" | PR | 23008 | 1FS4 | HB | 30 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.14 | 1 | III | MOD.G | Y | NR | Y | 32-P-044-01 |  | G | N | 141 | N | 337 | 10
PR23012 |  | 32 | 1" | PR | 23012 | D20S1 | HB | 30 | PR22015 | HCM24089 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.14 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR23013 | 7A | 32 | 4" | PR | 23013 | 1FS4 | HB | 30 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.14 | 1 | III | MOD.G | Y | NR | Y | 32-P-044-01 |  | G | N | 141 | N | 337 | 10
N67104 | 08 | 32 | 1" | N | 67104 | B-1 | N | 0 | N67029 | N67091 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67105 | 08 | 32 | 3/4" | N | 67105 | B-1 | N | 0 | N67029 | BDL60048 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67106 | 08 | 32 | 3/4" | N | 67106 | B-1 | N | 0 | N67029 | BDL60047 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67108 | 08 | 32 | 1/2" | N | 67108 | B-1 | N | 0 | N67017 | FL60001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67110 | 08 | 32 | 3/4" | N | 67110 | B-1 | N | 0 | N67046 | BDL60055 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
JWS72003 | 08 | 32 | 4" | JWS | 72003 | D20S1 | N | 0 | JWS64018 | 32-E-7203 | 33.7/33.7 | 245.0/-45.0 | 5.0 | 30.0 |  | 52.54 | 150.8 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-U-022-01 |  | M | N | 141 | N | 1030
JWS72004 | 08 | 32 | 4" | JWS | 72004 | C42S1 | N | 0 | JWS64017 | 32-E-7200 | 33.7/33.7 | 150.0/-45.0 | 3.0 | 30.0 |  | 50.56 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-U-022-01 |  | M | N | 141 | N | 1032
JWS72005 | 08 | 32 | 3/4" | JWS | 72005 | C42S1 | N | 0 | JWS72004 | VA72001 | 33.7/33.7 | 150.0/-45.0 | 3.0 | 30.0 |  | 50.56 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | M | N | 141 | N | 1032
JWS89001 | 08 | 32 | 3/4" | JWS | 89001 | B-1 | N | 0 | TP-N60101 (32-P-8906A) | TP-N30601 (32-E-8921A HEATING BARREL) | 10.0 | 120.0 | 7.0 | 50.0 |  | 15 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 50 | sh.68F | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 802
LA16002 |  | 32 | 1/2" | LA | 16002 | 4CS2 | HH | 30 | 32-D-1600 | LA16022 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16003 |  | 32 | 3/4" | LA | 16003 | 4CS2 | HH | 30 | 32-P-1601 | 32-S-1601 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16004 |  | 32 | 1/2" | LA | 16004 | 4CS2 | EH | 30 | 32-S-1601 | LA16021 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16004 |  | 32 | 1" | LA | 16004 | 4CS2 | HH | 30 | 32-S-1601 | LA16021 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16005 | 08 | 32 | 1" | LA | 16005 | 2CS2 | N | 0 | LA16004 | LA16006 | 6.0 | 200.0 | 1.0 | 110.0 |  | 9.62 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 110 | sh.10 | 2 | Art 4.3 | NA | N | NR | N | 32-P-023-01 |  | A | N | 210 | N | 409
LA16006 |  | 32 | 1-1/2" | LA | 16006 | 4CS2 | HH | 30 | LA16005 | 32-D-1600 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16007 |  | 32 | 1-1/2" | LA | 16007 | 4CS2 | ET | 30 | 32-D-1600 | LA16027 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16009 |  | 32 | 1" | LA | 16009 | 4CS2 | ET | 30 | 32-D-1601 | LA16007 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16010 |  | 32 | 3/4" | LA | 16010 | 1FS4 | ET | 30 | 32-P-1600A | LA16025 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16011 |  | 32 | 1/2" | LA | 16011 | 1FS4 | ET | 30 | 32-S-1600 | LA16031 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16011 |  | 32 | 1" | LA | 16011 | 1FS4 | ET | 30 | 32-S-1600 | LA16031 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16012 |  | 32 | 1/2" | LA | 16012 | 1FS4 | ET | 30 | LA16011 | LA16013 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LS31034 | 08 | 32 | 1/2" | LS | 31034 | B-5 | HB | 60 | PR31014 | LC31032 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31038 | 08 | 32 | 1" | LS | 31038 | B-5 | HB | 70 | PR31015 | LC31033 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31039 | 08 | 32 | 1" | LS | 31039 | B-5 | HB | 70 | PR31015 | LC31034 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31042 |  | 32 | 3/4" | LS | 31042 | B-5 | HB | 60 | PR24032 | LC31043 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31045 | 08 | 32 | 1-1/2" | LS | 31045 | B-5 | HB | 70 | PR31023 | LC31036 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31046 | 08 | 32 | 1-1/2" | LS | 31046 | B-5 | HB | 70 | PR31023 | LC31042 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31047 |  | 32 | 1/2" | LS | 31047 | B-5 | HB | 60 | LS63193 | PR31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS32001 |  | 32 | 3/4" | LS | 32001 | B-5 | HB | 60 | JLS32002 | LC32001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.24 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS33001 |  | 32 | 3/4" | LS | 33001 | C6S1 | HB | 50 | LS63048 | 32-E-3301 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS33002 |  | 32 | 3/4" | LS | 33002 | C6S1 | HA | 50 | 32-E-3301 | LC33001 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS33002 |  | 32 | 1-1/2" | LS | 33002 | C6S1 | HA | 50 | 32-E-3301 | LC33001 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS33003 |  | 32 | 3/4" | LS | 33003 | B-5 | HB | 60 | LS63048 | LC33003 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.25 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS34005 |  | 32 | 1/2" | LS | 34005 | B-5 | HB | 60 | 32-E-3400 | LC34005 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS34005 |  | 32 | 1" | LS | 34005 | B-5 | HB | 70 | 32-E-3400 | LC34005 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS34006 |  | 32 | 3/4" | LS | 34006 | B-5 | HB | 60 | 32-D-3400 | LC34001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N89098 | 08 | 32 | 1" | N | 89098 | B-1 | N | 0 | N01001 | N6700K | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N91014 | 08 | 32 | 2" | N | 91014 | 1CS2 | N | 0 | N91013 | 32-V-9001A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.70 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-01 |  | M | N | 000 | N | 166
HN67022 | 08 | 32 | 1-1/2" | HN | 67022 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67023 | 08 | 32 | 3/4" | HN | 67023 | C6S1 | N | 0 | HN67013 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67024 | 08 | 32 | 3/4" | HN | 67024 | C6S1 | N | 0 | HN67013 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN71001 | 08 | 32 | 1" | HN | 71001 | C6S1 | N | 0 | NITROGEN CONNECTION | ET71039 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.49 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN71005 | 08 | 32 | 1-1/2" | HN | 71005 | C6S1 | N | 0 | NITROGEN CONNECTION | ET71049 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-02 |  | E | N | 000 | N | 170
HN72001 | 08 | 32 | 1" | HN | 72001 | C6S1 | N | 0 | SP-04-172B2-01 | PR72004 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52A | 2 | I | MOD.A | Y | 1 | N | 32-P-007-01 |  | E | N | 000 | N | 170
BDL36010 |  | 32 | 6" | BDL | 36010 | B32S1 | P | 50 | BDL36018 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36011 | 08 | 32 | 1/2" | BDL | 36011 | B32S1 | N | 0 | PR36009 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36012 | 08 | 32 | 2" | BDL | 36012 | B32S1 | N | 0 | TP104,32-D-3603 | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36018 | 08 | 32 | 3" | BDL | 36018 | B32S1 | N | 0 | BDL36017 | BDL36010 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36020 | 08 | 32 | 2" | BDL | 36020 | B32S1 | N | 0 | TP-123 (32-D-3607) | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36024 | 08 | 32 | 3/4" | BDL | 36024 | B32S1 | N | 0 | T-185,32-E-3601 | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
BDL37001 | 08 | 32 | 1/2" | BDL | 37001 | B32S1 | N | 0 | 32-Z-2400A | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37001 | 08 | 32 | 1" | BDL | 37001 | B32S1 | N | 0 | 32-Z-2400A | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37002 | 08 | 32 | 1/2" | BDL | 37002 | B32S1 | N | 0 | 32-Z-2400B | BDL24067 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37002 | 08 | 32 | 1" | BDL | 37002 | B32S1 | N | 0 | 32-Z-2400B | BDL24067 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37003 | 08 | 32 | 1/2" | BDL | 37003 | B32S1 | N | 0 | 32-Z-3300A | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
FW68B12 | 08 | 45 | 6" | FW | 68B12 | PEB-69 | N | 0 | FW68B03 | FW68B96 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B14 | 08 | 45 | 8" | FW | 68B14 | PEB-69 | N | 0 | FW68B03 | FW68B95 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B15 | 08 | 45 | 6" | FW | 68B15 | B-7 | N | 0 | FW68B95 | HOSE STATION (INDOOR) | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B17 | 08 | 45 | 6" | FW | 68B17 | PEB-69 | N | 0 | FW68A10 | FW68B98 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B21 | 08 | 45 | 6" | FW | 68B21 | PEB-69 | N | 0 | FW68B03 | FW15476 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B23 | 08 | 45 | 1-1/2" | FW | 68B23 | B-7 | N | 0 | FW68B27 | 45-HR-6806 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B24 | 08 | 45 | 1-1/2" | FW | 68B24 | B-7 | N | 0 | FW68B27 | 45-HR-6807 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B25 | 08 | 45 | 1-1/2" | FW | 68B25 | B-7 | N | 0 | FW68B27 | 45-HR-6809 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A88 | 08 | 45 | 1-1/2" | FW | 68A88 | B-7 | N | 0 | FW68B0D | 45-HR-6811 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A88 | 08 | 45 | 4" | FW | 68A88 | B-7 | N | 0 | FW68B0D | 45-HR-6811 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B28 | 08 | 45 | 6" | FW | 68B28 | PEB-69 | N | 0 | FW68B0A | FW68A17 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B29 | 08 | 45 | 6" | FW | 68B29 | PEB-69 | N | 0 | FW68A17 | FW68B0B | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B34 | 08 | 45 | 6" | FW | 68B34 | B-7 | N | 0 | FW68B0N | XV-6802B | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B35 | 08 | 45 | 8" | FW | 68B35 | PEB-69 | N | 0 | FW68A10 | FW68B0M | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B39 | 08 | 45 | 8" | FW | 68B39 | PEB-69 | N | 0 | FW68A10 | FW68B0L | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B40 | 08 | 45 | 6" | FW | 68B40 | B-7 | N | 0 | FW68B0L | SPRINKLER SYSTEM FOR PP EXTRUSION | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-02 |  | E | N | 000 | N | 75
FW68B41 | 08 | 45 | 6" | FW | 68B41 | PEB-69 | N | 0 | FW68A10 | FW68B0O | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B43 | 08 | 45 | 6" | FW | 68B43 | B-7 | N | 0 | FW68B0G | DELUGE VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B45 | 08 | 45 | 6" | FW | 68B45 | PEB-69 | N | 0 | FW68A03 | FW68B0I | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B48 | 08 | 45 | 8" | FW | 68B48 | B-7 | N | 0 | FW68B0H | FW68R07 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
BDL72031 | 08 | 32 | 1/2" | BDL | 72031 | B32S1 | N | 0 | PR72061 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72032 | 08 | 32 | 1-1/2" | BDL | 72032 | B32S1 | N | 0 | PR72037 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72032 | 08 | 32 | 8" | BDL | 72032 | B32S1 | N | 0 | PR72037 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72033 | 08 | 32 | 1" | BDL | 72033 | B32S1 | N | 0 | PR72017 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72034 | 08 | 32 | 2" | BDL | 72034 | B32S1 | N | 0 | PR72039 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72034 | 08 | 32 | 6" | BDL | 72034 | B32S1 | N | 0 | PR72039 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72035 | 08 | 32 | 1/2" | BDL | 72035 | B32S1 | N | 0 | PR72015 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72036 | 08 | 32 | 6" | BDL | 72036 | B32S1 | N | 0 | PR72017 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72037 | 08 | 32 | 1/2" | BDL | 72037 | B32S1 | N | 0 | PR72062 | BDL72040 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72038 | 08 | 32 | 8" | BDL | 72038 | B32S1 | N | 0 | HEADER | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72039 | 08 | 32 | 1" | BDL | 72039 | B32S1 | N | 0 | PR72043 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72039 | 08 | 32 | 3" | BDL | 72039 | B32S1 | N | 0 | PR72043 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72039 | 08 | 32 | 6" | BDL | 72039 | B32S1 | N | 0 | PR72043 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72040 | 08 | 32 | 1" | BDL | 72040 | B32S1 | N | 0 | PR72015 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72041 | 08 | 32 | 1/2" | BDL | 72041 | B32S1 | N | 0 | VZ72025 | BDL72042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72042 | 08 | 32 | 1" | BDL | 72042 | B32S1 | N | 0 | BDL72044 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72044 | 08 | 32 | 1" | BDL | 72044 | B32S1 | N | 0 | PR72020 | BDL72042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72045 | 08 | 32 | 3" | BDL | 72045 | B32S1 | N | 0 | PR72044 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
DMW63001 | 08 | 32 | 1-1/2" | DMW | 63001 | SXB-48 | N | 0 | DMW64003 | LC63035 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.87 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-060-02 |  | M | N | 000 | N | 26
DMW63003 | 08 | 32 | 1" | DMW | 63003 | SXB-48 | N | 0 | DMW01001 | PW50020 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DMW63005 | 08 | 32 | 1" | DMW | 63005 | SXB-48 | N | 0 | DMW01001 | DMW50001 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DMW63006 | 08 | 32 | 2" | DMW | 63006 | SXB-48 | N | 0 | DMW64001 | TP-N50606 (32-D-8909, XV-8936) | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DMW63007 | 08 | 32 | 1" | DMW | 63007 | SXB-48 | N | 0 | DMW01001 | TP-N6 (DMW510115) | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DMW63009 | 08 | 32 | 2" | DMW | 63009 | SXB-48 | N | 0 | DMW01001 | PW52016 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DMW64003 | 08 | 32 | 3" | DMW | 64003 | SXB-48 | N | 0 | DMW01001 | DMW63001 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DO12001 | 08 | 32 | 3/4" | DO | 12001 | 1CS2 | N | 0 | DRUM | 32-P-1201 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12002 | 08 | 32 | 1/2" | DO | 12002 | 1CS2 | N | 0 | 32-P-1201 | DO12024 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12002 | 08 | 32 | 1" | DO | 12002 | 1CS2 | N | 0 | 32-P-1201 | DO12024 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12003 | 08 | 32 | 1-1/2" | DO | 12003 | 1CS2 | N | 0 | DO12004 | 32-D-1200A | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12004 | 08 | 32 | 1" | DO | 12004 | 1CS2 | N | 0 | 32-S-1201 | 32-D-1200B | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12005 |  | 32 | 1" | DO | 12005 | 1CS2 | ET | 30 | 32-D-1200A | 32-S-1200A | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12006 | 08 | 32 | 1/2" | DO | 12006 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12006 | 08 | 32 | 2" | DO | 12006 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
ET22007 | 08 | 32 | 1/2" | ET | 22007 | 3FS4 | N | 0 | ET22010 | P23022 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | N | 32-P-044-01 |  | G | N | 041 | N | 322 | 36,10,5
ET22007 | 08 | 32 | 1-1/2" | ET | 22007 | 3FS4 | N | 0 | ET22010 | P23022 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | N | 32-P-044-01 |  | G | N | 041 | N | 322 | 36,10,5
ET22008 | 08 | 32 | 3/4" | ET | 22008 | 1FS4 | N | 0 | HN22002 | ET22009 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | Art 4.3 | NA | N | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
CT14005 | 08 | 32 | 3" | CT | 14005 | 1CS2 | N | 0 | 32-Z-1402 | VZ14010 | 10.0/0.5 | 80.0/60.0 | 8.0/0.01 | 30.0/30.0 |  | 15 | 28.5 | IO | DRY CATALYST | SL | - | - | <1.5 | 30 | sh.7 | 1 | I | MOD.A | Y | NR | N | 32-P-026-01 |  | M | N | 232 | N | 283 | 23,25
CT14007 | 08 | 32 | 3/4" | CT | 14007 | 1CS2 | N | 0 | 32-S-1400A | BUCKET | 10.0/0.5 | 80.0/60.0 | 8.0/0.01 | 30.0/30.0 |  | 15 | 28.5 | IO | DRY CATALYST | SL | - | - | <1.5 | 30 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 283 | 23,25
CT14008 | 08 | 32 | 3/4" | CT | 14008 | 1CS2 | N | 0 | 32-S-1400B | BUCKET | 10.0/0.5 | 80.0/60.0 | 8.0/0.01 | 30.0/30.0 |  | 15 | 28.5 | IO | DRY CATALYST | SL | - | - | <1.5 | 30 | sh.8 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 283 | 23,25
CT14009 |  | 32 | 1" | CT | 14009 | 3FS3 | CF | 25 | VZ14016 | JCHW14002 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
CT14010 |  | 32 | 1/2" | CT | 14010 | 3FS3 | CF | 25 | VZ14012 | CT14002 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
CT15001 | 08 | 32 | 3/8" | CT | 15001 | 3FS3 | N | 0 | CT15002 | CT20001 | 70.0 | 100.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-04 |  | A | N | 232 | N | 282 | 23,29,25
CT15001 | 08 | 32 | 1/2" | CT | 15001 | 3FS3 | JP | 0 | CT15002 | CT20001 | 70.0 | 100.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-04 |  | A | N | 232 | N | 282 | 23,29,25
CT15002 | 08 | 32 | 1/2" | CT | 15002 | 3FS3 | N | 0 | CT15022 | CT15001 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-04 |  | M | N | 232 | N | 286 | 23,29,25
CT15003 | 08 | 32 | 1" | CT | 15003 | 3FS3 | CF | 25 | CT14004 | CT15011 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
CT20001 | 08 | 32 | 1/2" | CT | 20001 | 3FS3 | N | 0 | CT15001 | 32-R-2000 | 70.0 | 100.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.11 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-04 |  | A | N | 232 | N | 282 | 23,29,25
HCM24058 |  | 32 | 3" | HCM | 24058 | C42S1 | P | 50 | HCM24063 | HCM23046 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24059 |  | 32 | 2" | HCM | 24059 | D20S1 | ET | 30 | HCM24080 | HCM23046 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24059 |  | 32 | 6" | HCM | 24059 | D20S1 | ET | 30 | HCM24080 | HCM23046 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24061 | 08 | 32 | 3/4" | HCM | 24061 | 3FS4 | HB | 30 | TP-2 (HCM240161) | HCM24098 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM24062 |  | 32 | 3/4" | HCM | 24062 | 3FS4 | CF | 25 | HCM24064 | TP-1 (HCM240162) | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
BDL24060 | 08 | 32 | 1" | BDL | 24060 | B32S1 | N | 0 | HCM24063 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24061 | 08 | 32 | 3/4" | BDL | 24061 | B32S1 | N | 0 | HCM24066 | BDL24084 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24061 | 08 | 32 | 1" | BDL | 24061 | B32S1 | N | 0 | HCM24066 | BDL24084 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24062 | 08 | 32 | 3/4" | BDL | 24062 | B32S1 | N | 0 | BDL01037 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24062 | 08 | 32 | 1" | BDL | 24062 | B32S1 | N | 0 | BDL01037 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24063 | 08 | 32 | 1" | BDL | 24063 | B32S1 | N | 0 | HCM24092 | HCM24092 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24064 | 08 | 32 | 3/4" | BDL | 24064 | B32S1 | N | 0 | HCM24069 | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24065 | 08 | 32 | 1" | BDL | 24065 | B32S1 | N | 0 | HCM24074 | BDL24067 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24066 | 08 | 32 | 3/4" | BDL | 24066 | B32S1 | N | 0 | HCM24093 | HCM24093 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24066 | 08 | 32 | 1" | BDL | 24066 | B32S1 | N | 0 | HCM24093 | HCM24093 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24067 | 08 | 32 | 3/4" | BDL | 24067 | B32S1 | N | 0 | BDL24066 | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24067 | 08 | 32 | 1" | BDL | 24067 | B32S1 | N | 0 | BDL24066 | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24068 | 08 | 32 | 1" | BDL | 24068 | B32S1 | N | 0 | BDL24076 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24069 | 08 | 32 | 1" | BDL | 24069 | B32S1 | N | 0 | BDL24078 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24070 | 08 | 32 | 1" | BDL | 24070 | B32S1 | N | 0 | HCM24070 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24071 | 08 | 32 | 1" | BDL | 24071 | B32S1 | N | 0 | HCM24069 | BDL24074 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24072 | 08 | 32 | 3/4" | BDL | 24072 | B32S1 | N | 0 | BDL24001 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24072 | 08 | 32 | 1" | BDL | 24072 | B32S1 | N | 0 | BDL24001 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CWR64011 | 08 | 32 | 4" | CWR | 64011 | UGB-1PE | N | 0 | CWR80001 | CWR64015 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-03 |  | E | N | 000 | N | 16
CWR64012 | 08 | 32 | 32" | CWR | 64012 | UGB-1PE | N | 0 | CWR64013 | CWR01010 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
CWR64013 | 08 | 32 | 1-1/2" | CWR | 64013 | B-1 | N | 0 | 32-E-6400B | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64013 | 08 | 32 | 20" | CWR | 64013 | B-1 | N | 0 | 32-E-6400B | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64014 | 08 | 32 | 3/4" | CWR | 64014 | B-1 | N | 0 | 32-E-6400A | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64014 | 08 | 32 | 14" | CWR | 64014 | B-1 | N | 0 | 32-E-6400A | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
JWR37004 | 08 | 32 | 1-1/2" | JWR | 37004 | B-1 | N | 0 | 32-Z-3300B | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37006 | 08 | 32 | 1-1/2" | JWR | 37006 | B-1 | N | 0 | 32-Z-4300 | JWR40003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PR23029 |  | 32 | 3/4" | PR | 23029 | D20S1 | ST | 30 | PR23032 | 32-D-2300 | 55.0/55.0 | -45.0/190.0 | 40.0/40.0 | 80.0/121.0 |  | 82.81 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 334 | 10
PR23029 |  | 32 | 2" | PR | 23029 | D20S1 | ST | 40 | PR23032 | 32-D-2300 | 55.0/55.0 | -45.0/190.0 | 40.0/40.0 | 80.0/121.0 |  | 82.81 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | N | 141 | N | 334 | 10
PR23031 | 08 | 32 | 1" | PR | 23031 | D20S1 | N | 0 | 32-D-2300 | BDL23016 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 153.15 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
JWR63003 | 08 | 32 | 2" | JWR | 63003 | B-1 | N | 0 | JWR63002 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64001 | 08 | 32 | 4" | JWR | 64001 | B-1 | N | 0 | 32-D-6400 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64002 |  | 32 | 2" | JWR | 64002 | B-1 | HB | 30 | JWR64001 | JWR64003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64003 |  | 32 | 12" | JWR | 64003 | B-1 | HB | 30 | ACW | WW64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64004 | 08 | 32 | 1/2" | JWR | 64004 | B-1 | N | 0 | 32-D-6400 | JWR64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64004 | 08 | 32 | 1" | JWR | 64004 | B-1 | N | 0 | 32-D-6400 | JWR64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64004 | 08 | 32 | 3" | JWR | 64004 | B-1 | N | 0 | 32-D-6400 | JWR64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64006 | 08 | 32 | 2" | JWR | 64006 | UGB-1PE | N | 0 | JWR64042 | JWR64005 | 9.0 | 80.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-02 |  | E | N | 000 | N | 19
JWR64006 | 08 | 32 | 32" | JWR | 64006 | UGB-1PE | N | 0 | JWR64042 | JWR64005 | 9.0 | 80.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-02 |  | E | N | 000 | N | 19
JWR64007 | 08 | 32 | 1-1/2" | JWR | 64007 | B-1 | N | 0 | JWR64006 | 32-E-6400B | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64008 | 08 | 32 | 20" | JWR | 64008 | B-1 | N | 0 | JWR64006 | 32-E-6400C | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64041 | 08 | 32 | 8" | JWR | 64041 | B-1 | N | 0 | JWR61002 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64042 | 08 | 32 | 16" | JWR | 64042 | B-1 | N | 0 | HEADER | JWR64006 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64043 | 08 | 32 | 14" | JWR | 64043 | UGB-1PE | N | 0 | JWR40003 | JWR64006 | 9.0 | 80.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-02 |  | E | N | 000 | N | 19
JWR64044 | 08 | 32 | 8" | JWR | 64044 | B-1 | N | 0 | JWR63001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64045 | 08 | 32 | 2" | JWR | 64045 | B-1 | N | 0 | JWR23004 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
N67111 | 08 | 32 | 3/4" | N | 67111 | B-1 | N | 0 | N67013 | BDL60056 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67112 | 08 | 32 | 3/4" | N | 67112 | B-1 | N | 0 | N67013 | BDL60057 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67113 | 08 | 32 | 1" | N | 67113 | B-1 | N | 0 | N67013 | BDL60058 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67114 | 08 | 32 | 3/4" | N | 67114 | B-1 | N | 0 | N67039 | BDL60059 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N71017 | 08 | 32 | 2" | N | 71017 | B4S2 | P | 30 | N72007 | TP001 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.48 | 2 | Art 4.3 | NA | N | 7 | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N72006 | 08 | 32 | 3" | N | 72006 | B4S2 | HA | 70 | N72008 | PR72022 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.52B | 2 | Art 4.3 | NA | N | NR | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N72007 |  | 32 | 3" | N | 72007 | B4S2 | P | 30 | PR72015 | N71017 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.53 | 2 | Art 4.3 | NA | N | 7 | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N72008 | 08 | 32 | 3/4" | N | 72008 | B4S2 | HA | 60 | TP-013 (N720129) | N72006 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.48 | 2 | Art 4.3 | NA | N | NR | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N72008 | 08 | 32 | 2" | N | 72008 | B4S2 | HA | 70 | TP-013 (N720129) | N72006 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.48 | 2 | Art 4.3 | NA | N | NR | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
LA16012 |  | 32 | 1" | LA | 16012 | 1FS4 | ET | 30 | LA16011 | LA16013 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16013 |  | 32 | 1" | LA | 16013 | 4CS2 | ET | 30 | LA16012 | 32-D-1601 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16015 |  | 32 | 1/2" | LA | 16015 | 1FS4 | ET | 30 | LA16011 | P40031 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16015 |  | 32 | 1" | LA | 16015 | 1FS4 | ET | 30 | LA16011 | P40031 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16019 |  | 32 | 1/2" | LA | 16019 | 1FS4 | ET | 30 | 32-P-1600B | 32-S-1600 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16019 |  | 32 | 1" | LA | 16019 | 1FS4 | ET | 30 | 32-P-1600B | 32-S-1600 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16021 |  | 32 | 1" | LA | 16021 | B4S2 | ET | 30 | LA16004 | 32-D-6500 | 6.0 | 180.0 | 1.0 | 80.0 |  | 9.03 | 29.4 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 80 | sh.10 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-023-01 |  | E | N | 210 | N | 407
LA16021 |  | 32 | 1-1/2" | LA | 16021 | B4S2 | ET | 30 | LA16004 | 32-D-6500 | 6.0 | 180.0 | 1.0 | 80.0 |  | 9.03 | 29.4 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 80 | sh.10 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-023-01 |  | E | N | 210 | N | 407
LA16022 |  | 32 | 1" | LA | 16022 | 4CS2 | HH | 30 | LA16001 | 32-P-1601 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LS01001 |  | 32 | 1/2" | LS | 01001 | B-5 | HB | 60 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS01001 |  | 32 | 3/4" | LS | 01001 | B-5 | HB | 60 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS01001 |  | 32 | 3" | LS | 01001 | B-5 | HB | 80 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS01001 |  | 32 | 10" | LS | 01001 | B-5 | HB | 100 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS02001 |  | 32 | 1/2" | LS | 02001 | B-5 | HB | 60 | LS63177 | LS66002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N91016 | 08 | 32 | 2" | N | 91016 | 1CS2 | N | 0 | N91013 | 32-V-9001C | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.70 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-01 |  | M | N | 000 | N | 166
N91020 | 08 | 32 | 2" | N | 91020 | 1CS2 | N | 0 | N91013 | TP-257 (CVA910247) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.71 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-01 |  | M | N | 000 | N | 166
BDL37003 | 08 | 32 | 1" | BDL | 37003 | B32S1 | N | 0 | 32-Z-3300A | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37004 | 08 | 32 | 1" | BDL | 37004 | B32S1 | N | 0 | 32-Z-3300B | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37006 | 08 | 32 | 1/2" | BDL | 37006 | B32S1 | N | 0 | 32-Z-4300 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37006 | 08 | 32 | 1" | BDL | 37006 | B32S1 | N | 0 | 32-Z-4300 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL37008 | 08 | 32 | 1" | BDL | 37008 | B32S1 | N | 0 | 32-Z-7300 | BDL73044 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL40025 | 08 | 32 | 4" | BDL | 40025 | B32S1 | N | 0 | PR40032 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40026 | 08 | 32 | 3/4" | BDL | 40026 | B32S1 | N | 0 | PR40022 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40026 | 08 | 32 | 1" | BDL | 40026 | B32S1 | N | 0 | PR40022 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40027 | 08 | 32 | 3/4" | BDL | 40027 | B32S1 | N | 0 | PR40029 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40028 | 08 | 32 | 1" | BDL | 40028 | B32S1 | N | 0 | HD40006 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40029 | 08 | 32 | 3/4" | BDL | 40029 | B32S1 | N | 0 | ET71039 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40029 | 08 | 32 | 1" | BDL | 40029 | B32S1 | N | 0 | ET71039 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40031 | 08 | 32 | 1" | BDL | 40031 | B32S1 | N | 0 | BDL40035 | BDL40030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40032 | 08 | 32 | 1/2" | BDL | 40032 | B32S1 | N | 0 | P40047 | BDL40031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40035 | 08 | 32 | 1" | BDL | 40035 | B32S1 | N | 0 | P40029 | BDL40031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40036 |  | 32 | 6" | BDL | 40036 | B32S1 | SB | 100 | BDL40037 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40036 |  | 32 | 8" | BDL | 40036 | B32S1 | SB | 100 | BDL40037 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40037 |  | 32 | 6" | BDL | 40037 | B32S1 | SB | 100 | PR40026 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
LC66003 |  | 32 | 3/4" | LC | 66003 | B-5 | HB | 30 | LS02001 | INSIDE CURBED AREA | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC66004 |  | 32 | 3/4" | LC | 66004 | B-5 | HB | 30 | LS66001 | INSIDE CURBED AREA | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | Y | 000 | N | 130
LC71001 |  | 32 | 3/4" | LC | 71001 | B-5 | HB | 30 | LS71011 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.48 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC71002 |  | 32 | 1/2" | LC | 71002 | B-5 | HB | 30 | LS71012 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.48 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC71002 |  | 32 | 1" | LC | 71002 | B-5 | HB | 40 | LS71012 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.48 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC72002 |  | 32 | 1" | LC | 72002 | B-5 | HB | 40 | LS72003 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.51 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC72002 |  | 32 | 1-1/2" | LC | 72002 | B-5 | HB | 40 | LS72003 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.51 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC72004 | 08 | 32 | 1" | LC | 72004 | B-5 | HB | 40 | TP-005 (LC720158) | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC72006 |  | 32 | 3/4" | LC | 72006 | B-5 | HB | 30 | LS72005 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.51 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC73001 |  | 32 | 1/2" | LC | 73001 | B-5 | HB | 30 | LS73005 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.55 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC73006 |  | 32 | 1/2" | LC | 73006 | B-5 | HB | 30 | LS73005 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.55 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
N12028 | 08 | 32 | 1/2" | N | 12028 | 1CS2 | N | 0 | N12018 | 32-LT-1202 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12030 | 08 | 32 | 1-1/2" | N | 12030 | 1CS2 | N | 0 | N12025 | 32-LT-1205 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N13003 |  | 32 | 1" | N | 13003 | B-1 | ET | 30 | 32-D-1301 | N13002 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N14001 | 08 | 32 | 1/2" | N | 14001 | 1CS2 | N | 0 | N67038 | N14002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14001 | 08 | 32 | 1-1/2" | N | 14001 | 1CS2 | N | 0 | N67038 | N14002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14002 |  | 32 | 3/4" | N | 14002 | 1CS2 | ET | 30 | 32-D-1400A | N14023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14002 | 08 | 32 | 1" | N | 14002 | 1CS2 | N | 0 | 32-D-1400A | N14023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14002 | 08 | 32 | 2" | N | 14002 | 1CS2 | N | 0 | 32-D-1400A | N14023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14005 | 08 | 32 | 3/4" | N | 14005 | 1CS2 | N | 0 | CT14006 | VA14005 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14006 | 08 | 32 | 3/4" | N | 14006 | 1CS2 | N | 0 | N67033 | N14007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14007 | 08 | 32 | 1/2" | N | 14007 | 1CS2 | N | 0 | 32-D-1400B | N14020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14007 | 08 | 32 | 1" | N | 14007 | 1CS2 | N | 0 | 32-D-1400B | N14020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14007 | 08 | 32 | 2" | N | 14007 | 1CS2 | N | 0 | 32-D-1400B | N14020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14011 | 08 | 32 | 3/4" | N | 14011 | 1CS2 | N | 0 | 32-Z-1400B | N14007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14012 | 08 | 32 | 3/4" | N | 14012 | 1CS2 | N | 0 | 32-Z-1400A | N14002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
LS31026 |  | 32 | 1-1/2" | LS | 31026 | B-5 | HB | 70 | 32-D-3100 | LC31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31030 |  | 32 | 1/2" | LS | 31030 | B-5 | HB | 60 | PR31016 | LC31014 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31043 | 08 | 32 | 1-1/2" | LS | 31043 | B-5 | HB | 70 | PR31023 | LC31035 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS33001 |  | 32 | 1/2" | LS | 33001 | C6S1 | HB | 50 | LS63048 | 32-E-3301 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS33001 |  | 32 | 3" | LS | 33001 | C6S1 | HB | 60 | LS63048 | 32-E-3301 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | Y | 32-U-052-01 |  | E | N | 141 | N | 1092
LS33001 |  | 32 | 4" | LS | 33001 | C6S1 | HB | 70 | LS63048 | 32-E-3301 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | Y | 32-U-052-01 |  | E | N | 141 | N | 1092
LS34005 |  | 32 | 3/4" | LS | 34005 | B-5 | HB | 60 | 32-E-3400 | LC34005 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50003 |  | 32 | 3" | LS | 50003 | 3CS6 | HB | 60 | LS50002 | LS50004 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50003 |  | 32 | 6" | LS | 50003 | 3CS6 | HB | 70 | LS50002 | LS50004 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50009 |  | 32 | 3/4" | LS | 50009 | 3CS6 | HB | 30 | LS63002 | 32-T-5001 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-02 |  | M | N | 000 | N | 91
LS50009 |  | 32 | 3" | LS | 50009 | 3CS6 | HB | 50 | LS63002 | 32-T-5001 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-02 |  | M | N | 000 | N | 91
LS50009 |  | 32 | 6" | LS | 50009 | 3CS6 | HB | 50 | LS63002 | 32-T-5001 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-02 |  | M | N | 000 | N | 91
LS50031 |  | 32 | 1" | LS | 50031 | B-5 | HB | 30 | LS50033 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS50034 |  | 32 | 1" | LS | 50034 | B-5 | HB | 30 | LS50033 | 32-D-5011 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50038 |  | 32 | 3/4" | LS | 50038 | B-5 | HB | 60 | 32-S-5001 | LC50009 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50047 |  | 32 | 1/2" | LS | 50047 | B-5 | HB | 30 | JLS50005 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50048 |  | 32 | 3/4" | LS | 50048 | B-5 | HB | 30 | LS63052 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS50048 |  | 32 | 1" | LS | 50048 | B-5 | HB | 30 | LS63052 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
FW68G49 | 08 | 45 | 2" | FW | 68G49 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68H17 | 08 | 32 | 1" | FW | 68H17 | B-13 | N | 0 | FW68H14 | FW68H18 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H20 | 08 | 32 | 1" | FW | 68H20 | B-13 | N | 0 | FW68H15 | FW68H19 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H29 | 08 | 32 | 3" | FW | 68H29 | B-13 | N | 0 | FW68H30 | FW68H15 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H33 | 08 | 32 | 3" | FW | 68H33 | B-13 | N | 0 | FW68H29 | FW68H03 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H36 | 08 | 32 | 1-1/2" | FW | 68H36 | B-13 | N | 0 | FW68H35 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H38 | 08 | 32 | 1-1/2" | FW | 68H38 | B-13 | N | 0 | FW68H49 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H60 | 08 | 32 | 1-1/2" | FW | 68H60 | B-13 | N | 0 | FW68C07 | FW68H58 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I15 | 08 | 32 | 1" | FW | 68I15 | B-13 | N | 0 | FW68I17 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I16 | 08 | 32 | 1" | FW | 68I16 | B-13 | N | 0 | FW68I10 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I21 | 08 | 32 | 1-1/2" | FW | 68I21 | B-13 | N | 0 | FW68I18 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I27 | 08 | 32 | 1-1/2" | FW | 68I27 | B-13 | N | 0 | FW68I20 | FW68I37 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I38 | 08 | 32 | 1" | FW | 68I38 | B-13 | N | 0 | FW68I37 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I38 | 08 | 32 | 1-1/2" | FW | 68I38 | B-13 | N | 0 | FW68I37 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68K06 | 08 | 32 | 4" | FW | 68K06 | B-13 | N | 0 | XV6804A | FW68M25 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68K09 | 08 | 32 | 2" | FW | 68K09 | B-7 | N | 0 | FW68K11 | FW68K01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68L02 | 08 | 32 | 1" | FW | 68L02 | B-13 | N | 0 | FW68K12 | FW68L10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L02 | 08 | 32 | 3" | FW | 68L02 | B-13 | N | 0 | FW68K12 | FW68L10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L02 | 08 | 32 | 6" | FW | 68L02 | B-13 | N | 0 | FW68K12 | FW68L10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
BDL01009 | 08 | 32 | 10" | BDL | 01009 | B32S1 | N | 0 | BDL61001 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01036 |  | 32 | 3/4" | BDL | 01036 | B4S1 | P | 50 | HD01001 | BDL01039 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL20001 | 08 | 32 | 1/2" | BDL | 20001 | B32S1 | N | 0 | O20009 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.11 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23016 | 08 | 32 | 2" | BDL | 23016 | B32S1 | N | 0 | BDL23024 | BDL24079 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23069 | 08 | 32 | 1/2" | BDL | 23069 | B32S1 | N | 0 | P23032 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
HCM31023 | 08 | 32 | 3/4" | HCM | 31023 | C42S1 | N | 0 | CD31006 | BDL31037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32026 |  | 32 | 3/4" | HCM | 32026 | C42S1 | HB | 30 | 32-E-3200 | 32-D-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32026 |  | 32 | 1-1/2" | HCM | 32026 | C42S1 | HB | 30 | 32-E-3200 | 32-D-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32026 |  | 32 | 6" | HCM | 32026 | C42S1 | HB | 30 | 32-E-3200 | 32-D-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32030 | 08 | 32 | 3/4" | HCM | 32030 | C42S1 | HB | 30 | TP-06B, (32-D-3202B) | HCM32044 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24G | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM32030 | 08 | 32 | 4" | HCM | 32030 | C42S1 | HB | 40 | TP-06B, (32-D-3202B) | HCM32044 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24G | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM32034 |  | 32 | 3" | HCM | 32034 | C42S1 | HB | 30 | HCM32026 | BDL32016 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32042 | 08 | 32 | 1" | HCM | 32042 | C42S1 | HB | 30 | TP-03B (32-D-3201B) | HCM32032 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24G | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
PR36030 | 08 | 32 | 2" | PR | 36030 | C42S1 | P | 50 | 32-D-3607 | PR36023 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR40026 |  | 32 | 1" | PR | 40026 | C42S1 | HB | 30 | PR43027 | 32-Z-4001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR40029 |  | 32 | 3/4" | PR | 40029 | C42S1 | HB | 30 | ET40005 | PR40020 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 338 | 10
PR40029 |  | 32 | 1" | PR | 40029 | C42S1 | HB | 30 | ET40005 | PR40020 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 338 | 10
PR40029 |  | 32 | 1-1/2" | PR | 40029 | C42S1 | HB | 30 | ET40005 | PR40020 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 338 | 10
PR43039 |  | 32 | 4" | PR | 43039 | C42S1 | HB | 30 | 32-T-4300 | PR43038 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43042 |  | 32 | 1" | PR | 43042 | C42S1 | HB | 30 | 32-E-4302 | PR43043 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43042 |  | 32 | 2" | PR | 43042 | C42S1 | HB | 30 | 32-E-4302 | PR43043 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43042 |  | 32 | 4" | PR | 43042 | C42S1 | HB | 30 | 32-E-4302 | PR43043 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
CHWR21008 |  | 32 | 3/4" | CHWR | 21008 | D3S1 | CF | 25 | 32-E-2100 | CHWR21009 | 55.0 | 150.0 | 4.0 | 7.0 |  | 82.51 | 153.15 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.12 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 1049
CHWR21008 |  | 32 | 6" | CHWR | 21008 | D3S1 | CF | 40 | 32-E-2100 | CHWR21009 | 55.0 | 150.0 | 4.0 | 7.0 |  | 82.51 | 153.15 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.12 | 2 | II | MOD.A2 | Y | 20 | Y | 32-U-023-02 |  | E | N | 010 | N | 1049
CHWR43010 |  | 32 | 3/4" | CHWR | 43010 | C42S1 | CF | 25 | 32-E-4302 | CHWR43011 | 28.0/28.0 | 180.0/-45.0 | 2.0 | 7.0 |  | 42.12 | 76.65 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.33 | 2 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | M | N | 010 | N | 1052
CHWR43010 |  | 32 | 6" | CHWR | 43010 | C42S1 | CF | 40 | 32-E-4302 | CHWR43011 | 28.0/28.0 | 180.0/-45.0 | 2.0 | 7.0 |  | 42.12 | 76.65 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.33 | 2 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | M | N | 010 | N | 1052
CHWR61009 | 08 | 32 | 3/4" | CHWR | 61009 | B-1 | N | 0 | N67016 | 32-D-6101 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
CHWR61009 | 08 | 32 | 2" | CHWR | 61009 | B-1 | N | 0 | N67016 | 32-D-6101 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
PP81008 | 08 | 32 | 8" | PP | 81008 | 5CS7 | N | 0 | TP-077 (32-HV-8149) | 32-V-8107 | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.62 | 1 | II | MOD.A2 | Y | NR | N | 32-P-082-07 |  | M | N | 110 | N | 439 | 6,23,25
PP89013 | 08 | 32 | 20" | PP | 89013 | 5CS7 | N | 0 | TP-N50406 (A-8900) | COLLECTING BOX AT GROUND FLOOR | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.68M | 1 | NA | NA | NA | NR | N | 32-P-070-07 |  | M | N | 110 | N | 443 | 6,25,23
PR01001 | 08 | 32 | 3/4" | PR | 01001 | C42S1 | N | 0 | PR01002 | 32-D-7200 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
PR01001 | 08 | 32 | 6" | PR | 01001 | C42S1 | N | 0 | PR01002 | 32-D-7200 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
PR22014 | 08 | 32 | 3/4" | PR | 22014 | D20S1 | N | 0 | PR22016 | HCM24006 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22014 | 08 | 32 | 4" | PR | 22014 | D20S1 | N | 0 | PR22016 | HCM24006 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22016 | 08 | 32 | 4" | PR | 22016 | D20S1 | N | 0 | PR33019 | PR22014 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR23005 |  | 32 | 1/2" | PR | 23005 | D20S1 | ST | 30 | 32-D-2300 | 32-S-2300 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23005 |  | 32 | 1" | PR | 23005 | D20S1 | ST | 30 | 32-D-2300 | 32-S-2300 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23005 |  | 32 | 1-1/2" | PR | 23005 | D20S1 | ST | 30 | 32-D-2300 | 32-S-2300 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23005 |  | 32 | 4" | PR | 23005 | D20S1 | ST | 40 | 32-D-2300 | 32-S-2300 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
VZ71006 | 08 | 32 | 3/4" | VZ | 71006 | QXC25S1 | ET | 30 | 32-S-7100A | - | 38.3 | 120.0 | 28.0 | 40.0 |  | 57.45 | 74.4 | H | VESSEL TRIM | G | - | - | >1.5 | 40 | sh.49 | 1 | Art 4.3 | NA | N | NR | N | 32-P-006-03 |  | G | N | 041 | N | 327 | ,10
VZ72025 | 08 | 32 | 1/2" | VZ | 72025 | C42S1 | N | 0 | 32-T-7203 | PR72022 | 43.7/43.7 | 150.0/-45.0 | 23.5 | 40.0 |  | 65.56 | 76.65 | H | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 431 | ,15
VZ73007 | 08 | 32 | 3/4" | VZ | 73007 | B32S1 | N | 0 | 32-D-7302 | 32-D-7302 | 14.0/14.0 | 80.0/-7.0 | 5.0 | 50.0 |  | 21 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 50 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 730 | 15
VZ73007 |  | 32 | 1-1/2" | VZ | 73007 | B32S1 | HE | 30 | 32-D-7302 | 32-D-7302 | 14.0/14.0 | 80.0/-7.0 | 5.0 | 50.0 |  | 21 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 50 | sh.55 | 1 | I | MOD.A | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 730 | 15
JWS64003 | 08 | 32 | 3/4" | JWS | 64003 | B-1 | N | 0 | 32-E-6400C | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64003 | 08 | 32 | 20" | JWS | 64003 | B-1 | N | 0 | 32-E-6400C | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64004 | 08 | 32 | 20" | JWS | 64004 | UGB-1PE | N | 0 | JWS64001 | JWS64073 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
JWS64012 |  | 32 | 3/4" | JWS | 64012 | B-1 | SB | 100 | JWS64008 | JWR64006 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64012 |  | 32 | 20" | JWS | 64012 | B-1 | SB | 100 | JWS64008 | JWR64006 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64025 | 08 | 32 | 8" | JWS | 64025 | B-1 | N | 0 | JWS64055 | 32-E-4001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64025 | 08 | 32 | 18" | JWS | 64025 | B-1 | N | 0 | JWS64055 | 32-E-4001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64037 | 08 | 32 | 1/2" | JWS | 64037 | B-1 | N | 0 | JWS64056 | JW73001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64047 | 08 | 32 | 12" | JWS | 64047 | B-1 | N | 0 | JWS64054 | 32-E-2300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64047 | 08 | 32 | 24" | JWS | 64047 | B-1 | N | 0 | JWS64054 | 32-E-2300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
PW51011 |  | 32 | 3/4" | PW | 51011 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ12011 |  | 32 | 2" | VZ | 12011 | 1CS2 | ET | 30 | 32-D-1200C | 32-D-1200C | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ14012 |  | 32 | 1" | VZ | 14012 | QXC25S1 | CF | 25 | 32-D-1401A | 32-D-1401A | 20.0 | 190.0 | 10.0 | 6.0 |  | 31.64 | 74.4 | H | VESSEL TRIM | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 231 | N | 279
VZ15004 |  | 32 | 1/2" | VZ | 15004 | B4S2 | EH | 30 | 32-D-1501 | 32-D-1501 | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | NA | NA | NA | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 239 | 23,25
VZ16008 | 08 | 32 | 1" | VZ | 16008 | B-1 | ET | 30 | 32-D-1602 | - | 0.5 | 150.0 | 0.0 | 30.0 |  | 0.55 | 26.46 | P | VESSEL TRIM | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 144
VZ24003 | 08 | 32 | 3/4" | VZ | 24003 | C42S1 | N | 0 | 32-T-2401 | - | 42.0/42.0 | 150.0/-45.0 | 32.0/32.0 | 75.0/40.0 |  | 0 | 0 | V | VESSEL TRIM | LG | - | - | >1.5 | 40 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | G | Y | 141 | N | 514 | 10
VZ50008 |  | 32 | 1-1/2" | VZ | 50008 | 1CR9 | HB | 30 | 32-D-5001 | 32-D-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | VESSEL TRIM | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-2 | N | 141 | N | 441 | 16,10,11,13
VZ91015 | 08 | 32 | 2" | VZ | 91015 | 5CS7 | N | 0 | 32-H-9001B | - | 0.1/-0.01 | 100.0/100.0 | 0.01/0.01 | 60.0/80.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 60 | sh.70 | 1 | NA | NA | NA | NR | N | 32-P-082-02 |  | M | N | 110 | N | 447 | 6,25,23
WW20002 | 08 | 32 | 4" | WW | 20002 | B4S2 | N | 0 | REMOVABLE PLUG | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64003 | 08 | 32 | 1-1/2" | WW | 64003 | B4S2 | N | 0 | FROM LC-24014 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64007 | 08 | 32 | 1-1/2" | WW | 64007 | B4S2 | N | 0 | FROM LC-23049 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
SL21001 | 08 | 32 | 1-1/2" | SL | 21001 | 2FS4 | N | 0 | 32-R-2100 | BDH21001 | 50.0/50.0 | -40.0/200.0 | 37.0 | 20.0 |  | 80.16 | 148.95 | H | SLURRY | S | - | - | <1.5 | 20 | sh.12 | 2 | I | MOD.A | Y | NR | N | 32-P-042-01 |  | H-1 | N | 110 | N | 411 | 12,15,6,17
LS51001 |  | 32 | 1/2" | LS | 51001 | B-5 | HB | 60 | 32-D-5102 | LC51004 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60004 |  | 32 | 2" | LS | 60004 | B-5 | HB | 80 | BDH60006 | 32-D-6002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60013 |  | 32 | 1" | LS | 60013 | B-5 | HB | 70 | PURGE CONNECTION | BDL60043 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78A | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60018 |  | 32 | 1" | LS | 60018 | B-5 | HB | 70 | PURGE CONNECTION | BDL60048 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60031 |  | 32 | 1" | LS | 60031 | B-5 | HB | 70 | PURGE CONNECTION | FL60001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS6300V |  | 32 | 1-1/2" | LS | 6300V | B-5 | HB | 70 | LS63201 | 32-1121-S-004 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63020 |  | 32 | 1" | LS | 63020 | B-5 | HB | 70 | LS63013 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63027 |  | 32 | 2" | LS | 63027 | B-5 | HB | 80 | LS63199 | 32-E-5200 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
BDL40030 | 08 | 32 | 2" | BDL | 40030 | B32S1 | N | 0 | TP-7 (ET04010) | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40043 | 08 | 32 | 1/2" | BDL | 40043 | B32S1 | N | 0 | P40036 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CO26026 | 08 | 32 | 1/2" | CO | 26026 | 1IS5 | N | 0 | CO26025 | BDL26003 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26026 | 08 | 32 | 1" | CO | 26026 | 1IS5 | N | 0 | CO26025 | BDL26003 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26030 | 08 | 32 | 1" | CO | 26030 | 1IS5 | N | 0 | CO26037 | CO26032 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
LC13001 |  | 32 | 1/2" | LC | 13001 | B-5 | HB | 30 | LS13004 | LC13004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14003 |  | 32 | 1/2" | LC | 14003 | B-5 | HB | 30 | LS63005 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23019 |  | 32 | 3/4" | LC | 23019 | B-5 | HB | 30 | LC23020 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
N89013 | 08 | 32 | 3/4" | N | 89013 | B-1 | N | 0 | N89034 | 32-D-8107 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89035 | 08 | 32 | 1/2" | N | 89035 | B-1 | N | 0 | N89034 | LN89007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89070 | 08 | 32 | 3/4" | N | 89070 | B-1 | N | 0 | N89044 | IW89041 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N14020 | 08 | 32 | 3" | N | 14020 | 1CS2 | N | 0 | N14021 | VA14012 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14021 | 08 | 32 | 3/4" | N | 14021 | 1CS2 | N | 0 | N67034 | N14022 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14022 | 08 | 32 | 3/4" | N | 14022 | 1CS2 | N | 0 | N14021 | CATALYST DRUM | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14023 | 08 | 32 | 2" | N | 14023 | 1CS2 | N | 0 | N14024 | VA14002 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14024 | 08 | 32 | 1/2" | N | 14024 | 1CS2 | N | 0 | N67039 | N14025 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14024 | 08 | 32 | 1" | N | 14024 | 1CS2 | N | 0 | N67039 | N14025 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14025 | 08 | 32 | 3/4" | N | 14025 | 1CS2 | N | 0 | N14024 | 32-Z-1402 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14026 | 08 | 32 | 3/4" | N | 14026 | 1CS2 | N | 0 | CT14005 | VA14003 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N15002 |  | 32 | 1/2" | N | 15002 | B-1 | ET | 30 | O15011 | N15001 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.9 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N15005 | 08 | 32 | 1/2" | N | 15005 | B-1 | N | 0 | N67035 | N15001 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.9 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N16010 | 08 | 32 | 1-1/2" | N | 16010 | 1CS2 | N | 0 | 32-D-1600 | N16011 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N16011 | 08 | 32 | 1/2" | N | 16011 | 1CS2 | N | 0 | N16010 | 32-D-1602 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N16011 | 08 | 32 | 1-1/2" | N | 16011 | 1CS2 | N | 0 | N16010 | 32-D-1602 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N20001 | 08 | 32 | 1" | N | 20001 | B-1 | N | 0 | NITROGEN CONNECTION | TEA20003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-040-01 |  | E | N | 000 | N | 140
N23003 | 08 | 32 | 1" | N | 23003 | B-1 | N | 0 | N | P23018 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.17 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 140
N23004 | 08 | 32 | 1" | N | 23004 | B-1 | N | 0 | N | P23019 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.17 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 140
LS50048 |  | 32 | 2" | LS | 50048 | B-5 | HB | 40 | LS63052 | 32-D-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS51003 |  | 32 | 1/2" | LS | 51003 | B-5 | HB | 60 | 32-D-5101 | LC51007 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
VA00033 | 08 | 32 | 4" | VA | 00033 | B-1 | N | 0 | 2121-ACW-SM-116 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00037 | 08 | 32 | 4" | VA | 00037 | B-1 | N | 0 | 2121-ACW-SM-123 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00038 | 08 | 32 | 4" | VA | 00038 | B-1 | N | 0 | 4123-ACW-SM-058 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00039 | 08 | 32 | 4" | VA | 00039 | B-1 | N | 0 | 2131-ACW-SM-059 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00042 | 08 | 32 | 4" | VA | 00042 | B-1 | N | 0 | 2131-ACW-SM-061 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00044 | 08 | 32 | 4" | VA | 00044 | B-1 | N | 0 | 2131-ACW-SM-069 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00047 | 08 | 32 | 4" | VA | 00047 | B-1 | N | 0 | 2131-ACW-SM-124 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00049 | 08 | 32 | 4" | VA | 00049 | B-1 | N | 0 | 2211-ACW-SM-106 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00051 | 08 | 32 | 4" | VA | 00051 | B-1 | N | 0 | 2211-ACW-SM-112 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00052 | 08 | 32 | 4" | VA | 00052 | B-1 | N | 0 | 2211-ACW-SM-113 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00056 | 08 | 32 | 4" | VA | 00056 | B-1 | N | 0 | 3221-ACW-SM-098 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00060 | 08 | 32 | 4" | VA | 00060 | B-1 | N | 0 | 3221-ACW-SM-120 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00061 | 08 | 32 | 4" | VA | 00061 | B-1 | N | 0 | 4111-ACW-SM-010 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00065 | 08 | 32 | 4" | VA | 00065 | B-1 | N | 0 | 4111-SW-SM-810 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00066 | 08 | 32 | 4" | VA | 00066 | B-1 | N | 0 | 4111-SW-SM-810 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00068 | 08 | 32 | 4" | VA | 00068 | B-1 | N | 0 | 4121-ACW-SM-012 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
FW68L16 | 08 | 32 | 2" | FW | 68L16 | B-13 | N | 0 | MSN-001 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L16 | 08 | 32 | 4" | FW | 68L16 | B-13 | N | 0 | MSN-001 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L27 | 08 | 32 | 1-1/2" | FW | 68L27 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68M09 | 08 | 32 | 1" | FW | 68M09 | B-13 | N | 0 | FW68M08 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M47 | 08 | 32 | 1" | FW | 68M47 | B-13 | N | 0 | SWIVEL JOINT | FW68M08 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68N06 | 08 | 32 | 1" | FW | 68N06 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N08 | 08 | 32 | 3" | FW | 68N08 | B-13 | N | 0 | FW68N09 | FW68N41 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N42 | 08 | 32 | 1-1/2" | FW | 68N42 | B-13 | N | 0 | FW68N46 | FW68N44 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N51 | 08 | 32 | 1" | FW | 68N51 | B-13 | N | 0 | FW68N52 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N52 | 08 | 32 | 2" | FW | 68N52 | B-13 | N | 0 | FW68N47 | FW68N51 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N60 | 08 | 32 | 1-1/2" | FW | 68N60 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N60 | 08 | 32 | 2" | FW | 68N60 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N70 | 08 | 32 | 1" | FW | 68N70 | B-13 | N | 0 | FW68N51 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68O01 | 08 | 32 | 1" | FW | 68O01 | B-13 | N | 0 | FW68O04 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68P05 | 08 | 32 | 3" | FW | 68P05 | B-13 | N | 0 | FW68P04 | FW68P18 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P08 | 08 | 32 | 1/2" | FW | 68P08 | B-13 | N | 0 | FW68P06 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
BDL24051 | 08 | 32 | 3/4" | BDL | 24051 | B32S1 | N | 0 | 32-P-2400B | BDL24067 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24059 | 08 | 32 | 8" | BDL | 24059 | B32S1 | N | 0 | HCM24063 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24071 | 08 | 32 | 3/4" | BDL | 24071 | B32S1 | N | 0 | HCM24069 | BDL24074 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24072 | 08 | 32 | 1-1/2" | BDL | 24072 | B32S1 | N | 0 | BDL24001 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24076 | 08 | 32 | 3/4" | BDL | 24076 | B32S1 | N | 0 | HCM24064 | BDL24068 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24079 | 08 | 32 | 3" | BDL | 24079 | B32S1 | N | 0 | BDL23016 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24092 | 08 | 32 | 3/4" | BDL | 24092 | B32S1 | N | 0 | BDL24091 | BDL23055 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24095 | 08 | 32 | 3/4" | BDL | 24095 | B32S1 | N | 0 | BDL22020 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
PR43043 | 08 | 32 | 3" | PR | 43043 | C42S1 | N | 0 | PR43042 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43045 |  | 32 | 2" | PR | 43045 | C42S1 | ST | 30 | 32-E-4302 | PR43028 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43045 |  | 32 | 3" | PR | 43045 | C42S1 | ST | 30 | 32-E-4302 | PR43028 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43048 | 08 | 32 | 1/2" | PR | 43048 | C42S1 | N | 0 | 32-T-4300 | BDL43019 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43048 | 08 | 32 | 1" | PR | 43048 | C42S1 | N | 0 | 32-T-4300 | BDL43019 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43048 | 08 | 32 | 2" | PR | 43048 | C42S1 | N | 0 | 32-T-4300 | BDL43019 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR50013 |  | 32 | 1/2" | PR | 50013 | 1CS2 | ET | 30 | 32-D-5001 | PROPYLENE TO S-3400 DIFF. PRESS. TRANS. | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.02 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | 27 | N | 32-P-050-01 |  | G | N | 141 | N | 390 | ,10
PR50013 |  | 32 | 1" | PR | 50013 | 1CS2 | ET | 30 | 32-D-5001 | PROPYLENE TO S-3400 DIFF. PRESS. TRANS. | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.02 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | 27 | N | 32-P-050-01 |  | G | N | 141 | N | 390 | ,10
PR50013 |  | 32 | 1-1/2" | PR | 50013 | 1CS2 | ET | 30 | 32-D-5001 | PROPYLENE TO S-3400 DIFF. PRESS. TRANS. | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.02 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | 27 | N | 32-P-050-01 |  | G | N | 141 | N | 390 | ,10
PR53002 | 08 | 32 | 1/2" | PR | 53002 | B4S1 | N | 0 | TP-009, PR530130 | BDL53002 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39A | 1 | Art 4.3 | NA | N | 1 | N | 32-P-050-05 |  | C | N | 141 | N | 370 | 10
PR61003 | 08 | 32 | 1" | PR | 61003 | C42S1 | N | 0 | TP-005 (32-D-6109) | TP-017 (32-PSV-6169) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42C | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61003 | 08 | 32 | 6" | PR | 61003 | C42S1 | N | 0 | TP-005 (32-D-6109) | TP-017 (32-PSV-6169) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42C | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
CHWS14001 |  | 32 | 3/4" | CHWS | 14001 | B-1 | CF | 25 | 32-P-1401 | JLS14001 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
HN72002 | 08 | 32 | 1" | HN | 72002 | C6S1 | N | 0 | 172C0-06 | PR72015 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.53 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-03 |  | E | N | 000 | N | 170
HN72002 | 08 | 32 | 1-1/2" | HN | 72002 | C6S1 | N | 0 | 172C0-06 | PR72015 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.53 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-03 |  | E | N | 000 | N | 170
HN72008 | 08 | 32 | 1-1/2" | HN | 72008 | C6S1 | N | 0 | PR720105 | SP-04-172B1-10 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
VZ13005 |  | 32 | 1-1/2" | VZ | 13005 | B4S2 | HH | 30 | 32-D-1301 | 32-D-1301 | 0.5 | 180.0 | 0.05/0.05 | 70.0/100.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 222 | 23,25
VZ13006 |  | 32 | 1" | VZ | 13006 | B4S2 | ST | 30 | 32-D-1300 | 32-D-1300 | 0.5 | 180.0 | 0.05 | 100.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 100 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-025-01 |  | E | N | 110 | N | 223 | 23,25
VZ13007 | 08 | 32 | 3/4" | VZ | 13007 | 1CS2 | EH | 30 | 32-S-1301 | VENT | 6.0 | 180.0 | 5.0/5.0 | 100.0/70.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 224 | 23,25
VZ13008 | 08 | 32 | 3/4" | VZ | 13008 | 1CS2 | ST | 30 | 32-S-1300 | VENT | 6.0 | 200.0 | 5.0/5.0 | 100.0/70.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 232 | 23,25
VZ13008 | 08 | 32 | 1" | VZ | 13008 | 1CS2 | ST | 30 | 32-S-1300 | VENT | 6.0 | 200.0 | 5.0/5.0 | 100.0/70.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 232 | 23,25
VZ14010 |  | 32 | 1/2" | VZ | 14010 | 1CS2 | CR | 25 | 32-D-1400A | 32-D-1400A | 12.0 | 190.0 | 7.0/0.01 | 5.0/60.0 |  | 18.98 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 5 | sh.7 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-01 |  | M | N | 232 | N | 287 | 6,23,25
VZ14010 |  | 32 | 3" | VZ | 14010 | 1CS2 | CR | 25 | 32-D-1400A | 32-D-1400A | 12.0 | 190.0 | 7.0/0.01 | 5.0/60.0 |  | 18.98 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 5 | sh.7 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-01 |  | M | N | 232 | N | 287 | 6,23,25
VZ14012 |  | 32 | 2" | VZ | 14012 | QXC25S1 | CF | 25 | 32-D-1401A | 32-D-1401A | 20.0 | 190.0 | 10.0 | 6.0 |  | 31.64 | 74.4 | H | VESSEL TRIM | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 231 | N | 279
VZ14014 | 08 | 32 | 1/2" | VZ | 14014 | 1CS2 | CR | 25 | 32-D-1400B | - | 12.0 | 190.0 | 7.0/0.01 | 5.0/60.0 |  | 18.98 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 5 | sh.8 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-02 |  | M | N | 232 | N | 287 | 6,23,25
VZ14015 | 08 | 32 | 1/2" | VZ | 14015 | QXC25S1 | CF | 25 | 32-S-1400B | 32-S-1400B | 20.0 | 190.0 | 10.0/0.01 | 10.0/10.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 10 | sh.8 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 231 | N | 280
VZ14017 | 08 | 32 | 1/2" | VZ | 14017 | QXC25S1 | CF | 25 | 32-S-1400A | 32-S-1400A | 20.0 | 190.0 | 10.0/0.01 | 10.0/10.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 10 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 231 | N | 280
CWR64014 | 08 | 32 | 1-1/2" | CWR | 64014 | B-1 | N | 0 | 32-E-6400A | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64014 | 08 | 32 | 20" | CWR | 64014 | B-1 | N | 0 | 32-E-6400A | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64016 | 08 | 32 | 3/4" | CWR | 64016 | B-1 | N | 0 | 32-E-6400C | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64016 | 08 | 32 | 14" | CWR | 64016 | B-1 | N | 0 | 32-E-6400C | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
LS50008 |  | 32 | 3/4" | LS | 50008 | 3CS6 | HB | 50 | LS50002 | 32-J-5001 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50030 |  | 32 | 1/2" | LS | 50030 | B-5 | HB | 30 | 32-D-5011 | 32-J-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50030 |  | 32 | 1" | LS | 50030 | B-5 | HB | 30 | 32-D-5011 | 32-J-5001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50035 |  | 32 | 1" | LS | 50035 | B-5 | HB | 30 | JLS50006 | LS50034 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50045 |  | 32 | 1" | LS | 50045 | B-5 | HB | 30 | 32-D-5001 | LC50004 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS51004 |  | 32 | 3/4" | LS | 51004 | B-5 | HB | 60 | 32-D-5104 | LC51006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-U-060-01 |  | E | N | 000 | N | 90
LS60012 |  | 32 | 1" | LS | 60012 | B-5 | HB | 70 | PURGE CONNECTION | BDL60041 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78A | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS63005 |  | 32 | 3/4" | LS | 63005 | B-5 | HB | 60 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63005 |  | 32 | 1" | LS | 63005 | B-5 | HB | 70 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63030 |  | 32 | 1" | LS | 63030 | B-5 | HB | 70 | LS63014 | 32-E-3400 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63046 |  | 32 | 3/4" | LS | 63046 | B-5 | HB | 60 | LS63206 | 32-D-6011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63046 |  | 32 | 1-1/2" | LS | 63046 | B-5 | HB | 70 | LS63206 | 32-D-6011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63052 |  | 32 | 3/4" | LS | 63052 | B-5 | HB | 60 | LS63199 | LS50048 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
BDL43018 | 08 | 32 | 3" | BDL | 43018 | B32S1 | N | 0 | PR43049 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CWS01010 | 08 | 32 | 20" | CWS | 01010 | UGB-1PE | N | 0 | CWS01009 | CWS64001 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS80001 | 08 | 32 | 3/4" | CWS | 80001 | B-1 | N | 0 | CWS64005 | 32-E-8001 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
BDL72024 | 08 | 32 | 1/2" | BDL | 72024 | B32S1 | N | 0 | PR72018 | BDL72025 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
CHWR15006 | 08 | 32 | 1-1/2" | CHWR | 15006 | B-1 | N | 0 | HEADER | HEADER | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR20003 |  | 32 | 3/4" | CHWR | 20003 | B-1 | CF | 25 | 32-Z-2004 | CHWR43011 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR65001 |  | 32 | 1-1/2" | CHWR | 65001 | B-1 | CF | 25 | 32-D-6500 | CHWR65003 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
SWW92001 | 08 | 32 | 4" | SWW | 92001 | 1CS2 | N | 0 | 32-D-9005 | 32-P-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92002 | 08 | 32 | 3/4" | SWW | 92002 | 1CS2 | N | 0 | DRAIN | BLIND FLANGE | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92002 | 08 | 32 | 2" | SWW | 92002 | 1CS2 | N | 0 | DRAIN | BLIND FLANGE | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92004 | 08 | 32 | 8" | SWW | 92004 | 1CS2 | N | 0 | SWW92016 | 32-S-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92005 | 08 | 32 | 3/4" | SWW | 92005 | 1CS2 | N | 0 | 32-P-9005 | HEADER | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92005 | 08 | 32 | 2" | SWW | 92005 | 1CS2 | N | 0 | 32-P-9005 | HEADER | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92011 | 08 | 32 | 1-1/2" | SWW | 92011 | 1CS2 | N | 0 | SWW92005 | 32-H-9001A | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92012 | 08 | 32 | 3" | SWW | 92012 | 1CS2 | N | 0 | SWW92026 | 32-H-9001B | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92013 | 08 | 32 | 3" | SWW | 92013 | 1CS2 | N | 0 | SWW92027 | 32-H-9001C | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92014 | 08 | 32 | 3" | SWW | 92014 | 1CS2 | N | 0 | SWW92005 | 32-H-9001D | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
ET40007 | 08 | 32 | 4" | ET | 40007 | C3S1 | N | 0 | ET71039 | BDL40046 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71042 | 7A | 32 | 3/4" | ET | 71042 | C3S1 | HA | 60 | ET71079 | 32-T-7110B | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71042 | 7A | 32 | 4" | ET | 71042 | C3S1 | HA | 70 | ET71079 | 32-T-7110B | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71051 | 08 | 32 | 4" | ET | 71051 | C3S1 | N | 0 | 32-E-7102 | 32-S-7100A | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.48 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-02 |  | C | N | 041 | N | 323 | ,10
ET71061 | 08 | 32 | 1" | ET | 71061 | C3S1 | N | 0 | 32-S-7100B | BDL71034 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
LC23037 |  | 32 | 1/2" | LC | 23037 | B-5 | HB | 30 | LS23032 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23043 |  | 32 | 1/2" | LC | 23043 | B-5 | HB | 30 | LS23028 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23055 | 08 | 32 | 3/4" | LC | 23055 | B-5 | P | 50 | LS23037 | LC31017 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31003 |  | 32 | 1/2" | LC | 31003 | B-5 | HB | 30 | LS31025 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31011 |  | 32 | 1/2" | LC | 31011 | B-5 | HB | 30 | LC31010 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31011 |  | 32 | 3/4" | LC | 31011 | B-5 | HB | 30 | LC31010 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC5001A |  | 32 | 3/4" | LC | 5001A | B-5 | HB | 30 | LS630AE | LC50001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC61003 |  | 32 | 3/4" | LC | 61003 | B-5 | HB | 30 | LS61002 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC6300R |  | 32 | 3/4" | LC | 6300R | B-5 | HB | 30 | 32-1127-S-008 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63033 |  | 32 | 3/4" | LC | 63033 | B-5 | P | 50 | 32-P-6300A | LC63034 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63033 |  | 32 | 3" | LC | 63033 | B-5 | P | 50 | 32-P-6300A | LC63034 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
O13007 | 7A | 32 | 3/4" | O | 13007 | 1CS2 | P | 50 | 32-S-1301 | 32-D-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13007 | 7A | 32 | 1-1/2" | O | 13007 | 1CS2 | P | 50 | 32-S-1301 | 32-D-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13027 | 08 | 32 | 1-1/2" | O | 13027 | 1CS2 | N | 0 | 32-D-1300 | O13003 | 6.0 | 200.0 | 5.0 | 100.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 100 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-025-01 |  | A | N | 010 | N | 231 | 23,25
O13036 |  | 32 | 1-1/2" | O | 13036 | B4S2 | ET | 30 | VZ13005 | O13037 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O14011 |  | 32 | 3/4" | O | 14011 | 1CS2 | ET | 30 | O15004 | 32-Z-1400B | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-02 |  | M | N | 110 | N | 236 | 23,25
O15011 |  | 32 | 1" | O | 15011 | 1CS2 | ET | 30 | O15013 | N15002 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 110 | N | 236 | 23,25
PG61002 | 08 | 32 | 1" | PG | 61002 | 1CS2 | N | 0 | PROPYLENE GLYCOL DRUM | 32-P-6101 | 10.0 | 60.0 | 5.0 | 20.0 |  | 15 | 28.5 | H | PROPYLENE GLYCOL | L | - | - | <1.5 | 20 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-023-01 |  | M | N | 010 | N | 80
PN52020 | 7A | 32 | 1" | PN | 52020 | 1CS2 | HB | 30 | 32-T-5200 | ACW | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52023 | 7A | 32 | 3/4" | PN | 52023 | 1CS2 | HB | 30 | PN52028 | PN52026 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52028 | 7A | 32 | 1/2" | PN | 52028 | 1CS2 | HB | 30 | 32-Z-5202B | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52028 | 7A | 32 | 3/4" | PN | 52028 | 1CS2 | HB | 30 | 32-Z-5202B | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52028 | 7A | 32 | 20" | PN | 52028 | 1CS2 | HB | 40 | 32-Z-5202B | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PP81006 | 08 | 32 | 8" | PP | 81006 | 5CS7 | N | 0 | 32-V-8107 | PP81003 | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.62 | 1 | II | MOD.A2 | Y | NR | N | 32-P-070-01 |  | M | N | 110 | N | 439 | 6,23,25
PR21011 | 7A | 32 | 4" | PR | 21011 | 1FS4 | HB | 30 | PR21010 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.12 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-045-01 |  | G | N | 141 | N | 337 | 10
N32014 | 08 | 32 | 1" | N | 32014 | B4S1 | N | 0 | TP-30B, (CYLINDER 1) | TO TEMPORARY TANK | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.52B | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N36007 | 08 | 32 | 1-1/2" | N | 36007 | B4S1 | N | 0 | TP-166 (CYLINDER 1, STAGE 1, PACKING 1, C58) | N36006 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N40002 | 08 | 32 | 1" | N | 40002 | B-1 | N | 0 | NITROGEN CONNECTION | P40042 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-049-01 |  | E | N | 000 | N | 140
N52035 | 08 | 32 | 1/2" | N | 52035 | 1CS2 | N | 0 | N52025 | N52030 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N60001 | 08 | 32 | 1/2" | N | 60001 | B-1 | N | 0 | N67050 | BDL60060 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
CWR80001 | 08 | 32 | 2" | CWR | 80001 | B-1 | N | 0 | 32-E-8000 | CWR64011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86001 |  | 32 | 1/2" | CWR | 86001 | B-1 | HB | 30 | PX86030 | CWR86011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86001 |  | 32 | 1" | CWR | 86001 | B-1 | HB | 30 | PX86030 | CWR86011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
LO71003 | 08 | 32 | 3/4" | LO | 71003 | QXB-55 | N | 0 | TP-11 (LO-710109) | TO PORTABLE POT | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.50C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-006-05 |  | M | N | 110 | N | 800
LPN01001 | 08 | 32 | 1/2" | LPN | 01001 | 1C13 | N | 0 | N01008 | SP-0105 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN01001 | 08 | 32 | 4" | LPN | 01001 | 1C13 | N | 0 | N01008 | SP-0105 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN02001 | 08 | 32 | 1" | LPN | 02001 | 1C13 | N | 0 | LPN01001 | LPN10016 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
CWR01010 | 08 | 32 | 3" | CWR | 01010 | UGB-1PE | N | 0 | CWR00C01 | 48"-CW-200002-B1 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
CWR01010 | 08 | 32 | 40" | CWR | 01010 | UGB-1PE | N | 0 | CWR00C01 | 48"-CW-200002-B1 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
CWR01010 | 08 | 32 | 48" | CWR | 01010 | UGB-1PE | N | 0 | CWR00C01 | 48"-CW-200002-B1 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
O66023 |  | 32 | 3/4" | O | 66023 | 1CS2 | ET | 30 | O66015 | O66003 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66023 |  | 32 | 1-1/2" | O | 66023 | 1CS2 | ET | 30 | O66015 | O66003 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
OG01004 | 7A | 32 | 3/4" | OG | 01004 | 1FS4 | P | 50 | OG00A01 | PPG80001 | 42.0/42.0 | -40.0/200.0 | 3.0/3.0 | 60.0/10.0 |  | 67.34 | 148.95 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-U-034-01 |  | G | N | 141 | N | 503 | 10
OG01004 | 7A | 32 | 2" | OG | 01004 | 1FS4 | P | 50 | OG00A01 | PPG80001 | 42.0/42.0 | -40.0/200.0 | 3.0/3.0 | 60.0/10.0 |  | 67.34 | 148.95 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.1 | 1 | II | MOD.A2 | Y | 5 | Y | 32-U-034-01 |  | G | N | 141 | N | 503 | 10
OG01004 | 7A | 32 | 4" | OG | 01004 | 1FS4 | P | 50 | OG00A01 | PPG80001 | 42.0/42.0 | -40.0/200.0 | 3.0/3.0 | 60.0/10.0 |  | 67.34 | 148.95 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.1 | 1 | II | MOD.A2 | Y | 5 | Y | 32-U-034-01 |  | G | N | 141 | N | 503 | 10
OG53001 | 08 | 32 | 3" | OG | 53001 | B4S1 | N | 0 | PR53004 | 32-S-3400 | 7.0 | 165.0 | 5.0 | 10.0 |  | 10.52 | 29.4 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 526 | 10
P23019 | 7A | 32 | 1/2" | P | 23019 | 1FS4 | HB | 30 | 32-Z-2300B | P23015 | 42.0/42.0 | -40.0/200.0 | 30.0 | 100.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.17 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 141 | N | 521 | 10
P23031 | 08 | 32 | 3" | P | 23031 | C42S2 | HB | 30 | 32-R-2300 | BDL23067 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P31008 | 08 | 32 | 4" | P | 31008 | C42S2 | N | 0 | P23017 | 32-S-3100 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P31012 |  | 32 | 4" | P | 31012 | C42S2 | P | 50 | 32-S-3100 | P31007 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P34004 |  | 32 | 12" | P | 34004 | 1CR9 | P | 100 | 32-S-3400 | VZ50008 | 5.0/5.0 | 200.0/-45.0 | 0.6 | 80.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.26 | 1 | II | MOD.A2 | Y | NR | N | 32-P-048-01 |  | F-4 | N | 141 | N | 430 | 16,10,18,13
P40033 |  | 32 | 1" | P | 40033 | C42S2 | ET | 30 | N40009 | P40032 | 20.0/20.0 | 120.0/-40.0 | 14.0/14.0 | 110.0/80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 426 | 10,11,13,39
P40041 |  | 32 | 4" | P | 40041 | C42S2 | ET | 30 | 32-R-4001 | Z-4003 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
CWS01009 | 08 | 32 | 3" | CWS | 01009 | UGB-1PE | N | 0 | CW200001 OSBL LINE | CWS01012 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS01009 | 08 | 32 | 48" | CWS | 01009 | UGB-1PE | N | 0 | CW200001 OSBL LINE | CWS01012 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS64009 | 08 | 32 | 3/4" | CWS | 64009 | B-1 | N | 0 | CWS64006 | 32-E-8005 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS80001 | 08 | 32 | 2" | CWS | 80001 | B-1 | N | 0 | CWS64005 | 32-E-8001 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS80001 | 08 | 32 | 4" | CWS | 80001 | B-1 | N | 0 | CWS64005 | 32-E-8001 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86017 | 08 | 32 | 3/4" | CWS | 86017 | B-1 | N | 0 | CWS89042 | CWS86019 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS86018 | 08 | 32 | 1/2" | CWS | 86018 | B-1 | N | 0 | CWS86019 | JCW86018 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89042 | 08 | 32 | 1/2" | CWS | 89042 | B-1 | N | 0 | CWS64010 | CWS86016 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
DO12004 | 08 | 32 | 1-1/2" | DO | 12004 | 1CS2 | N | 0 | 32-S-1201 | 32-D-1200B | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
LS01001 |  | 32 | 1" | LS | 01001 | B-5 | HB | 70 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS01001 |  | 32 | 2" | LS | 01001 | B-5 | HB | 80 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS01001 |  | 32 | 4" | LS | 01001 | B-5 | HB | 90 | LS500002 OSBL LINE | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63054 |  | 32 | 1/2" | LS | 63054 | B-5 | HB | 60 | LS63178 | 32-S-1300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63064 |  | 32 | 3/4" | LS | 63064 | B-5 | HB | 60 | LS63206 | 32-D-6500 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63064 |  | 32 | 1-1/2" | LS | 63064 | B-5 | HB | 70 | LS63206 | 32-D-6500 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63084 |  | 32 | 1" | LS | 63084 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
CWR89026 | 08 | 32 | 4" | CWR | 89026 | B-1 | N | 0 | CWR89037 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93002 | 08 | 32 | 1-1/2" | CWR | 93002 | B-1 | N | 0 | 32-E-9001A | CWR93005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93002 | 08 | 32 | 4" | CWR | 93002 | B-1 | N | 0 | 32-E-9001A | CWR93005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
VA88001 | 08 | 32 | 1" | VA | 88001 | B4S2 | N | 0 | CWR88003 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.67 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
VA93001 | 08 | 32 | 1" | VA | 93001 | B4S2 | N | 0 | CWR93005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.73 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
LS630AN |  | 32 | 1" | LS | 630AN | B-5 | HB | 70 | LS63201 | JLS23010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AV |  | 32 | 1-1/2" | LS | 630AV | B-5 | HB | 70 | LS63193 | PR31023 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63136 |  | 32 | 1" | LS | 63136 | B-5 | HB | 70 | LS63201 | 32-S-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63202 |  | 32 | 2" | LS | 63202 | B-5 | HB | 80 | LS01001 | LS89051 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS66002 |  | 32 | 1-1/2" | LS | 66002 | B-5 | HB | 70 | LS02001 | LS66003 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.46 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS71010 |  | 32 | 1" | LS | 71010 | C6S1 | HB | 50 | LS63059 | 32-E-7101 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS72002 |  | 32 | 3/4" | LS | 72002 | D1S1 | HB | 50 | LS72129 | 32-E-7201 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.51 | 1 | III | MOD.G | Y | 20 | N | 32-U-052-01 |  | E | N | 041 | N | 1090
LS72002 |  | 32 | 1" | LS | 72002 | D1S1 | HB | 50 | LS72129 | 32-E-7201 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.51 | 1 | III | MOD.G | Y | 20 | N | 32-U-052-01 |  | E | N | 041 | N | 1090
LS72003 |  | 32 | 1/2" | LS | 72003 | B-5 | HB | 60 | LS72004 | LC72002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.51 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS72003 |  | 32 | 1-1/2" | LS | 72003 | B-5 | HB | 70 | LS72004 | LC72002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.51 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N01001 | 08 | 32 | 3/4" | N | 01001 | B-1 | N | 0 | NT400003 OSBL LINE | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N01001 | 08 | 32 | 4" | N | 01001 | B-1 | N | 0 | NT400003 OSBL LINE | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N01007 | 08 | 32 | 1" | N | 01007 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | OG01004 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-034-01 |  | E | N | 000 | N | 140
N12022 | 08 | 32 | 1/2" | N | 12022 | 1CS2 | N | 0 | N12020 | 32-LT-1204 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12022 | 08 | 32 | 3/4" | N | 12022 | 1CS2 | N | 0 | N12020 | 32-LT-1204 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12026 | 08 | 32 | 3/4" | N | 12026 | 1CS2 | N | 0 | N12030 | 32-LT-1206 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N13003 |  | 32 | 3/4" | N | 13003 | B-1 | ET | 30 | 32-D-1301 | N13002 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N13003 |  | 32 | 2" | N | 13003 | B-1 | ET | 30 | 32-D-1301 | N13002 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N14001 | 08 | 32 | 3/4" | N | 14001 | 1CS2 | N | 0 | N67038 | N14002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14006 | 08 | 32 | 1/2" | N | 14006 | 1CS2 | N | 0 | N67033 | N14007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14006 | 08 | 32 | 1-1/2" | N | 14006 | 1CS2 | N | 0 | N67033 | N14007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
ET71052 | 08 | 32 | 4" | ET | 71052 | C3S1 | N | 0 | ET01001 | ET71051 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.48 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-006-02 |  | C | N | 041 | N | 323 | ,10
PR21014 |  | 32 | 1/2" | PR | 21014 | 1FS4 | CF | 25 | PR21017 | TP-12 (Z-2101) | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | Art 4.3 | NA | N | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR22012 | 08 | 32 | 3/4" | PR | 22012 | D20S1 | N | 0 | PR33019 | 32-E-2100 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22012 | 08 | 32 | 3" | PR | 22012 | D20S1 | N | 0 | PR33019 | 32-E-2100 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22012 | 08 | 32 | 4" | PR | 22012 | D20S1 | N | 0 | PR33019 | 32-E-2100 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR24047 |  | 32 | 1/2" | PR | 24047 | D20S1 | HB | 30 | PR24046 | HCM23081 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24047 |  | 32 | 1-1/2" | PR | 24047 | D20S1 | HB | 30 | PR24046 | HCM23081 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR31014 | 7A | 32 | 1-1/2" | PR | 31014 | 1FS4 | HB | 30 | PR31015 | PR34021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31014 | 08 | 32 | 1-1/2" | PR | 31014 | 1FS4 | N | 0 | PR31015 | PR34021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR33017 | 08 | 32 | 10" | PR | 33017 | C42S1 | N | 0 | 32-D-3300 | PR33018 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR34002 |  | 32 | 6" | PR | 34002 | B4S1 | P | 50 | 32-S-3400 | BDL34018 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34026 |  | 32 | 3/4" | PR | 34026 | B4S1 | P | 50 | 32-S-3401A | BDL34016 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34026 |  | 32 | 1-1/2" | PR | 34026 | B4S1 | P | 50 | 32-S-3401A | BDL34016 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR35011 | 08 | 32 | 3/4" | PR | 35011 | B4S1 | N | 0 | 32-D-3500 | PR36016 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35011 | 08 | 32 | 12" | PR | 35011 | B4S1 | N | 0 | 32-D-3500 | PR36016 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
FO10001 | 08 | 32 | 1/2" | FO | 10001 | 3DS3 | N | 0 | TEA10002 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.4 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11003 | 08 | 32 | 1/2" | FO | 11003 | 1CS2 | N | 0 | O66039 | FO11021 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11003 |  | 32 | 1" | FO | 11003 | 1CS2 | ET | 30 | O66039 | FO11021 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
N14023 | 08 | 32 | 1" | N | 14023 | 1CS2 | N | 0 | N14024 | VA14002 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14023 | 08 | 32 | 3" | N | 14023 | 1CS2 | N | 0 | N14024 | VA14002 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14024 | 08 | 32 | 3/4" | N | 14024 | 1CS2 | N | 0 | N67039 | N14025 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N15001 | 08 | 32 | 1-1/2" | N | 15001 | B-1 | N | 0 | HEADER | 32-D-1602 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.9 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N20001 | 08 | 32 | 1/2" | N | 20001 | B-1 | N | 0 | NITROGEN CONNECTION | TEA20003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-040-01 |  | E | N | 000 | N | 140
N21002 | 08 | 32 | 1" | N | 21002 | B-1 | N | 0 | NITROGEN CONNECTION | PR22013 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.12 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N23002 | 08 | 32 | 1" | N | 23002 | B-1 | N | 0 | NITROGEN CONNECTION | HCM23045 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 140
N32009 | 08 | 32 | 1/2" | N | 32009 | B4S1 | N | 0 | TP-41A, (N32009) | N32010 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N67004 | 08 | 32 | 3/4" | N | 67004 | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N6700K | 08 | 32 | 1" | N | 6700K | B-1 | N | 0 | N89098 | TP-N11203 (32-H-8901, PCV-8906) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N6700O | 08 | 32 | 1/2" | N | 6700O | B-1 | N | 0 | N67046 | FLANGE | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67013 | 08 | 32 | 1" | N | 67013 | B-1 | N | 0 | N01001 | N67070 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67016 | 08 | 32 | 3/4" | N | 67016 | B-1 | N | 0 | N67041 | N61004 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67026 | 08 | 32 | 3/4" | N | 67026 | B-1 | N | 0 | N67028 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67029 | 08 | 32 | 2" | N | 67029 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67029 | 08 | 32 | 4" | N | 67029 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67031 | 08 | 32 | 1" | N | 67031 | B-1 | N | 0 | N67005 | 32-D-1301 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
CWR88001 | 08 | 32 | 3/4" | CWR | 88001 | B-1 | N | 0 | 32-E-8005 | CWR88003 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.67 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR88001 | 08 | 32 | 2" | CWR | 88001 | B-1 | N | 0 | 32-E-8005 | CWR88003 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.67 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89010 | 08 | 32 | 20" | CWR | 89010 | B-1 | N | 0 | CWR89009 | IA40001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR91001 | 08 | 32 | 1/2" | CWR | 91001 | B-1 | N | 0 | 32-E-9004 | CWR64001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR91001 | 08 | 32 | 3/4" | CWR | 91001 | B-1 | N | 0 | 32-E-9004 | CWR64001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR91001 | 08 | 32 | 4" | CWR | 91001 | B-1 | N | 0 | 32-E-9004 | CWR64001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93001 | 08 | 32 | 1-1/2" | CWR | 93001 | B-1 | N | 0 | 32-E-9001B | CWR93006 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93001 | 08 | 32 | 4" | CWR | 93001 | B-1 | N | 0 | 32-E-9001B | CWR93006 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CT14003 |  | 32 | 1" | CT | 14003 | QXC25S1 | CF | 25 | 32-D-1400B | 32-D-1401B | 20.0 | 190.0 | 10.0/0.03 | 6.0/70.0 |  | 31.64 | 74.4 | H | DRY CATALYST | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-03 |  | M | N | 231 | N | 284
CT14003 |  | 32 | 2" | CT | 14003 | QXC25S1 | CF | 25 | 32-D-1400B | 32-D-1401B | 20.0 | 190.0 | 10.0/0.03 | 6.0/70.0 |  | 31.64 | 74.4 | H | DRY CATALYST | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-03 |  | M | N | 231 | N | 284
CT15002 | 08 | 32 | 3/8" | CT | 15002 | 3FS3 | N | 0 | CT15022 | CT15001 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-04 |  | M | N | 232 | N | 286 | 23,29,25
CWR64012 | 08 | 32 | 3" | CWR | 64012 | UGB-1PE | N | 0 | CWR64013 | CWR01010 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
CWR64012 | 08 | 32 | 20" | CWR | 64012 | UGB-1PE | N | 0 | CWR64013 | CWR01010 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 16
CWR64013 | 08 | 32 | 3/4" | CWR | 64013 | B-1 | N | 0 | 32-E-6400B | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64013 | 08 | 32 | 14" | CWR | 64013 | B-1 | N | 0 | 32-E-6400B | CWR64012 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 13
CWR64015 | 08 | 32 | 3" | CWR | 64015 | UGB-1PE | N | 0 | CWR64001 | CWR01010 | 7.5 | 80.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-03 |  | E | N | 000 | N | 16
CWR80005 | 08 | 32 | 3/4" | CWR | 80005 | B-1 | N | 0 | CWR80002 | VA80010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86016 | 08 | 32 | 1/2" | CWR | 86016 | B-1 | N | 0 | 32-D-8600 | CWR86021 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89008 | 08 | 32 | 1/2" | CWR | 89008 | B-1 | N | 0 | PX86018 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
O15012 |  | 32 | 3/4" | O | 15012 | B4S2 | ET | 30 | 32-D-1501 | 32-S-1500 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15016 |  | 32 | 1/2" | O | 15016 | B4S2 | ET | 30 | O15015 | 32-D-1401B | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15022 |  | 32 | 1" | O | 15022 | 1FS4 | ET | 30 | O15021 | O15023 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O31012 | 08 | 32 | 1-1/2" | O | 31012 | B4S2 | N | 0 | VZ31006 | O31011 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
P50013 |  | 32 | 12" | P | 50013 | 1CR9 | JP | 0 | 32-D-5011 | PR50010 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-02 |  | F-4 | N | 141 | N | 436 | ,16,10,18,13
P50015 |  | 32 | 1-1/2" | P | 50015 | 1CR9 | HB | 30 | 32-D-5001 | LC50007 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P50015 |  | 32 | 2" | P | 50015 | 1CR9 | HB | 40 | 32-D-5001 | LC50007 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P52010 |  | 32 | 6" | P | 52010 | 1CR9 | P | 50 | 32-A-5200 | 32-D-5200 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.37 | 1 | III | MOD.G | Y | NR | N | 32-P-052-02 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
PA01001 | 08 | 32 | 1-1/2" | PA | 01001 | B-1 | N | 0 | PA300003 OSBL LINE | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA01001 | 08 | 32 | 2" | PA | 01001 | B-1 | N | 0 | PA300003 OSBL LINE | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA02008 | 08 | 32 | 3/4" | PA | 02008 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62001 | 08 | 32 | 1" | PA | 62001 | B-1 | N | 0 | PA62053 | PA14001 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62055 | 08 | 32 | 3/4" | PA | 62055 | B-1 | N | 0 | PA62072 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89055 | 08 | 32 | 3/4" | PA | 89055 | B-1 | N | 0 | PA01001 | 32-US-7112-01 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
CWS89042 | 08 | 32 | 1" | CWS | 89042 | B-1 | N | 0 | CWS64010 | CWS86016 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
LS13005 |  | 32 | 1/2" | LS | 13005 | B-5 | HB | 60 | 32-D-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13005 |  | 32 | 3/4" | LS | 13005 | B-5 | HB | 60 | 32-D-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13006 |  | 32 | 1/2" | LS | 13006 | B-5 | HB | 60 | JLS13001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13009 |  | 32 | 1/2" | LS | 13009 | B-5 | HB | 60 | 32-E-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13009 |  | 32 | 1" | LS | 13009 | B-5 | HB | 70 | 32-E-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS21001 |  | 32 | 1" | LS | 21001 | B-5 | HB | 70 | JLS21002 | LC21001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.12 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23018 |  | 32 | 3/4" | LS | 23018 | B-5 | HB | 60 | 32-E-2301 | LC23017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.18 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23018 |  | 32 | 1-1/2" | LS | 23018 | B-5 | HB | 70 | 32-E-2301 | LC23017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.18 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23031 |  | 32 | 1/2" | LS | 23031 | B-5 | HB | 60 | JLS23017 | LC23038 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31028 |  | 32 | 1/2" | LS | 31028 | B-5 | HB | 60 | JLS31012 | LC31021 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31033 |  | 32 | 1" | LS | 31033 | B-5 | HB | 70 | JLS31009 | LC31038 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31035 | 08 | 32 | 1/2" | LS | 31035 | B-5 | HB | 60 | PR31014 | LC31041 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS32001 |  | 32 | 1" | LS | 32001 | B-5 | HB | 70 | JLS32002 | LC32001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.24 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50004 |  | 32 | 3/4" | LS | 50004 | 3CS6 | HB | 30 | LS50003 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50004 |  | 32 | 6" | LS | 50004 | 3CS6 | HB | 40 | LS50003 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
CWS64007 | 08 | 32 | 3/4" | CWS | 64007 | B-1 | N | 0 | CWS64006 | 32-E-9001A | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64008 | 08 | 32 | 4" | CWS | 64008 | B-1 | N | 0 | CWS64006 | 32-E-9001B | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89048 | 08 | 32 | 1/2" | CWS | 89048 | B-1 | N | 0 | CWS64010 | TP-N11217 (32-H-8901) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
VA21003 | 08 | 32 | 1" | VA | 21003 | B4S2 | N | 0 | CHWR21008 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.12 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA23003 | 08 | 32 | 2" | VA | 23003 | C42S1 | N | 0 | HCM23059 | 32-Z-2302 | 42.0 | 65.0 | 40.0 | 30.0 |  | 63 | 76.65 | H | VENT TO ATMOSPHERE | G | - | - | >1.5 | 30 | sh.16 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | G | N | 141 | N | 518 | 10
VA33004 | 08 | 32 | 1" | VA | 33004 | B-1 | N | 0 | 32-P-3300B | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.25 | 2 | NA | NA | NA | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 181
VA43011 | 08 | 32 | 1" | VA | 43011 | B4S2 | N | 0 | JWR43003 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.33 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA50006 | 08 | 32 | 3" | VA | 50006 | B4S2 | N | 0 | LS50048 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.34 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA52010 | 08 | 32 | 18" | VA | 52010 | B4S2 | N | 0 | PN52026 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA52014 | 08 | 32 | 3/4" | VA | 52014 | B4S2 | N | 0 | 32-Z-5202A | ACW | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA81018 | 08 | 32 | 4" | VA | 81018 | B-1 | N | 0 | 32-PSV-8104E | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.61 | 2 | NA | NA | NA | 1 | N | 32-P-061-02 |  | E | N | 000 | N | 181
VA81022 | 08 | 32 | 8" | VA | 81022 | B4S2 | N | 0 | 32-C-8122 | OUTDOOR TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.60 | 2 | NA | NA | NA | 6 | N | 32-P-061-02 |  | E | N | 000 | N | 183
DO12007 | 08 | 32 | 3/4" | DO | 12007 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12007 | 08 | 32 | 8" | DO | 12007 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12023 |  | 32 | 1/2" | DO | 12023 | 3FS3 | ET | 30 | DO12008 | 32-P-1200B | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12023 |  | 32 | 1" | DO | 12023 | 3FS3 | ET | 30 | DO12008 | 32-P-1200B | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12030 | 08 | 32 | 1-1/2" | DO | 12030 | 1CS2 | N | 0 | DO12004 | 32-D-1200C | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DW69B12 | 08 | 32 | 1-1/2" | DW | 69B12 | B-13 | N | 0 | DW69B05 | 32-ES-6918 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
LS89052 |  | 32 | 3/4" | LS | 89052 | B-5 | HB | 60 | PA01001 | PA89038 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | 7 | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89052 |  | 32 | 2" | LS | 89052 | B-5 | HB | 80 | PA01001 | PA89038 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89054 |  | 32 | 3/4" | LS | 89054 | B-5 | HB | 60 | LS89052 | PA89053 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | 7 | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89056 |  | 32 | 3/4" | LS | 89056 | B-5 | HB | 60 | LC91A70 | LS89035 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89059 |  | 32 | 3/4" | LS | 89059 | B-5 | HB | 60 | LS01001 | LC89049 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N14020 | 08 | 32 | 1" | N | 14020 | 1CS2 | N | 0 | N14021 | VA14012 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14020 | 08 | 32 | 2" | N | 14020 | 1CS2 | N | 0 | N14021 | VA14012 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
DMW64001 | 08 | 32 | 2" | DMW | 64001 | SXB-48 | N | 0 | DMW01001 | TP-N10501 (D-8905) | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DO12002 | 08 | 32 | 3/4" | DO | 12002 | 1CS2 | N | 0 | 32-P-1201 | DO12024 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12005 |  | 32 | 1/2" | DO | 12005 | 1CS2 | ET | 30 | 32-D-1200A | 32-S-1200A | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12005 |  | 32 | 1-1/2" | DO | 12005 | 1CS2 | ET | 30 | 32-D-1200A | 32-S-1200A | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12006 | 08 | 32 | 1" | DO | 12006 | 1CS2 | N | 0 | N12018 | DO12005 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12009 | 08 | 32 | 1/2" | DO | 12009 | 1CS2 | N | 0 | 32-S-1200A | N12018 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12011 | 08 | 32 | 1/2" | DO | 12011 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12011 | 08 | 32 | 2" | DO | 12011 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12020 | 08 | 32 | 1/2" | DO | 12020 | 1CS2 | N | 0 | DO12008 | DO12009 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12033 | 08 | 32 | 1" | DO | 12033 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12033 | 08 | 32 | 2" | DO | 12033 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12034 | 08 | 32 | 3/4" | DO | 12034 | 1CS2 | N | 0 | 32-S-1200C | N12030 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
ET71074 | 7A | 32 | 3" | ET | 71074 | C3S1 | HA | 70 | ET71042 | BDL71033 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71079 | 7A | 32 | 1" | ET | 71079 | C3S1 | HB | 60 | 32-E-7101 | ET71042 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71082 | 08 | 32 | 1/2" | ET | 71082 | C3S1 | N | 0 | ET71051 | BDL71028 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.48 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-006-02 |  | C | N | 041 | N | 323 | ,10
PR35013 |  | 32 | 6" | PR | 35013 | B4S1 | P | 50 | PR36012 | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR36021 | 08 | 32 | 1" | PR | 36021 | C42S1 | P | 50 | PR36036 | PR36028 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28A | 1 | Art 4.3 | NA | N | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36031 | 08 | 32 | 6" | PR | 36031 | B4S1 | N | 0 | TP-118,32-D-3605 | BDL36018 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
IA89040 | 08 | 32 | 1" | IA | 89040 | B-13 | N | 0 | IA89037 | 32-IAM-126 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89045 | 08 | 32 | 3/4" | IA | 89045 | B-13 | N | 0 | IA62006 | TP-N52804 (PCV-8970) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89047 | 08 | 32 | 3/4" | IA | 89047 | B-13 | N | 0 | IA62006 | TP-N50424 (D-8901) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89049 | 08 | 32 | 1/2" | IA | 89049 | B-13 | N | 0 | IA62006 | 32-PK-8300 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89051 | 08 | 32 | 1" | IA | 89051 | B-13 | N | 0 | IA62006 | 32-D-8007 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89053 | 08 | 32 | 1" | IA | 89053 | B-13 | N | 0 | IA89037 | N83002 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89054 | 08 | 32 | 1" | IA | 89054 | B-13 | N | 0 | IA89027 | 32-IAM-108 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89055 | 08 | 32 | 1" | IA | 89055 | B-13 | N | 0 | IA89054 | 32-IAM-109 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89056 | 08 | 32 | 1" | IA | 89056 | B-13 | N | 0 | IA89054 | 32-IAM-110 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89058 | 08 | 32 | 1" | IA | 89058 | B-13 | N | 0 | IA89027 | 32-IAM-104 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89059 | 08 | 32 | 1" | IA | 89059 | B-13 | N | 0 | IA89027 | 32-IAM-053 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89060 | 08 | 32 | 1" | IA | 89060 | B-13 | N | 0 | IA89027 | 32-IAM-115 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89064 | 08 | 32 | 1" | IA | 89064 | B-13 | N | 0 | IA89027 | 32-IAM-114 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89066 | 08 | 32 | 1/2" | IA | 89066 | B-13 | N | 0 | IA89075 | 105981A0 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89067 | 08 | 32 | 1" | IA | 89067 | B-13 | N | 0 | IA62006 | TP-N30606 (32-E-8921A HEATING BARREL) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89069 | 08 | 32 | 3/4" | IA | 89069 | B-13 | N | 0 | IA620A0 | 32-IAT-072 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89070 | 08 | 32 | 3/4" | IA | 89070 | B-13 | N | 0 | IA89040 | 32-IAT-098 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89071 | 08 | 32 | 3/4" | IA | 89071 | B-13 | N | 0 | IA89067 | 32-IAT-071 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89072 | 08 | 32 | 1/2" | IA | 89072 | B-13 | N | 0 | IA89012 | 168K8911 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89073 | 08 | 32 | 1-1/2" | IA | 89073 | B-13 | N | 0 | IA89054 | 32-IAM-148 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
LN81003 | 08 | 32 | 1/2" | LN | 81003 | 1CS2 | N | 0 | LN89008 | 32-PK-8102 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 175
LN81011 | 08 | 32 | 1/2" | LN | 81011 | 1CS2 | N | 0 | LN89003 | 32-ZF-8100B | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.59 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 175
LN84001 | 08 | 32 | 1/2" | LN | 84001 | 1CS2 | N | 0 | 32-D-8402 | VENT TO C-8100 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-063-01 |  | M | N | 000 | N | 175
LN89001 | 08 | 32 | 1/2" | LN | 89001 | B-1 | N | 0 | LN89007 | LN84001 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89001 | 08 | 32 | 1" | LN | 89001 | B-1 | N | 0 | LN89007 | LN84001 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89003 | 08 | 32 | 1/2" | LN | 89003 | B-1 | N | 0 | LN89001 | LN81011 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89004 | 08 | 32 | 1/2" | LN | 89004 | B-1 | N | 0 | LN89001 | LN81010 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89006 | 08 | 32 | 1/2" | LN | 89006 | B-1 | N | 0 | LN89001 | LN81016 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89007 | 08 | 32 | 1" | LN | 89007 | B-1 | N | 0 | N89035 | VA89016 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89008 | 08 | 32 | 1/2" | LN | 89008 | B-1 | N | 0 | LN89001 | LN81003 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LS72003 |  | 32 | 1" | LS | 72003 | B-5 | HB | 70 | LS72004 | LC72002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.51 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS72004 |  | 32 | 1-1/2" | LS | 72004 | D1S1 | HB | 50 | 32-E-7201 | LS72003 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.51 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 041 | N | 1090
N23005 | 08 | 32 | 1" | N | 23005 | B-1 | N | 0 | N | PR23032 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.17 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N24003 | 08 | 32 | 1" | N | 24003 | B-1 | N | 0 | SP--04-124C2-01 | HCM24051 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.21B | 2 | Art 4.3 | NA | N | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 140
N31003 | 08 | 32 | 1" | N | 31003 | B-1 | N | 0 | NITROGEN CONNECTION | PR31018 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 000 | N | 140
N32003 | 08 | 32 | 1" | N | 32003 | B-1 | N | 0 | NITROGEN CONNECTION | HCM32026 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.24 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 000 | N | 140
N32004 | 08 | 32 | 2" | N | 32004 | B4S1 | N | 0 | TP-24A, (CYLINDER) | TP-35A, (D-3204) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32006 | 08 | 32 | 2" | N | 32006 | B4S1 | N | 0 | TP-28A, (CYLINDER) | 32-D-3204 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32010 | 08 | 32 | 2" | N | 32010 | B4S1 | N | 0 | TP-33A, (32-D-3203) | HEADER | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32011 | 08 | 32 | 1/2" | N | 32011 | B4S1 | N | 0 | TP-40A, (32-D-3204) | N32012 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32012 | 08 | 32 | 2" | N | 32012 | B4S1 | N | 0 | TP-37A, (32-D-3204) | HEADER | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32016 | 08 | 32 | 2" | N | 32016 | B4S1 | N | 0 | TP-26B, (CYLINDER 1) | TO TEMPORARY TANK | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N32017 | 08 | 32 | 2" | N | 32017 | B4S1 | N | 0 | TP-24B, (CYLINDER 1) | TP-35B, (32-D-3204B) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
PA62082 | 08 | 32 | 3/4" | PA | 62082 | B-1 | N | 0 | PA62080 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62086 | 08 | 32 | 3/4" | PA | 62086 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62088 | 08 | 32 | 3/4" | PA | 62088 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62093 | 08 | 32 | 3/4" | PA | 62093 | B-1 | N | 0 | PA62053 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
VA00072 | 08 | 32 | 4" | VA | 00072 | B-1 | N | 0 | 4123-ACW-SM-068 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00074 | 08 | 32 | 4" | VA | 00074 | B-1 | N | 0 | 4131-ACW-SM-014 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00080 | 08 | 32 | 4" | VA | 00080 | B-1 | N | 0 | 4221-ACW-SM-090 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00081 | 08 | 32 | 4" | VA | 00081 | B-1 | N | 0 | 4221-ACW-SM-103 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00085 | 08 | 32 | 4" | VA | 00085 | B-1 | N | 0 | 6111-ACW-BS-001A | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00086 | 08 | 32 | 4" | VA | 00086 | B-1 | N | 0 | 6111-ACW-BS-001A | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00087 | 08 | 32 | 4" | VA | 00087 | B-1 | N | 0 | 6111-ACW-BS-001A | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00090 | 08 | 32 | 4" | VA | 00090 | B-1 | N | 0 | 6111-ACW-SM-077 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00092 | 08 | 32 | 4" | VA | 00092 | B-1 | N | 0 | 6111-SW-MH-005 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00100 | 08 | 32 | 4" | VA | 00100 | B-1 | N | 0 | 6111-ACW-SM-078 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00103 | 08 | 32 | 4" | VA | 00103 | B-1 | N | 0 | 7111-ACW-SM-081 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00105 | 08 | 32 | 4" | VA | 00105 | B-1 | N | 0 | 2211-ACW-SM-083 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA10001 | 08 | 32 | 2" | VA | 10001 | B4S2 | N | 0 | LPN10016 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.4 | 2 | NA | NA | NA | 6 | N | 32-U-002-01 |  | E | N | 000 | N | 183
VA11005 | 08 | 32 | 2" | VA | 11005 | B4S2 | N | 0 | VA11006 | To SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.47 | 2 | NA | NA | NA | 6 | N | 32-P-020-01 |  | E | N | 000 | N | 183
VA11006 | 08 | 32 | 1" | VA | 11006 | B4S2 | N | 0 | 32-D-1102 | VA11005 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.47 | 2 | NA | NA | NA | 6 | N | 32-P-020-01 |  | E | N | 000 | N | 183
N01004 | 08 | 32 | 1" | N | 01004 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | ET01001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-006-01 |  | E | N | 000 | N | 140
N01005 | 08 | 32 | 1" | N | 01005 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | HD01001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-002-01 |  | E | N | 000 | N | 140
N12009 | 08 | 32 | 1-1/2" | N | 12009 | B-1 | N | 0 | HEADER | 32-D-1602 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N12018 | 08 | 32 | 1/2" | N | 12018 | 1CS2 | N | 0 | END CAP | 32-LT-1201 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12028 | 08 | 32 | 3/4" | N | 12028 | 1CS2 | N | 0 | N12018 | 32-LT-1202 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N13001 | 08 | 32 | 1" | N | 13001 | B-1 | N | 0 | 32-D-1300 | N13002 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.6 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N13001 | 08 | 32 | 2" | N | 13001 | B-1 | N | 0 | 32-D-1300 | N13002 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.6 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N14002 | 08 | 32 | 3/4" | N | 14002 | 1CS2 | N | 0 | 32-D-1400A | N14023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14002 | 08 | 32 | 1-1/2" | N | 14002 | 1CS2 | N | 0 | 32-D-1400A | N14023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.7 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 166
N14005 | 08 | 32 | 1/2" | N | 14005 | 1CS2 | N | 0 | CT14006 | VA14005 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14005 | 08 | 32 | 1-1/2" | N | 14005 | 1CS2 | N | 0 | CT14006 | VA14005 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14005 | 08 | 32 | 2" | N | 14005 | 1CS2 | N | 0 | CT14006 | VA14005 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14007 | 08 | 32 | 3/4" | N | 14007 | 1CS2 | N | 0 | 32-D-1400B | N14020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
N14007 | 08 | 32 | 1-1/2" | N | 14007 | 1CS2 | N | 0 | 32-D-1400B | N14020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.8 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 166
BDL24095 | 08 | 32 | 1-1/2" | BDL | 24095 | B32S1 | N | 0 | BDL22020 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31023 | 08 | 32 | 6" | BDL | 31023 | B32S1 | N | 0 | 32-S-3100 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31031 | 08 | 32 | 2" | BDL | 31031 | B32S1 | N | 0 | BDL31025 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31035 | 08 | 32 | 3/4" | BDL | 31035 | B32S1 | N | 0 | HCM31019 | BDL31034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32019 | 08 | 32 | 3/4" | BDL | 32019 | B32S1 | N | 0 | HCM32019 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32026 | 08 | 32 | 3/4" | BDL | 32026 | B32S1 | N | 0 | HCM32019 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
PCW89015 | 08 | 32 | 10" | PCW | 89015 | 1CS2 | P | 100 | TP-N51705 (XV-8941) | PCW89012 | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PR23012 |  | 32 | 1/2" | PR | 23012 | D20S1 | HB | 30 | PR22015 | HCM24089 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.14 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR23012 |  | 32 | 4" | PR | 23012 | D20S1 | HB | 30 | PR22015 | HCM24089 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.14 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24035 | 08 | 32 | 1/2" | PR | 24035 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
VZ15004 |  | 32 | 1" | VZ | 15004 | B4S2 | EH | 30 | 32-D-1501 | 32-D-1501 | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | NA | NA | NA | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 239 | 23,25
VZ15004 |  | 32 | 1-1/2" | VZ | 15004 | B4S2 | EH | 30 | 32-D-1501 | 32-D-1501 | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | NA | NA | NA | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 239 | 23,25
VZ15005 | 08 | 32 | 3/4" | VZ | 15005 | 1CS2 | EH | 30 | 32-S-1500 | BLIND FLANGE | 1.0 | 150.0 | 0.1 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 240 | 23,25
VZ15006 |  | 32 | 1" | VZ | 15006 | 1CS2 | ET | 30 | 32-S-1501 | 32-S-1501 | 1.0 | 150.0 | 0.1 | 30.0 |  | 1.5 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 241 | 23,25
VZ16006 | 08 | 32 | 1" | VZ | 16006 | 4CS2 | ET | 30 | 32-D-1601 | 32-D-1601 | 0.5 | 180.0 | 0.05 | 50.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 404
VZ16007 |  | 32 | 1/2" | VZ | 16007 | 4CS2 | ET | 30 | 32-D-1600 | 32-D-1600 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 400
VZ16008 | 08 | 32 | 1/2" | VZ | 16008 | B-1 | ET | 30 | 32-D-1602 | - | 0.5 | 150.0 | 0.0 | 30.0 |  | .55 | 26.46 | P | VESSEL TRIM | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 144
VZ16009 | 08 | 32 | 3/4" | VZ | 16009 | 1FS4 | EH | 30 | 32-S-1600 | - | 60.0 | 180.0 | 45.0 | 50.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 408
VZ16010 | 08 | 32 | 3/4" | VZ | 16010 | 4CS2 | EH | 30 | 32-S-1601 | - | 6.0 | 180.0 | 5.0 | 50.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
CWR86017 |  | 32 | 3/4" | CWR | 86017 | B-1 | HB | 30 | JCW86021 | CWR86001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89021 | 08 | 32 | 3" | CWR | 89021 | B-1 | N | 0 | TP-N60104 (32-E-8906) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68Q | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89025 | 08 | 32 | 1" | CWR | 89025 | B-1 | N | 0 | TP-N21106 (E-8903) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68E | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
PW51013 |  | 32 | 2" | PW | 51013 | B4S1 | ST | 30 | 32-D-5101 | BDL51017 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51014 | 08 | 32 | 3/4" | PW | 51014 | B4S1 | N | 0 | 32-D-5101 | BDL51018 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51015 | 08 | 32 | 3/4" | PW | 51015 | B4S1 | N | 0 | 32-D-5102 | BDL51009 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51016 |  | 32 | 1/2" | PW | 51016 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51016 |  | 32 | 1" | PW | 51016 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51016 |  | 32 | 2" | PW | 51016 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51017 |  | 32 | 3/4" | PW | 51017 | B4S1 | ST | 30 | FLANGE HEADER | FLANGE HEADER | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51017 |  | 32 | 1-1/2" | PW | 51017 | B4S1 | ST | 30 | FLANGE HEADER | FLANGE HEADER | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51018 | 08 | 32 | 2" | PW | 51018 | B4S1 | N | 0 | TP-N3 (PW510114) | 32-D-5100 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-03 |  | E | N | 110 | N | 82
PW52007 | 08 | 32 | 2" | PW | 52007 | B4S2 | N | 0 | 32-D-5202 | ACW | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PW52010 | 08 | 32 | 6" | PW | 52010 | B4S2 | N | 0 | PW52014 | PW50023 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 85 | 78
PW52012 | 08 | 32 | 1-1/2" | PW | 52012 | B4S2 | N | 0 | 32-E-5201 | 32-T-5200 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52012 | 08 | 32 | 6" | PW | 52012 | B4S2 | N | 0 | 32-E-5201 | 32-T-5200 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52013 | 08 | 32 | 3/4" | PW | 52013 | B4S2 | N | 0 | 32-P-5200A | 32-E-5201 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52013 | 08 | 32 | 4" | PW | 52013 | B4S2 | N | 0 | 32-P-5200A | 32-E-5201 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52014 | 08 | 32 | 3/4" | PW | 52014 | B4S2 | N | 0 | 32-P-5200B | PW52010 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52015 | 08 | 32 | 1" | PW | 52015 | B4S2 | N | 0 | PW52016 | 32-P-5200B | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PW52016 | 08 | 32 | 1" | PW | 52016 | B4S2 | N | 0 | 32-D-5202 | 32-P-5200A | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PW52016 | 08 | 32 | 6" | PW | 52016 | B4S2 | N | 0 | 32-D-5202 | 32-P-5200A | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
CHWS20005 |  | 32 | 1" | CHWS | 20005 | B-1 | CF | 25 | 32-Z-2005 | 32-P-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61001 |  | 32 | 12" | CHWS | 61001 | B-1 | CF | 40 | 32-D-6100 | 32-P-6100A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CO26033 | 08 | 32 | 1/2" | CO | 26033 | 1IS5 | N | 0 | 1 ST. EMERGENCY KILLER SYSTEM | CO26025 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
HCM24057 |  | 32 | 3/4" | HCM | 24057 | D20S1 | P | 50 | HCM24069 | P23027 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
BDL14001 | 08 | 32 | 1" | BDL | 14001 | B4S1 | N | 0 | N14002 | BDL60023 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.7 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL21008 | 08 | 32 | 2" | BDL | 21008 | B32S1 | N | 0 | PR22012 | BDL24073 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24088 | 08 | 32 | 1" | BDL | 24088 | B32S1 | N | 0 | HCM24094 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
DMW63001 | 08 | 32 | 3/4" | DMW | 63001 | SXB-48 | N | 0 | DMW64003 | LC63035 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.87 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-060-02 |  | M | N | 000 | N | 26
DMW63001 | 08 | 32 | 3" | DMW | 63001 | SXB-48 | N | 0 | DMW64003 | LC63035 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.87 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-060-02 |  | M | N | 000 | N | 26
SWW92015 | 08 | 32 | 3" | SWW | 92015 | 1CS2 | N | 0 | SWW92005 | 32-H-9001E | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92016 | 08 | 32 | 8" | SWW | 92016 | 1CS2 | N | 0 | DETAIL A | SWW92004 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92019 | 08 | 32 | 8" | SWW | 92019 | 1CS2 | N | 0 | DETAIL A | SWW92004 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92020 | 08 | 32 | 8" | SWW | 92020 | 1CS2 | N | 0 | DETAIL A | SWW92004 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
WW24001 | 08 | 32 | 1" | WW | 24001 | B4S2 | N | 0 | TP-MP-16 (PK-2400) | TO PORTABLE POT | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.21A | 2 | Art 4.3 | NA | N | 1 | N | 32-P-045-03 |  | E | N | 000 | N | 87
BDL43022 | 08 | 32 | 3/4" | BDL | 43022 | B32S1 | N | 0 | PR43031 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL51018 |  | 32 | 2" | BDL | 51018 | B4S1 | ST | 30 | PW51014 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51020 |  | 32 | 1" | BDL | 51020 | B4S1 | ST | 30 | 32-D-5104 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL51020 |  | 32 | 3" | BDL | 51020 | B4S1 | ST | 30 | 32-D-5104 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL60034 | 08 | 32 | 6" | BDL | 60034 | B32S1 | N | 0 | BDL24079 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60034 | 08 | 32 | 8" | BDL | 60034 | B32S1 | N | 0 | BDL24079 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60044 | 08 | 32 | 1" | BDL | 60044 | B32S1 | N | 0 | N67095 | BDL60038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60056 | 08 | 32 | 1" | BDL | 60056 | B32S1 | N | 0 | N67111 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL60058 | 08 | 32 | 1" | BDL | 60058 | B32S1 | N | 0 | N67113 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL61011 | 08 | 32 | 1/2" | BDL | 61011 | B32S1 | N | 0 | TP-039 (32-E-6101) | BDL61013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL65003 |  | 32 | 2" | BDL | 65003 | B4S1 | ST | 30 | BDL65002 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71020 | 08 | 32 | 2" | BDL | 71020 | B4S1 | N | 0 | FL710120 | BDL71041 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.50A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71042 | 08 | 32 | 3/4" | BDL | 71042 | B32S1 | N | 0 | TP-5 (ET710108) | BDL71020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.50A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
LC63060 |  | 32 | 3/4" | LC | 63060 | B-5 | HB | 30 | LS63175 | LC63104 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.2 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63091 |  | 32 | 1-1/2" | LC | 63091 | B-5 | HB | 40 | HEADER | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC630AE |  | 32 | 3/4" | LC | 630AE | B-5 | HB | 30 | 32-1127-S-009 | LC6300M | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC71006 |  | 32 | 3/4" | LC | 71006 | B-5 | HB | 30 | LS71011 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.48 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LN81002 | 08 | 32 | 1/2" | LN | 81002 | 1CS2 | N | 0 | LN89005 | 32-PK-8102 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.62 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 175
LN84001 | 08 | 32 | 2" | LN | 84001 | 1CS2 | N | 0 | 32-D-8402 | VENT TO C-8100 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-063-01 |  | M | N | 000 | N | 175
LN89001 | 08 | 32 | 1-1/2" | LN | 89001 | B-1 | N | 0 | LN89007 | LN84001 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LN89007 | 08 | 32 | 1-1/2" | LN | 89007 | B-1 | N | 0 | N89035 | VA89016 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
BDL51021 |  | 32 | 1/2" | BDL | 51021 | B4S1 | ST | 30 | 32-D-5104 | ACW | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL51021 | 08 | 32 | 1-1/2" | BDL | 51021 | B4S1 | N | 0 | 32-D-5104 | ACW | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 1 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL53004 | 08 | 32 | 3/4" | BDL | 53004 | B4S1 | N | 0 | PR53004 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
LS89035 |  | 32 | 3/4" | LS | 89035 | B-5 | HB | 60 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89035 |  | 32 | 2" | LS | 89035 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89035 |  | 32 | 3" | LS | 89035 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89038 |  | 32 | 3/4" | LS | 89038 | B-5 | HB | 60 | LS89035 | US-5111-01 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89040 |  | 32 | 3/4" | LS | 89040 | B-5 | HB | 60 | LS89039 | 32-US-1211-07 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89041 |  | 32 | 3/4" | LS | 89041 | B-5 | HB | 60 | LS89039 | 32-US-1211-08 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89045 |  | 32 | 3/4" | LS | 89045 | B-5 | HB | 60 | LS89052 | PA89037 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89048 |  | 32 | 1" | LS | 89048 | B-5 | HB | 70 | LS01001 | 32-US-1211-01 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89049 |  | 32 | 1" | LS | 89049 | B-5 | HB | 70 | LS01001 | 32-US-1211-03 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89051 |  | 32 | 3/4" | LS | 89051 | B-5 | HB | 60 | LS01001 | 32-S-8905 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-11 |  | E | N | 000 | N | 90
LS89052 |  | 32 | 1" | LS | 89052 | B-5 | HB | 70 | PA01001 | PA89038 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89053 |  | 32 | 3/4" | LS | 89053 | B-5 | HB | 60 | LS89052 | US | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | 7 | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89056 |  | 32 | 1/2" | LS | 89056 | B-5 | HB | 60 | LC91A70 | LS89035 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89057 | 08 | 32 | 3/4" | LS | 89057 | B-5 | HB | 60 | LS89035 | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89059 |  | 32 | 1/2" | LS | 89059 | B-5 | HB | 60 | LS01001 | LC89049 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
IW01001 | 08 | 32 | 2" | IW | 01001 | B-1 | N | 0 | RW220007 OSBL LINE | HEADER | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW02001 | 08 | 32 | 3/4" | IW | 02001 | B-1 | N | 0 | IW64003 | 32-US-1115-003 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64002 | 08 | 32 | 3/4" | IW | 64002 | B-1 | N | 0 | IW01001 | IW64001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64006 | 08 | 32 | 3/4" | IW | 64006 | B-1 | N | 0 | IW64041 | 32-US-1127-002 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64011 | 08 | 32 | 3/4" | IW | 64011 | B-1 | N | 0 | IW64010 | 32-US-1122-01 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64014 | 08 | 32 | 3/4" | IW | 64014 | B-1 | N | 0 | IW64015 | 32-US-1112-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64016 | 08 | 32 | 1" | IW | 64016 | B-1 | N | 0 | IW01001 | IW64024 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64018 | 08 | 32 | 3/4" | IW | 64018 | B-1 | N | 0 | IW64016 | 32-US-1121-02 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64019 | 08 | 32 | 3/4" | IW | 64019 | B-1 | N | 0 | IW64016 | 32-US-1121-03 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64020 | 08 | 32 | 3/4" | IW | 64020 | B-1 | N | 0 | IW64016 | 32-US-1121-04 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64024 | 08 | 32 | 3/4" | IW | 64024 | B-1 | N | 0 | IW64016 | 32-US-1121-01 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64025 | 08 | 32 | 2" | IW | 64025 | B-1 | N | 0 | IW01001 | IW64028 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64033 | 08 | 32 | 3/4" | IW | 64033 | B-1 | N | 0 | IW64025 | 32-US-1121-12 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64035 | 08 | 32 | 3/4" | IW | 64035 | B-1 | N | 0 | IW64025 | 32-US-1121-13 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
PA89021 | 08 | 32 | 2" | PA | 89021 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-062-01 |  | E | N | 000 | N | 190
PA89022 | 08 | 32 | 3/4" | PA | 89022 | B-1 | N | 0 | PA89021 | US-..... | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89032 | 08 | 32 | 1-1/2" | PA | 89032 | B-1 | N | 0 | PA01001 | 32-US-1211-10 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89037 | 08 | 32 | 3/4" | PA | 89037 | B-1 | N | 0 | PA89038 | LS89045 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89038 | 08 | 32 | 1-1/2" | PA | 89038 | B-1 | N | 0 | PA01001 | IW89028 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89039 | 08 | 32 | 1/2" | PA | 89039 | B-1 | N | 0 | PA01001 | PX86001 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89040 | 08 | 32 | 1/2" | PA | 89040 | B-1 | N | 0 | PA01001 | 32-PK-8700 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89040 | 08 | 32 | 1" | PA | 89040 | B-1 | N | 0 | PA01001 | 32-PK-8700 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89042 | 08 | 32 | 3/4" | PA | 89042 | B-1 | N | 0 | PK-9002 | PA89021 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89044 | 08 | 32 | 3/4" | PA | 89044 | B-1 | N | 0 | PA89021 | US-3221-01 AT GRADE | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89049 | 08 | 32 | 3/4" | PA | 89049 | B-1 | N | 0 | PA89021 | US-3221-01 AT GRADE | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89053 |  | 32 | 3/4" | PA | 89053 | B-1 | HA | 30 | PA89038 | LS89054 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-091-01 |  | E | N | 000 | N | 190
VA11006 | 08 | 32 | 3" | VA | 11006 | B4S2 | N | 0 | 32-D-1102 | VA11005 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.47 | 2 | NA | NA | NA | 6 | N | 32-P-020-01 |  | E | N | 000 | N | 183
N14025 | 08 | 32 | 1/2" | N | 14025 | 1CS2 | N | 0 | N14024 | 32-Z-1402 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N15003 | 08 | 32 | 1/2" | N | 15003 | B-1 | N | 0 | O15018 | N15001 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.9 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N16003 | 08 | 32 | 1" | N | 16003 | 1CS2 | N | 0 | N67002 | 32-D-1600 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.10 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-023-01 |  | M | N | 000 | N | 166
N32003 | 08 | 32 | 3/4" | N | 32003 | B-1 | N | 0 | NITROGEN CONNECTION | HCM32026 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.24 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 000 | N | 140
N32007 | 08 | 32 | 1" | N | 32007 | B4S1 | N | 0 | TP-27A, (PRESSURE PACKING COMBINED VENT AND DRAIN) | 32-FT-3256 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32017 | 08 | 32 | 1-1/2" | N | 32017 | B4S1 | N | 0 | TP-24B, (CYLINDER 1) | TP-35B, (32-D-3204B) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N32018 | 08 | 32 | 1" | N | 32018 | B4S1 | N | 0 | TP-28B, (CYLINDER 1) | TP-34B, (32-D-3204B) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N34008 | 08 | 32 | 1" | N | 34008 | B-1 | N | 0 | NITROGEN CONNECTION | PR34021 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.26 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-01 |  | E | N | 000 | N | 140
N40008 | 08 | 32 | 1" | N | 40008 | B-1 | N | 0 | NITROGEN CONNECTION | PR40027 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-03 |  | E | N | 000 | N | 140
N52025 | 08 | 32 | 1/2" | N | 52025 | 1CS2 | N | 0 | N67040 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N52025 | 08 | 32 | 3/4" | N | 52025 | 1CS2 | N | 0 | N67040 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N52033 | 08 | 32 | 3/4" | N | 52033 | 1CS2 | N | 0 | N67043 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N52041 | 08 | 32 | 1/2" | N | 52041 | 1CS2 | N | 0 | N67064 | PN52029 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 166
N52041 | 08 | 32 | 1" | N | 52041 | 1CS2 | N | 0 | N67064 | PN52029 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 166
VG89001 | 08 | 32 | 24" | VG | 89001 | B-1 | N | 0 | TP-N60802 (C-8901) | 19-D-5003 | 0.25 | 110.0 | 0.015 | 40.0 |  | .28 | 26.46 | P | PROCESS VENT/EQUALIZ.LINE | G | - | - | >1.5 | 40 | sh.4 | 1 | NA | NA | NA | 1 | N | 32-P-082-09 |  | E | N | 010 | N | 3282
VG91001 | 08 | 32 | 20" | VG | 91001 | B-1 | N | 0 | TP-265 (VG910260) | S-5001 | 0.25 | 110.0 | 0.015 | 40.0 |  | .28 | 26.46 | P | PROCESS VENT/EQUALIZ.LINE | G | - | - | >1.5 | 40 | sh.71 | 1 | NA | NA | NA | 1 | N | 32-P-082-09 |  | E | N | 010 | N | 3282
PR24035 | 08 | 32 | 3/4" | PR | 24035 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24035 | 08 | 32 | 1-1/2" | PR | 24035 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24035 | 08 | 32 | 3" | PR | 24035 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24037 | 08 | 32 | 2" | PR | 24037 | D20S1 | N | 0 | HCM24083 | PR24039 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24037 | 08 | 32 | 4" | PR | 24037 | D20S1 | N | 0 | HCM24083 | PR24039 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24039 |  | 32 | 3" | PR | 24039 | D20S1 | P | 50 | HCM24084 | PR24040 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24039 |  | 32 | 4" | PR | 24039 | D20S1 | P | 50 | HCM24084 | PR24040 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24042 |  | 32 | 1-1/2" | PR | 24042 | D20S1 | P | 50 | PR24039 | PR24043 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR31018 |  | 32 | 1-1/2" | PR | 31018 | D20S1 | HB | 30 | JLS31012 | PR31019 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
PR31022 | 08 | 32 | 3/4" | PR | 31022 | D20S1 | N | 0 | PR31023 | HCM31017 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR31022 | 08 | 32 | 1-1/2" | PR | 31022 | D20S1 | N | 0 | PR31023 | HCM31017 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR33002 | 08 | 32 | 3/4" | PR | 33002 | C42S1 | N | 0 | 32-D-3300 | BDL33002 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33002 | 08 | 32 | 3" | PR | 33002 | C42S1 | N | 0 | 32-D-3300 | BDL33002 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33002 | 08 | 32 | 4" | PR | 33002 | C42S1 | N | 0 | 32-D-3300 | BDL33002 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33006 |  | 32 | 3" | PR | 33006 | C42S1 | HB | 30 | 32-D-3300 | BDL33007 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33014 | 08 | 32 | 3" | PR | 33014 | C42S1 | N | 0 | PR72002 | PR33013 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33015 | 08 | 32 | 10" | PR | 33015 | C42S1 | N | 0 | 32-D-3300 | PR33016 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
VZ24004 | 08 | 32 | 1/2" | VZ | 24004 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
VZ24009 |  | 32 | 1/2" | VZ | 24009 | D20S1 | HB | 30 | 32-E-2402 | BDL24085 | 49.0/49.0 | -45.0/250.0 | 32.18/32.18 | 74.0/73.9 |  | 76.71 | 153.15 | H | VESSEL TRIM | LG | - | - | >1.5 | 73.9 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 510 | 15
VZ31005 | 08 | 32 | 1" | VZ | 31005 | C42S1 | HB | 30 | 32-D-3100 | - | 35.0/35.0 | 250.0/-45.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | VESSEL TRIM | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 363 | 10
VZ31005 | 08 | 32 | 2" | VZ | 31005 | C42S1 | HB | 40 | 32-D-3100 | - | 35.0/35.0 | 250.0/-45.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | VESSEL TRIM | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 363 | 10
VZ32002 |  | 32 | 1/2" | VZ | 32002 | C42S1 | HB | 30 | 32-D-3200 | HCM32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
VZ32002 |  | 32 | 1-1/2" | VZ | 32002 | C42S1 | HB | 30 | 32-D-3200 | HCM32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
VZ32002 |  | 32 | 2" | VZ | 32002 | C42S1 | HB | 30 | 32-D-3200 | HCM32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
VZ34004 | 08 | 32 | 1" | VZ | 34004 | B4S1 | HB | 30 | 32-D-3400 | - | 8.0/8.0 | 250.0/0.0 | 5.0 | 80.0 |  | 12.52 | 29.4 | H | VESSEL TRIM | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 379 | 10
IW01001 | 08 | 32 | 3/4" | IW | 01001 | B-1 | N | 0 | RW220007 OSBL LINE | HEADER | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW01001 | 08 | 32 | 4" | IW | 01001 | B-1 | N | 0 | RW220007 OSBL LINE | HEADER | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW02002 | 08 | 32 | 3/4" | IW | 02002 | B-1 | N | 0 | IW64003 | 32-US-4131-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW6200H | 08 | 32 | 3/4" | IW | 6200H | B-1 | N | 0 | IW64051 | 32-US-1128-002 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64012 | 08 | 32 | 3/4" | IW | 64012 | B-1 | N | 0 | IW64010 | 32-US-1122-02 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64036 | 08 | 32 | 3/4" | IW | 64036 | B-1 | N | 0 | IW64025 | 32-US-1121-14 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64069 | 08 | 32 | 3/4" | IW | 64069 | B-1 | N | 0 | IW64010 | 32-US-1122-03 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89030 | 08 | 32 | 2" | IW | 89030 | B-1 | N | 0 | IW01001 | IW00C02 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
PW72007 | 08 | 32 | 3/4" | PW | 72007 | B4S2 | N | 0 | PR72006 | ACW | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.51 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 30
WW92001 | 08 | 32 | 2" | WW | 92001 | B4S2 | N | 0 | SWW92033 | TO TRENCH | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.72 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW94004 | 08 | 32 | 1/2" | WW | 94004 | B4S2 | N | 0 | DRAIN | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-090-02 |  | E | N | 000 | N | 87
VZ16007 |  | 32 | 2" | VZ | 16007 | 4CS2 | EH | 30 | 32-D-1600 | 32-D-1600 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 400
VZ16008 | 08 | 32 | 2" | VZ | 16008 | B-1 | EH | 30 | 32-D-1602 | - | 0.5 | 150.0 | 0.0 | 30.0 |  | .55 | 26.46 | P | VESSEL TRIM | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 20 | N | 32-P-024-01 |  | E | N | 000 | N | 144
VZ21003 | 08 | 32 | 1" | VZ | 21003 | 2FS4 | CR | 25 | 32-R-2100 | - | 50.0/50.0 | -40.0/200.0 | 37.0 | 20.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 20 | sh.12 | 2 | Art 4.3 | NA | N | NR | N | 32-P-042-01 |  | H-1 | N | 110 | N | 412 | 12,15,6,17
DMW64003 | 08 | 32 | 1-1/2" | DMW | 64003 | SXB-48 | N | 0 | DMW01001 | DMW63001 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DO12001 | 08 | 32 | 1/2" | DO | 12001 | 1CS2 | N | 0 | DRUM | 32-P-1201 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12001 | 08 | 32 | 1" | DO | 12001 | 1CS2 | N | 0 | DRUM | 32-P-1201 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12003 | 08 | 32 | 1" | DO | 12003 | 1CS2 | N | 0 | DO12004 | 32-D-1200A | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12010 |  | 32 | 1/2" | DO | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-S-1200B | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12010 |  | 32 | 1-1/2" | DO | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-S-1200B | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12017 | 08 | 32 | 3/4" | DO | 12017 | 3FS3 | N | 0 | 32-P-1200A | DO12019 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12018 | 08 | 32 | 1/2" | DO | 12018 | 3FS3 | N | 0 | 32-P-1200B | DO12019 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12019 | 08 | 32 | 1/4" | DO | 12019 | 3FS3 | N | 0 | DO12017 | DO12017 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12022 |  | 32 | 3/4" | DO | 12022 | 3FS3 | ET | 30 | DO12008 | 32-P-1200A | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 275 | 23,29,25
DO12032 | 08 | 32 | 1/2" | DO | 12032 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12032 | 08 | 32 | 1" | DO | 12032 | 1CS2 | N | 0 | N12030 | DO12036 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO20001 |  | 32 | 1/2" | DO | 20001 | 3FS3 | ET | 30 | DO12017 | DO12017 | 70.0 | 150.0 | 50.25 | 30.0 |  | 105.15 | 148.95 | IO | DONOR | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 220 | N | 275 | 23,29,25
LO32006 | 08 | 32 | 1/2" | LO | 32006 | QXB-55 | N | 0 | TP 20B (LO320114) | TP 19B (32-PK-3200 B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LO36004 | 08 | 32 | 1-1/2" | LO | 36004 | QXB-55 | N | 0 | TP-139 (32-P-3601) | TP-140 (LO360121) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.28D | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 110 | N | 800
LO36004 | 08 | 32 | 3" | LO | 36004 | QXB-55 | N | 0 | TP-139 (32-P-3601) | TP-140 (LO360121) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.28D | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 110 | N | 800
LO40002 | 08 | 32 | 1-1/2" | LO | 40002 | QXB-55 | N | 0 | TP-13 (32-D-4002) | TP-12 (LO400118) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.30B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-049-03 |  | M | N | 110 | N | 800
LO40005 | 08 | 32 | 6" | LO | 40005 | QXB-55 | P | 50 | TP-22 (LO400125) | TP-23- (32-D-4001) | 15.0/16.0 | 120.0/80.0 | 2.0 | 65.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 65 | sh.30B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-049-03 |  | M | N | 110 | N | 801
BDL72040 | 08 | 32 | 3/4" | BDL | 72040 | B32S1 | N | 0 | PR72015 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72044 | 08 | 32 | 3/4" | BDL | 72044 | B32S1 | N | 0 | PR72020 | BDL72042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL73047 | 08 | 32 | 2" | BDL | 73047 | B4S1 | N | 0 | BU73042 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73078 | 08 | 32 | 1" | BDL | 73078 | B4S1 | N | 0 | BU73043 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BU73042 | 08 | 32 | 1" | BU | 73042 | B32S1 | N | 0 | 32-S-7302A | BDL73047 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73042 | 08 | 32 | 1-1/2" | BU | 73042 | B32S1 | N | 0 | 32-S-7302A | BDL73047 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73053 | 08 | 32 | 1" | BU | 73053 | D20S1 | N | 0 | BU73051 | BU73040 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BDL60002 | 08 | 32 | 20" | BDL | 60002 | B32S1 | N | 0 | BDL60029 | FL60001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60021 | 08 | 32 | 2" | BDL | 60021 | B32S1 | N | 0 | BDL33018 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL60033 | 08 | 32 | 10" | BDL | 60033 | B32S1 | N | 0 | BDL24059 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60057 | 08 | 32 | 1" | BDL | 60057 | B32S1 | N | 0 | N67112 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL61008 | 08 | 32 | 1-1/2" | BDL | 61008 | B32S1 | N | 0 | TP-026 (LO610171) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61019 | 08 | 32 | 1" | BDL | 61019 | B32S1 | N | 0 | TP-029 (E-6102) | BDL61008 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL71025 | 08 | 32 | 3/4" | BDL | 71025 | B4S1 | N | 0 | BDL71035 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL71026 | 08 | 32 | 1" | BDL | 71026 | B4S1 | N | 0 | ET71076 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL72034 | 08 | 32 | 1" | BDL | 72034 | B32S1 | N | 0 | PR72039 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72042 | 08 | 32 | 1/2" | BDL | 72042 | B32S1 | N | 0 | BDL72044 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72042 | 08 | 32 | 3/4" | BDL | 72042 | B32S1 | N | 0 | BDL72044 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
LC61001 |  | 32 | 1" | LC | 61001 | B-5 | HB | 40 | LS61001 | LC63104 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC61002 |  | 32 | 3/4" | LC | 61002 | B-5 | HB | 30 | LS61002 | LC63104 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300F |  | 32 | 1-1/2" | LC | 6300F | B-5 | HB | 40 | 32-1121-R-004 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300G |  | 32 | 2" | LC | 6300G | B-5 | HB | 40 | 32-1121-R-005 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300J |  | 32 | 1-1/2" | LC | 6300J | B-5 | HB | 40 | 32-1121-R-015 | LC630AA | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300L |  | 32 | 2" | LC | 6300L | B-5 | HB | 40 | 32-1127-R-008 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300M |  | 32 | 2" | LC | 6300M | B-5 | HB | 40 | 32-1127-R-009 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300N |  | 32 | 1-1/2" | LC | 6300N | B-5 | HB | 40 | 32-1127-R-010 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300O |  | 32 | 1-1/2" | LC | 6300O | B-5 | HB | 40 | 32-1111-R-011 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300Q |  | 32 | 1-1/2" | LC | 6300Q | B-5 | HB | 40 | 32-1124-R-013 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300U |  | 32 | 3/4" | LC | 6300U | B-5 | HB | 30 | LS630BA | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300X |  | 32 | 2" | LC | 6300X | B-5 | HB | 40 | 32-1121-R-001 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63027 |  | 32 | 3/4" | LC | 63027 | B-5 | P | 50 | LC63034 | 32-D-6100 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63027 |  | 32 | 1" | LC | 63027 | B-5 | P | 50 | LC63034 | 32-D-6100 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
IW64040 | 08 | 32 | 3/4" | IW | 64040 | B-1 | N | 0 | IW64025 | 32-US-1121-18 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64041 | 08 | 32 | 3/4" | IW | 64041 | B-1 | N | 0 | IW01001 | IW64045 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64045 | 08 | 32 | 3/4" | IW | 64045 | B-1 | N | 0 | IW64041 | 32-US-1127-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64046 | 08 | 32 | 3/4" | IW | 64046 | B-1 | N | 0 | IW01001 | IW64047 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64049 | 08 | 32 | 3/4" | IW | 64049 | B-1 | N | 0 | IW64046 | 32-US-1127-003 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64052 | 08 | 32 | 3/4" | IW | 64052 | B-1 | N | 0 | IW64051 | 32-US-1128-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64068 | 08 | 32 | 1" | IW | 64068 | B-1 | N | 0 | IW64016 | - | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64070 | 08 | 32 | 3/4" | IW | 64070 | B-1 | N | 0 | IW64003 | 32-US-1115-002 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
LO23003 | 08 | 32 | 1-1/2" | LO | 23003 | QXB-55 | P | 50 | TP 14 (D-2501) | TP-15 (D-2500) | 15.0/16.0 | 120.0/80.0 | 2.0 | 65.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 65 | sh.16B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-044-03 |  | M | N | 110 | N | 801
VA43012 | 08 | 32 | 1" | VA | 43012 | B4S2 | N | 0 | CHWR43010 | WW64001 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.33 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA50006 | 08 | 32 | 4" | VA | 50006 | B4S2 | N | 0 | LS50048 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.34 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA50008 | 08 | 32 | 6" | VA | 50008 | B4S2 | N | 0 | LS50002 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.34 | 2 | NA | NA | NA | 6 | N | 32-P-050-01 |  | E | N | 000 | N | 183
VA50009 | 08 | 32 | 1" | VA | 50009 | B4S2 | N | 0 | JWR50002 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.35 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA52010 | 08 | 32 | 10" | VA | 52010 | B4S2 | N | 0 | PN52026 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
FW68Z02 | 08 | 45 | 3" | FW | 68Z02 | B-13 | N | 0 | FW68Z01 | WC | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | Y | 000 | - | 74
FW68Z03 | 08 | 45 | 3" | FW | 68Z03 | B-13 | N | 0 | WC | FW68Z02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | Y | 000 | - | 74
HCM23003 |  | 32 | 3/4" | HCM | 23003 | C42S1 | HB | 30 | 32-S-2300 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23003 |  | 32 | 6" | HCM | 23003 | C42S1 | HB | 40 | 32-S-2300 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23003 |  | 32 | 10" | HCM | 23003 | C42S1 | HB | 40 | 32-S-2300 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23046 |  | 32 | 3/4" | HCM | 23046 | C42S1 | HB | 30 | HCM24059 | HCM23058 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23046 |  | 32 | 3" | HCM | 23046 | C42S1 | HB | 40 | HCM24059 | HCM23058 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23046 |  | 32 | 6" | HCM | 23046 | C42S1 | HB | 40 | HCM24059 | HCM23058 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23050 |  | 32 | 1/2" | HCM | 23050 | 1FS4 | JP | 0 | HCM23049 | HCM23052 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23050 | 08 | 32 | 1" | HCM | 23050 | 1FS4 | N | 0 | HCM23049 | HCM23052 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23057 |  | 32 | 1/2" | HCM | 23057 | 1FS4 | JP | 0 | JLS23009 | JLS23011 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23057 | 08 | 32 | 1" | HCM | 23057 | 1FS4 | N | 0 | JLS23009 | JLS23011 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23060 |  | 32 | 3/4" | HCM | 23060 | C42S1 | HB | 30 | HCM23004 | HCM24089 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23060 |  | 32 | 6" | HCM | 23060 | C42S1 | HB | 40 | HCM23004 | HCM24089 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23068 | 08 | 32 | 1/2" | HCM | 23068 | 1FS4 | N | 0 | HCM23070 | HCM23067 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23069 |  | 32 | 1/2" | HCM | 23069 | C42S1 | HB | 30 | HCM23004 | P23017 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23069 |  | 32 | 1-1/2" | HCM | 23069 | C42S1 | HB | 30 | HCM23004 | P23017 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
BDL72021 | 08 | 32 | 3/4" | BDL | 72021 | B32S1 | N | 0 | BDL72022 | BDL72026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72026 | 08 | 32 | 2" | BDL | 72026 | B32S1 | N | 0 | PR72050 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72033 | 08 | 32 | 3/4" | BDL | 72033 | B32S1 | N | 0 | PR72017 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72039 | 08 | 32 | 2" | BDL | 72039 | B32S1 | N | 0 | PR72043 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72051 | 08 | 32 | 3/4" | BDL | 72051 | B32S1 | N | 0 | PR72024 | BDL60024 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72064 | 08 | 32 | 1/2" | BDL | 72064 | B32S1 | P | 50 | 32-LI-7252 | BDL72060 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72065 | 08 | 32 | 1/2" | BDL | 72065 | B32S1 | N | 0 | T-7202A, 32-BV-7231 | BDL72064 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72070 | 08 | 32 | 3" | BDL | 72070 | B32S1 | N | 0 | PR72066 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
PR33019 | 08 | 32 | 3/4" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33019 | 08 | 32 | 1-1/2" | PR | 33019 | D20S1 | N | 0 | 32-P-3300A | PR33022 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33023 | 08 | 32 | 3/4" | PR | 33023 | C42S1 | N | 0 | PR72002 | PR40022 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33023 | 08 | 32 | 1-1/2" | PR | 33023 | C42S1 | N | 0 | PR72002 | PR40022 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR33025 | 08 | 32 | 1-1/2" | PR | 33025 | C42S1 | N | 0 | PR33020 | PR33021 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33027 | 08 | 32 | 1-1/2" | PR | 33027 | C42S1 | N | 0 | 32-E-3301 | BDL33003 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR34001 |  | 32 | 3/4" | PR | 34001 | B4S1 | P | 50 | 32-S-3400 | BDL34013 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34001 |  | 32 | 10" | PR | 34001 | B4S1 | P | 100 | 32-S-3400 | BDL34013 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34015 |  | 32 | 3/4" | PR | 34015 | B4S1 | P | 50 | 32-S-3400 | 32-S-3401A | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34015 |  | 32 | 10" | PR | 34015 | B4S1 | P | 100 | 32-S-3400 | 32-S-3401A | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34015 |  | 32 | 12" | PR | 34015 | B4S1 | P | 100 | 32-S-3400 | 32-S-3401A | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34021 |  | 32 | 1" | PR | 34021 | D20S1 | HB | 30 | PR36009 | PR34020 | 55.0/55.0 | -45.0/190.0 | 40.0/40.0 | 80.0/121.0 |  | 82.81 | 153.15 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-048-01 |  | G | N | 141 | N | 334 | 10
PR34028 |  | 32 | 1" | PR | 34028 | QXB26S1 | ET | 30 | PR34019 | PR34002 | 8.0/8.0 | 200.0/-45.0 | 5.0 | 80.0 |  | 12.83 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-048-01 |  | G | N | 141 | N | 392 | 10
PR35019 | 08 | 32 | 10" | PR | 35019 | B4S1 | N | 0 | 32-E-3500 | 32-D-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35021 | 08 | 32 | 1" | PR | 35021 | B4S1 | N | 0 | 32-D-3500 | PR35020 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
VZ35002 | 08 | 32 | 3/4" | VZ | 35002 | B4S1 | N | 0 | 32-D-3500 | 32-D-3500 | 5.0 | 120.0 | 0.5 | 45.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | G | - | - | >1.5 | 45 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 378 | ,10
VZ35002 | 08 | 32 | 1-1/2" | VZ | 35002 | B4S1 | N | 0 | 32-D-3500 | 32-D-3500 | 5.0 | 120.0 | 0.5 | 45.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | G | - | - | >1.5 | 45 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 378 | ,10
CT14002 | 08 | 32 | 1" | CT | 14002 | 3FS3 | N | 0 | CT14010 | CT15003 | 20.0 | 190.0 | 10.0 | 6.0 |  | 31.64 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | A | N | 232 | N | 285 | 23,25
CT14006 | 08 | 32 | 3" | CT | 14006 | 1CS2 | N | 0 | CATALYST DRUM | 32-D-1400B | 10.0/0.5 | 80.0/60.0 | 8.0/0.01 | 30.0/30.0 |  | 15 | 28.5 | IO | DRY CATALYST | SL | - | - | <1.5 | 30 | sh.8 | 1 | I | MOD.A | Y | NR | N | 32-P-026-02 |  | M | N | 232 | N | 283 | 23,25
CT14009 |  | 32 | 1/2" | CT | 14009 | 3FS3 | CF | 25 | VZ14016 | JCHW14002 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
JCHW14002 |  | 32 | 2" | JCHW | 14002 | B-1 | CF | 25 | CT14009 | CT14004 | 9.0 | 100.0 | 6.0 | 3.0 |  | 13.5 | 29.4 | H | JACKET REFR.WATER CHILLED | L | - | - | <1.5 | 3 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-03 |  | E | N | 000 | N | 65
JCW86021 |  | 32 | 1/2" | JCW | 86021 | B-1 | HB | 30 | JCW86020 | CWR86017 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JLS20001 |  | 32 | 2" | JLS | 20001 | B-5 | HB | 50 | CHWR20004 | CHWR20004 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 000 | N | 111 | 1
JLS21002 |  | 32 | 1-1/2" | JLS | 21002 | B-5 | HB | 50 | CHWS21003 | CHWS21004 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.12 | 2 | I | MOD.A | Y | 20 | N | 32-U-023-01 |  | E | N | 000 | N | 111 | 1
JLS21002 |  | 32 | 8" | JLS | 21002 | B-5 | HB | 60 | CHWS21003 | CHWS21004 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.12 | 2 | I | MOD.A | Y | 20 | N | 32-U-023-01 |  | E | N | 000 | N | 111 | 1
JLS23008 |  | 32 | 3" | JLS | 23008 | B-5 | HB | 50 | HCM23045 | HCM23048 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23009 |  | 32 | 2" | JLS | 23009 | B-5 | HB | 50 | HCM23048 | HCM23057 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23012 |  | 32 | 1-1/2" | JLS | 23012 | B-5 | HB | 50 | JLS23011 | LS23026 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23016 |  | 32 | 1-1/2" | JLS | 23016 | B-5 | HB | 50 | LS63044 | HCM23067 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23019 |  | 32 | 1-1/2" | JLS | 23019 | B-5 | HB | 50 | LS63146 | LS23030 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS24001 |  | 32 | 1" | JLS | 24001 | B-5 | HB | 50 | LS63038 | LS24010 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-046-01 |  | E | N | 000 | N | 111 | 1
JWR24007 | 08 | 32 | 3/4" | JWR | 24007 | D20S1 | N | 0 | 32-E-2403 | JWR24008 | 49.0/49.0 | -45.0/150.0 | 5.0 | 40.0 |  | 73.51 | 128.56 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 000 | N | 1021
JWR24007 | 08 | 32 | 6" | JWR | 24007 | D20S1 | N | 0 | 32-E-2403 | JWR24008 | 49.0/49.0 | -45.0/150.0 | 5.0 | 40.0 |  | 73.51 | 128.56 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.20 | 2 | II | MOD.A2 | Y | 1 | Y | 32-U-022-02 |  | M | N | 000 | N | 1021
PR72017 | 08 | 32 | 1-1/2" | PR | 72017 | C42S1 | N | 0 | 32-T-7201 | BDL72036 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72017 | 08 | 32 | 4" | PR | 72017 | C42S1 | N | 0 | 32-T-7201 | BDL72036 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72018 | 08 | 32 | 1/2" | PR | 72018 | C42S1 | N | 0 | PR72028 | BDL72024 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
VZ24003 | 08 | 32 | 2" | VZ | 24003 | C42S1 | N | 0 | 32-T-2401 | - | 42.0/42.0 | 150.0/-45.0 | 32.0/32.0 | 75.0/40.0 |  | 0 | 0 | V | VESSEL TRIM | LG | - | - | >1.5 | 40 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | G | Y | 141 | N | 514 | 10
VZ24004 | 08 | 32 | 1-1/2" | VZ | 24004 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
VZ24006 | 08 | 32 | 3/4" | VZ | 24006 | D20S1 | HB | 30 | 32-T-2400 | - | 48.0/48.0 | 150.0/-45.0 | 35.0/35.0 | 80.0/55.0 |  | 72.01 | 153.15 | H | VESSEL TRIM | L | - | - | >1.5 | 55 | sh.20 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 508 | 15
VZ31007 |  | 32 | 1-1/2" | VZ | 31007 | C42S1 | HB | 30 | 32-S-3101A | O31016 | 25.0/25.0 | 190.0/-45.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.23 | 1 | I | MOD.A | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 365 | 10
VZ32002 |  | 32 | 1" | VZ | 32002 | C42S1 | HB | 30 | 32-D-3200 | HCM32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
VZ33002 | 08 | 32 | 3/4" | VZ | 33002 | C42S1 | N | 0 | 32-D-3300 | 32-D-3300 | 25.0/25.0 | 120.0/-45.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 45 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 384 | 15
VZ33002 | 08 | 32 | 1-1/2" | VZ | 33002 | C42S1 | N | 0 | 32-D-3300 | 32-D-3300 | 25.0/25.0 | 120.0/-45.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 45 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 384 | 15
VZ34003 |  | 32 | 3/4" | VZ | 34003 | B32S1 | P | 50 | 32-S-3400 | PR34019 | 5.0/5.0 | 120.0/-45.0 | 0.6 | 80.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | GS | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | G | N | 141 | N | 425 | ,10
VZ34003 |  | 32 | 1-1/2" | VZ | 34003 | B32S1 | P | 50 | 32-S-3400 | PR34019 | 5.0/5.0 | 120.0/-45.0 | 0.6 | 80.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | GS | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | G | N | 141 | N | 425 | ,10
VZ34004 | 08 | 32 | 2" | VZ | 34004 | B4S1 | HB | 30 | 32-D-3400 | - | 8.0/8.0 | 250.0/0.0 | 5.0 | 80.0 |  | 12.52 | 29.4 | H | VESSEL TRIM | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 379 | 10
VZ35002 | 08 | 32 | 1" | VZ | 35002 | B4S1 | N | 0 | 32-D-3500 | 32-D-3500 | 5.0 | 120.0 | 0.5 | 45.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | G | - | - | >1.5 | 45 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 378 | ,10
DW69A05 | 08 | 32 | 1-1/2" | DW | 69A05 | B-13 | IS | 50 | DW69A03 | 32-ES-6905 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B14 | 08 | 32 | 1-1/2" | DW | 69B14 | B-13 | N | 0 | DW01001 | 32-ES-6910 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
LC63073 |  | 32 | 1-1/2" | LC | 63073 | B-5 | HB | 40 | HEADER | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63147 |  | 32 | 1/2" | LC | 63147 | B-5 | HB | 30 | LS23030 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC66001 |  | 32 | 3/4" | LC | 66001 | B-5 | HB | 30 | LS66001 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
CD34009 | 08 | 32 | 1/2" | CD | 34009 | 1CS2 | ET | 30 | CD34008 | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34009 | 08 | 32 | 3/4" | CD | 34009 | 1CS2 | ET | 30 | CD34008 | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
JWS52004 | 08 | 32 | 3/4" | JWS | 52004 | B-1 | N | 0 | JWS52003 | 32-E-5252B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS61002 | 08 | 32 | 1-1/2" | JWS | 61002 | B-1 | N | 0 | JWS64061 | TP-006 (JWS610200) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.42C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64001 | 08 | 32 | 1-1/2" | JWS | 64001 | B-1 | N | 0 | 32-E-6400A | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64007 | 08 | 32 | 1-1/2" | JWS | 64007 | B-1 | N | 0 | JWS64004 | 32-P-6400B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64008 | 08 | 32 | 3/4" | JWS | 64008 | UGB-1PE | N | 0 | JWS64009 | JWS64054 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
JWS64008 | 08 | 32 | 1" | JWS | 64008 | UGB-1PE | N | 0 | JWS64009 | JWS64054 | 9.0 | 80.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-01 |  | E | N | 000 | N | 18
JWS64009 | 08 | 32 | 3/4" | JWS | 64009 | B-1 | N | 0 | 32-P-6400B | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64009 | 08 | 32 | 14" | JWS | 64009 | B-1 | N | 0 | 32-P-6400B | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64024 | 08 | 32 | 3/4" | JWS | 64024 | B-1 | N | 0 | JWS64054 | 32-E-3500 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
BDL72052 | 08 | 32 | 2" | BDL | 72052 | B32S1 | N | 0 | PR72052 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72069 | 08 | 32 | 1" | BDL | 72069 | B32S1 | N | 0 | PR72064 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72069 | 08 | 32 | 4" | BDL | 72069 | B32S1 | N | 0 | PR72064 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL73043 | 08 | 32 | 1/2" | BDL | 73043 | B4S1 | N | 0 | BU73053 | BDL73044 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BU73045 | 08 | 32 | 1" | BU | 73045 | B32S1 | N | 0 | BU73047 | JLS73005 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
LC63027 |  | 32 | 1-1/2" | LC | 63027 | B-5 | P | 50 | LC63034 | 32-D-6100 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63027 |  | 32 | 2" | LC | 63027 | B-5 | P | 50 | LC63034 | 32-D-6100 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63028 |  | 32 | 3/4" | LC | 63028 | B-5 | P | 50 | LC63034 | JWR64006 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63028 |  | 32 | 2" | LC | 63028 | B-5 | P | 50 | LC63034 | JWR64006 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63029 |  | 32 | 1-1/2" | LC | 63029 | B-5 | P | 50 | LC63059 | LC63040 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63030 |  | 32 | 2" | LC | 63030 | B-5 | P | 50 | 32-D-6300 | LC63040 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63031 |  | 32 | 6" | LC | 63031 | B-5 | P | 50 | 32-D-6300 | LC63041 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63032 |  | 32 | 4" | LC | 63032 | B-5 | P | 50 | LC63031 | 32-P-6300A | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 136
LC63033 |  | 32 | 1-1/2" | LC | 63033 | B-5 | P | 50 | 32-P-6300A | LC63034 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63034 |  | 32 | 3/4" | LC | 63034 | B-5 | P | 50 | 32-P-6300B | LC63035 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63034 |  | 32 | 2" | LC | 63034 | B-5 | P | 50 | 32-P-6300B | LC63035 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63034 |  | 32 | 3" | LC | 63034 | B-5 | P | 50 | 32-P-6300B | LC63035 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63037 |  | 32 | 3" | LC | 63037 | B-5 | P | 50 | LC63036 | SC500001 OSBL LINE | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63038 |  | 32 | 1/2" | LC | 63038 | B-5 | P | 50 | 32-D-6300 | 32-D-6300 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63038 |  | 32 | 1" | LC | 63038 | B-5 | P | 50 | 32-D-6300 | 32-D-6300 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63040 |  | 32 | 4" | LC | 63040 | B-5 | P | 50 | 32-D-6300 | ACW | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63041 |  | 32 | 4" | LC | 63041 | B-5 | P | 50 | LC63031 | LC63042 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63042 |  | 32 | 3/4" | LC | 63042 | B-5 | P | 50 | LC63041 | 32-P-6300B | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 136
LC63042 |  | 32 | 4" | LC | 63042 | B-5 | P | 50 | LC63041 | 32-P-6300B | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 136
P40032 |  | 32 | 10" | P | 40032 | C42S2 | ET | 40 | P40041 | VZ40006 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40035 |  | 32 | 3" | P | 40035 | C42S2 | ET | 30 | 32-R-4001 | P40037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40036 |  | 32 | 2" | P | 40036 | C42S2 | ET | 30 | 32-R-4001 | P40037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40037 |  | 32 | 3" | P | 40037 | C42S2 | P | 50 | P40034 | P40038 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40038 |  | 32 | 8" | P | 40038 | C42S2 | P | 75 | P40037 | P34003 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40039 | 08 | 32 | 1-1/2" | P | 40039 | C42S2 | N | 0 | P40025 | P40040 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40040 |  | 32 | 1-1/2" | P | 40040 | C42S2 | P | 50 | P40025 | P40037 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40040 |  | 32 | 3" | P | 40040 | C42S2 | P | 50 | P40025 | P40037 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
LO32001 | 08 | 32 | 1-1/2" | LO | 32001 | QXB-55 | N | 0 | TP-20A, LO320114 (LO320313) | TP-19A, PK-3600, COMPRESSOR INTERNAL PIPE | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO89008 | 08 | 32 | 3/4" | LO | 89008 | QXB-55 | N | 0 | TP-N20352 (32-Z-8900) | TP-N20452 (32-P-8902B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LO89008 | 08 | 32 | 6" | LO | 89008 | QXB-55 | N | 0 | TP-N20352 (32-Z-8900) | TP-N20452 (32-P-8902B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LPN10005 | 08 | 32 | 2" | LPN | 10005 | 3DS3 | N | 0 | N10006 | PK-1001 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10015 | 08 | 32 | 1/2" | LPN | 10015 | 3DS3 | N | 0 | LPN10001 | 32-D-1001 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
FW68A0A | 08 | 45 | 6" | FW | 68A0A | UGB-1PE | N | 0 | FW68A29 | FW68A0B | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0K | 08 | 45 | 6" | FW | 68A0K | UGB-1PE | N | 0 | FW68A47 | 45-HM-6805 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0W | 08 | 45 | 6" | FW | 68A0W | B-13 | N | 0 | FW68A0D | 45-EM-6802 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68A17 | 08 | 45 | 18" | FW | 68A17 | PEB-69 | N | 0 | FW68A03 | FW68B02 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A26 | 08 | 45 | 1" | FW | 68A26 | B-13 | N | 0 | FW68A34 | FOR HOSE REEL ON THE STRUCTURE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A26 | 08 | 45 | 2" | FW | 68A26 | B-13 | N | 0 | FW68A34 | FOR HOSE REEL ON THE STRUCTURE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A34 | 08 | 45 | 2" | FW | 68A34 | B-13 | N | 0 | FW68A97 | FOR HOSE REEL ON THE STRUCTURE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A34 | 08 | 45 | 6" | FW | 68A34 | B-13 | N | 0 | FW68A97 | FOR HOSE REEL ON THE STRUCTURE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A53 | 08 | 45 | 10" | FW | 68A53 | PEB-69 | N | 0 | FW68B03 | FW68B93 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A56 | 08 | 45 | 8" | FW | 68A56 | B-7 | N | 0 | FW68B92 | FW68D09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A66 | 08 | 45 | 3/4" | FW | 68A66 | B-7 | N | 0 | FW68A0H | FW68C01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A68 | 08 | 45 | 3/4" | FW | 68A68 | B-7 | N | 0 | FW68A0I | FW68C01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A73 | 08 | 45 | 1-1/2" | FW | 68A73 | B-13 | N | 0 | FW68A34 | 45-HR-6853 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
VA52011 | 08 | 32 | 3/4" | VA | 52011 | B4S2 | N | 0 | 32-Z-5202B | ACW | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA52015 | 08 | 32 | 1" | VA | 52015 | B4S2 | N | 0 | JWR52001 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-U-022-01 |  | E | N | 000 | N | 183
VA52016 | 08 | 32 | 4" | VA | 52016 | B4S2 | N | 0 | PN52030 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA61001 | 08 | 32 | 3" | VA | 61001 | B4S2 | N | 0 | VA61005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA61002 | 08 | 32 | 1" | VA | 61002 | B4S2 | N | 0 | VA61005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA61005 | 08 | 32 | 1" | VA | 61005 | B4S2 | N | 0 | 32-D-6100 | VA61001 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA62002 | 08 | 32 | 2" | VA | 62002 | B4S2 | N | 0 | IA62091 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.43 | 2 | NA | NA | NA | 6 | N | 32-U-094-02 |  | E | N | 000 | N | 183
VA62003 | 08 | 32 | 3" | VA | 62003 | B4S2 | N | 0 | IA62092 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.43 | 2 | NA | NA | NA | 6 | N | 32-U-094-01 |  | E | N | 000 | N | 183
VA62005 | 08 | 32 | 2" | VA | 62005 | 1CS2 | N | 0 | TP-03 (VA620118) | VENT TO SAFE LOCATION | 0.5 | 80.0 | 0.05 | 40.0 |  | .55 | 25.65 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.43B | 2 | NA | NA | NA | NR | N | 32-U-094-03 |  | M | N | 000 | N | 182
HCM23069 |  | 32 | 4" | HCM | 23069 | C42S1 | HB | 40 | HCM23004 | P23017 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23071 |  | 32 | 3/4" | HCM | 23071 | 3FS4 | HB | 30 | HCM24061 | PR23012 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23076 |  | 32 | 1/2" | HCM | 23076 | 3FS4 | HB | 30 | HCM23072 | PR24045 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.15 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23077 | 08 | 32 | 1/2" | HCM | 23077 | C42S1 | HB | 30 | HCM23069 | LA21003 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15A | 1 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23087 | 08 | 32 | 1/2" | HCM | 23087 | D20S1 | HB | 30 | HCM23084 | 32-HV-2303A | 55.0/55.0 | 280.0/-45.0 | 30.0 | 100.0 |  | 88.69 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15A | 1 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 321 | 10
PA62033 | 08 | 32 | 3/4" | PA | 62033 | B-1 | N | 0 | PA62035 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
BDL73040 | 08 | 32 | 1" | BDL | 73040 | B4S1 | N | 0 | BU73087 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73049 | 08 | 32 | 1/2" | BDL | 73049 | B4S1 | N | 0 | BU73086 | BDL60024 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BU01001 | 08 | 32 | 3/4" | BU | 01001 | B32S1 | N | 0 | BU01003 | 32-S-7302B | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.1 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-01 |  | F | N | 140 | N | 731 | 15
PR35021 | 08 | 32 | 1-1/2" | PR | 35021 | B4S1 | N | 0 | 32-D-3500 | PR35020 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR36012 |  | 32 | 3" | PR | 36012 | C42S1 | P | 50 | PR36013 | PR35013 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | III | MOD.G | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36019 | 08 | 32 | 2" | PR | 36019 | B4S1 | P | 50 | D-3602 | TP-186, PSV-3684 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
PR36019 | 08 | 32 | 6" | PR | 36019 | B4S1 | P | 50 | D-3602 | TP-186, PSV-3684 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
PR36022 |  | 32 | 1-1/2" | PR | 36022 | C42S1 | P | 50 | PR36028 | PR36014 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36025 | 08 | 32 | 10" | PR | 36025 | B4S1 | N | 0 | PR36026 | TP-103 (32-D-3603, 32-FO-3656) | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28A | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
IA68R06 | 08 | 45 | 1" | IA | 68R06 | B-13 | N | 0 | IA68R02 | To Air Maintenance Device | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
PR72018 | 08 | 32 | 1" | PR | 72018 | C42S1 | N | 0 | PR72028 | BDL72024 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72018 | 08 | 32 | 2" | PR | 72018 | C42S1 | N | 0 | PR72028 | BDL72024 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72020 | 08 | 32 | 3/4" | PR | 72020 | C42S1 | N | 0 | TP-014 (PR720106) | 32-S-7201A | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52D | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72022 | 08 | 32 | 1/2" | PR | 72022 | C42S1 | N | 0 | 32-T-7203 | TP-014 (PR720101) | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72022 | 08 | 32 | 1" | PR | 72022 | C42S1 | N | 0 | 32-T-7203 | TP-014 (PR720101) | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72024 | 08 | 32 | 1" | PR | 72024 | C42S1 | N | 0 | PR72020 | 32-S-7201B | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72025 | 08 | 32 | 6" | PR | 72025 | C42S1 | N | 0 | 32-S-7201B | BDL72049 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72027 | 08 | 32 | 1/2" | PR | 72027 | C42S1 | N | 0 | HEADER | BDL72030 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72027 | 08 | 32 | 1" | PR | 72027 | C42S1 | N | 0 | HEADER | BDL72030 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72027 | 08 | 32 | 2" | PR | 72027 | C42S1 | N | 0 | HEADER | BDL72030 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72028 | 08 | 32 | 1/2" | PR | 72028 | C42S1 | N | 0 | 32-D-7200 | PR72018 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72028 | 08 | 32 | 1" | PR | 72028 | C42S1 | N | 0 | 32-D-7200 | PR72018 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72028 | 08 | 32 | 2" | PR | 72028 | C42S1 | N | 0 | 32-D-7200 | PR72018 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72037 | 08 | 32 | 1-1/2" | PR | 72037 | C42S1 | N | 0 | PR72017 | BDL72032 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72037 | 08 | 32 | 6" | PR | 72037 | C42S1 | N | 0 | PR72017 | BDL72032 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72038 | 08 | 32 | 1" | PR | 72038 | C42S1 | N | 0 | PR72009 | BDL72023 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72039 | 08 | 32 | 1" | PR | 72039 | C42S1 | N | 0 | PR72015 | BDL72034 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72040 | 08 | 32 | 3/4" | PR | 72040 | C42S1 | N | 0 | PR72009 | BDL72020 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
VZ50011 |  | 32 | 3/4" | VZ | 50011 | B4S2 | HB | 30 | 32-T-5001 | 32-T-5001 | 5.0/-1.0 | 180.0/180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 28
VZ51004 | 08 | 32 | 1/2" | VZ | 51004 | B4S1 | ST | 30 | 32-D-5102 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ62002 | 08 | 32 | 3/4" | VZ | 62002 | C3S1 | N | 0 | 32-D-6200 | - | 28.0 | 150.0 | 25.0 | 30.0 |  | 37.24 | 68.99 | P | VESSEL TRIM | G | - | - | >1.5 | 30 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 204
VZ65003 |  | 32 | 1/2" | VZ | 65003 | B4S2 | ET | 30 | 32-D-6500 | 32-D-6500 | 3.5 | 180.0 | 0.05/0.05 | 100.0/30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 230 | 23,25
VZ65003 |  | 32 | 1-1/2" | VZ | 65003 | B4S2 | HH | 30 | 32-D-6500 | 32-D-6500 | 3.5 | 180.0 | 0.05/0.05 | 100.0/30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 230 | 23,25
BDL23043 | 08 | 32 | 1-1/2" | BDL | 23043 | B32S1 | N | 0 | BDL23025 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23046 |  | 32 | 6" | BDL | 23046 | B32S1 | SB | 100 | HCM23058 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23068 | 08 | 32 | 1/2" | BDL | 23068 | B32S1 | N | 0 | P23030 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24067 | 08 | 32 | 1/2" | BDL | 24067 | B32S1 | N | 0 | BDL24066 | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24069 | 08 | 32 | 3/4" | BDL | 24069 | B32S1 | N | 0 | BDL24078 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24094 | 08 | 32 | 3/4" | BDL | 24094 | B32S1 | N | 0 | PR24046 | BDL24092 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24099 | 08 | 32 | 1" | BDL | 24099 | B32S1 | N | 0 | HCM24099 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
JWS64031 | 08 | 32 | 1" | JWS | 64031 | B-1 | N | 0 | JWS64054 | 32-E-5201 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64059 | 08 | 32 | 1" | JWS | 64059 | B-1 | N | 0 | JWS64054 | JWS64020 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64072 | 08 | 32 | 2" | JWS | 64072 | B-1 | N | 0 | JWS64054 | JWS64048 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64073 | 08 | 32 | 1-1/2" | JWS | 64073 | B-1 | N | 0 | JWS64004 | 32-P-6400A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.9 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
LA16001 |  | 32 | 1-1/2" | LA | 16001 | 4CS2 | ET | 30 | ADDITIVE DRUM | LA16022 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16022 |  | 32 | 3/4" | LA | 16022 | 4CS2 | HH | 30 | LA16001 | 32-P-1601 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16022 |  | 32 | 1-1/2" | LA | 16022 | 4CS2 | HH | 30 | LA16001 | 32-P-1601 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16026 |  | 32 | 2" | LA | 16026 | 1FS4 | ET | 30 | LA16025 | LA16027 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16028 |  | 32 | 3/4" | LA | 16028 | 1FS4 | ET | 30 | LA16030 | 32-P-1600B | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16029 |  | 32 | 1" | LA | 16029 | 1FS4 | ET | 30 | LA16019 | LA16030 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA23004 |  | 32 | 1/2" | LA | 23004 | 1FS4 | ET | 30 | LA23006 | PR24039 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.16 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
BU73047 | 08 | 32 | 3/4" | BU | 73047 | B32S1 | N | 0 | 32-S-7302A | 32-D-7302 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73047 | 08 | 32 | 2" | BU | 73047 | B32S1 | N | 0 | 32-S-7302A | 32-D-7302 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
CD31005 | 08 | 32 | 1" | CD | 31005 | 1CS2 | N | 0 | 32-SP-04-13100-03 | HCM31020 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | F | N | 100 | N | 288
CD34008 | 08 | 32 | 1/2" | CD | 34008 | 1IS5 | N | 0 | 32-E-3400 | CD34009 | 130.0 | 150.0 | 50.0 | 80.0 |  | 75 | 75 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 80 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 292
CD34014 | 08 | 32 | 1/2" | CD | 34014 | 1CS2 | ET | 30 | 32-SP-04-13400-06 | CD34009 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
N16011 | 08 | 32 | 3/4" | N | 16011 | 1CS2 | N | 0 | N16010 | 32-D-1602 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N16012 |  | 32 | 3/4" | N | 16012 | 1CS2 | ET | 30 | 32-D-1601 | N16011 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | NR | N | 32-P-023-01 |  | M | N | 000 | N | 154
N22001 | 08 | 32 | 1" | N | 22001 | B-1 | N | 0 | NITROGEN CONNECTION | 32-D-2202 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.13 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 140
N32004 | 08 | 32 | 1-1/2" | N | 32004 | B4S1 | N | 0 | TP-24A, (CYLINDER) | TP-35A, (D-3204) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32008 | 08 | 32 | 1" | N | 32008 | B4S1 | N | 0 | 32-FT-3256 | TP-31A, (32-D-3203) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32008 | 08 | 32 | 2" | N | 32008 | B4S1 | N | 0 | 32-FT-3256 | TP-31A, (32-D-3203) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32020 | 08 | 32 | 2" | N | 32020 | B4S1 | N | 0 | TP-31B, (32-D-3203B) | N32019 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N32024 | 08 | 32 | 1" | N | 32024 | B-1 | N | 0 | N | HCM32024 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.24G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-02 |  | E | N | 000 | N | 140
N32025 | 08 | 32 | 1/2" | N | 32025 | B4S1 | N | 0 | TP-41B, (32-D-3203B) | N32022 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 000 | N | 148
N36005 | 08 | 32 | 1" | N | 36005 | B4S1 | N | 0 | TP-167 (CYLINDER 1, STAGE 1, PACKING 1, C46) | TO TEMPORARY TANK | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36006 | 08 | 32 | 1-1/2" | N | 36006 | B4S1 | N | 0 | TP-165 (CYLINDER 1, STAGE 1, PACKING 1, C97) | TP-182 (32-D-3609) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36010 | 08 | 32 | 1-1/2" | N | 36010 | B4S1 | N | 0 | TP-176 (CYLINDER 3, STAGE 1, PACKING 3, C58) | N36006 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
LC63059 |  | 32 | 4" | LC | 63059 | B-5 | P | 50 | LC01001 | 32-D-6300 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | I | MOD.A | Y | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63059 |  | 32 | 8" | LC | 63059 | B-5 | P | 75 | LC01001 | 32-D-6300 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | I | MOD.A | Y | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63075 |  | 32 | 3/4" | LC | 63075 | B-5 | HB | 30 | LS63186 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63076 |  | 32 | 3/4" | LC | 63076 | B-5 | HB | 30 | LS63185 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63081 |  | 32 | 1-1/2" | LC | 63081 | B-5 | HB | 40 | 32-1121-R-002 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63085 |  | 32 | 1-1/2" | LC | 63085 | B-5 | HB | 40 | LC24015 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63088 |  | 32 | 2" | LC | 63088 | B-5 | P | 50 | HEADER | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63092 |  | 32 | 3" | LC | 63092 | B-5 | HB | 50 | HEADER | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC630AA |  | 32 | 3/4" | LC | 630AA | B-5 | HB | 30 | LC6300J | 32-1121-S-001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC630AB |  | 32 | 3/4" | LC | 630AB | B-5 | HB | 30 | 32-1121-S-002 | LC23019 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC630AC |  | 32 | 3/4" | LC | 630AC | B-5 | HB | 30 | LC34006 | 32-1121-S-004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC630AD |  | 32 | 3/4" | LC | 630AD | B-5 | HB | 30 | 32-1121-S-006 | LC23021 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63101 |  | 32 | 3/4" | LC | 63101 | B-5 | HB | 30 | LS63009 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65001 |  | 32 | 3/4" | LC | 65001 | B-5 | HB | 30 | LS65003 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65002 |  | 32 | 1-1/2" | LC | 65002 | B-5 | HB | 40 | LS65001 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65006 |  | 32 | 3/4" | LC | 65006 | B-5 | HB | 30 | LS65001 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | Y | 000 | N | 130
LC66001 |  | 32 | 1" | LC | 66001 | B-5 | HB | 40 | LS66001 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
P40041 |  | 32 | 1" | P | 40041 | C42S2 | ET | 30 | 32-R-4001 | Z-4003 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40041 |  | 32 | 6" | P | 40041 | C42S2 | ET | 30 | 32-R-4001 | Z-4003 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40046 |  | 32 | 1" | P | 40046 | C42S1 | HB | 30 | P40025 | P40032 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
P50002 | 08 | 32 | 12" | P | 50002 | 1CR9 | P | 100 | 32-D-5001 | P50012 | 5.0/5.0 | 200.0/-45.0 | 0.6 | 80.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 430 | DELETED
P50015 |  | 32 | 1" | P | 50015 | 1CR9 | HB | 30 | 32-D-5001 | LC50007 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P50016 |  | 32 | 1" | P | 50016 | 1CR9 | HB | 30 | 32-D-5001 | LC50005 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P50016 |  | 32 | 2" | P | 50016 | 1CR9 | HB | 40 | 32-D-5001 | LC50005 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P50017 | 08 | 32 | 3" | P | 50017 | 1CR9 | N | 0 | 32-J-5001 | 32-D-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P52010 |  | 32 | 3" | P | 52010 | 1CR9 | P | 50 | 32-A-5200 | 32-D-5200 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.37 | 1 | III | MOD.G | Y | NR | N | 32-P-052-02 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P52010 |  | 32 | 20" | P | 52010 | 1CR9 | P | 100 | 32-A-5200 | 32-D-5200 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.37 | 1 | III | MOD.G | Y | NR | Y | 32-P-052-02 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
LPN11011 | 08 | 32 | 1/2" | LPN | 11011 | 1CS2 | N | 0 | LPN02004 | FO11003 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | F | N | 343 | N | 167 | 8,29,23,25
SWW92025 | 08 | 32 | 3" | SWW | 92025 | 1CS2 | N | 0 | SWW92011 | 32-H-9001A | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92026 | 08 | 32 | 1-1/2" | SWW | 92026 | 1CS2 | N | 0 | 32-H-9001B | SWW92012 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92027 | 08 | 32 | 3" | SWW | 92027 | 1CS2 | N | 0 | 32-H-9001C | SWW92013 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92028 | 08 | 32 | 3" | SWW | 92028 | 1CS2 | N | 0 | SWW92014 | 32-H-9001D | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92029 | 08 | 32 | 3" | SWW | 92029 | 1CS2 | N | 0 | SWW92015 | 32-H-9001E | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92031 | 08 | 32 | 2" | SWW | 92031 | 1CS2 | N | 0 | 32-S-9015 | 32-D-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92032 | 08 | 32 | 8" | SWW | 92032 | 1CS2 | N | 0 | 32-S-9005 | 32-D-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
FW68A86 | 08 | 45 | 10" | FW | 68A86 | B-7 | N | 0 | FW68A0M | FW68S11 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B0A | 08 | 45 | 6" | FW | 68B0A | UGB-1PE | N | 0 | FW68B27 | FW68B28 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0F | 08 | 45 | 6" | FW | 68B0F | UGB-1PE | N | 0 | FW68B87 | 45-HY-6825 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0G | 08 | 45 | 8" | FW | 68B0G | UGB-1PE | N | 0 | FW68B44 | FW68B43 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0H | 08 | 45 | 10" | FW | 68B0H | UGB-1PE | N | 0 | FW68B47 | FW68B48 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0J | 08 | 45 | 10" | FW | 68B0J | UGB-1PE | N | 0 | FW68B49 | FW68B50 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0M | 08 | 45 | 8" | FW | 68B0M | UGB-1PE | N | 0 | FW68B35 | FW68B36 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B36 | 08 | 45 | 2" | FW | 68B36 | B-7 | N | 0 | FW68B0M | SPRINKLER SYSTEM FOR PEL EXTRUSION | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-01 |  | E | N | 000 | N | 75
FW68B36 | 08 | 45 | 6" | FW | 68B36 | B-7 | N | 0 | FW68B0M | SPRINKLER SYSTEM FOR PEL EXTRUSION | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-01 |  | E | N | 000 | N | 75
FW68B44 | 08 | 45 | 8" | FW | 68B44 | PEB-69 | N | 0 | FW68A03 | FW68B0G | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B50 | 08 | 45 | 8" | FW | 68B50 | B-7 | N | 0 | FW68B0J | FW68R07 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B76 | 08 | 45 | 1-1/2" | FW | 68B76 | B-7 | N | 0 | FW68B15 | 45-HR-6818 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B91 | 08 | 45 | 1-1/2" | FW | 68B91 | B-7 | N | 0 | FW68B27 | 45-HR-6824 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C01 | 08 | 32 | 2" | FW | 68C01 | B-7 | N | 0 | FW68A68 | FW68C04 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C01 | 08 | 32 | 12" | FW | 68C01 | B-7 | N | 0 | FW68A68 | FW68C04 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C03 | 08 | 32 | 4" | FW | 68C03 | B-7 | N | 0 | FW68C01 | 32-XV-6802A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C09 | 08 | 32 | 6" | FW | 68C09 | B-13 | N | 0 | 32-XV-6810A | FW68Q01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68D02 | 08 | 45 | 4" | FW | 68D02 | B-7 | N | 0 | FW68D09 | 45-XV-6816A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D03 | 08 | 45 | 4" | FW | 68D03 | B-7 | N | 0 | FW68D09 | 45-XV-6817A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
VA64001 | 08 | 32 | 1" | VA | 64001 | B4S2 | N | 0 | CWR64014 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.44 | 2 | NA | NA | NA | 6 | N | 32-U-021-01 |  | E | N | 000 | N | 183
LO32008 | 08 | 32 | 1/2" | LO | 32008 | QXB-55 | N | 0 | TP-15B (32-P-3201B) | TP-16B (LO320108) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
PA62059 | 08 | 32 | 3/4" | PA | 62059 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62075 | 08 | 32 | 1/2" | PA | 62075 | B-1 | N | 0 | PA62053 | PA12010 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62076 | 08 | 32 | 3/4" | PA | 62076 | B-1 | N | 0 | PA01001 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62089 | 08 | 32 | 3/4" | PA | 62089 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62091 | 08 | 32 | 3/4" | PA | 62091 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89023 | 08 | 32 | 3/4" | PA | 89023 | B-1 | N | 0 | PA89021 | US-5111-01 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89047 | 08 | 32 | 3/4" | PA | 89047 | B-1 | N | 0 | PA89021 | US-3211-05 EL.10000 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
BU73043 |  | 32 | 4" | BU | 73043 | B32S1 | HB | 30 | 32-D-7302 | BDL73078 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73049 | 08 | 32 | 1/2" | BU | 73049 | B32S1 | N | 0 | 32-D-7302 | 32-P-7300 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73049 | 08 | 32 | 3/4" | BU | 73049 | B32S1 | N | 0 | 32-D-7302 | 32-P-7300 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73049 | 08 | 32 | 2" | BU | 73049 | B32S1 | N | 0 | 32-D-7302 | 32-P-7300 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73049 | 08 | 32 | 4" | BU | 73049 | B32S1 | N | 0 | 32-D-7302 | 32-P-7300 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73051 | 08 | 32 | 1" | BU | 73051 | D20S1 | N | 0 | 32-P-7300 | BU73053 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73051 | 08 | 32 | 2" | BU | 73051 | D20S1 | N | 0 | 32-P-7300 | BU73053 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73081 | 08 | 32 | 1-1/2" | BU | 73081 | B32S1 | N | 0 | 32-S-7302B | BDL73048 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73083 | 08 | 32 | 3/4" | BU | 73083 | B32S1 | N | 0 | 32-S-7302B | BDL73050 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
VZ01003 | 08 | 32 | 3/4" | VZ | 01003 | 3FS4 | N | 0 | 32-S-0101 | BDL01037 | 45.0 | 100.0 | 40.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | G | - | - | >1.5 | 40 | sh.1 | 1 | Art 4.3 | NA | N | NR | N | 32-P-002-01 |  | F | Y | 040 | N | 290 | 5,23,10,25,36
IA71005 | 08 | 32 | 3/4" | IA | 71005 | B-13 | N | 0 | IA62056 | N72008 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.48 | 2 | Art 4.3 | NA | N | 4 | N | 32-P-007-05 |  | - | N | 000 | - | 200
IA71005 | 08 | 32 | 1" | IA | 71005 | B-13 | N | 0 | IA62056 | N72008 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.48 | 2 | Art 4.3 | NA | N | 4 | N | 32-P-007-05 |  | - | N | 000 | - | 200
IA89039 | 08 | 32 | 1" | IA | 89039 | B-13 | N | 0 | IA62006 | CAP | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89046 | 08 | 32 | 1/2" | IA | 89046 | B-13 | N | 0 | IA89047 | TP-N50405 (A-8900 PCV-8959) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.68M | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89073 | 08 | 32 | 1" | IA | 89073 | B-13 | N | 0 | IA89054 | 32-IAM-148 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89077 | 08 | 32 | 1" | IA | 89077 | B-13 | N | 0 | IA89076 | TO 32-IAM-511 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
PR72041 | 08 | 32 | 1" | PR | 72041 | C42S1 | N | 0 | 32-S-7201B | BDL72047 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72042 | 08 | 32 | 1" | PR | 72042 | C42S1 | N | 0 | PR72015 | BDL72039 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72043 | 08 | 32 | 1-1/2" | PR | 72043 | C42S1 | N | 0 | PR72015 | BDL72039 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72044 | 08 | 32 | 1-1/2" | PR | 72044 | C42S1 | N | 0 | 32-S-7201A | BDL72045 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72045 | 08 | 32 | 1" | PR | 72045 | C42S1 | N | 0 | 32-S-7201A | BDL72046 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72047 | 08 | 32 | 1" | PR | 72047 | C42S1 | N | 0 | 32-S-7201B | BDL72048 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72050 | 08 | 32 | 2" | PR | 72050 | C42S1 | N | 0 | 32-D-7201 | BDL72026 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72051 | 08 | 32 | 1" | PR | 72051 | C42S1 | N | 0 | N67048 | 32-D-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72052 | 08 | 32 | 2" | PR | 72052 | C42S1 | N | 0 | PR72014 | BDL72052 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72053 | 08 | 32 | 1/2" | PR | 72053 | C42S1 | N | 0 | PR72022 | BDL72076 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PR72060 | 08 | 32 | 1" | PR | 72060 | C42S1 | HA | 30 | TP-023 (PR720161) | BDL72072 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PR72061 | 08 | 32 | 1/2" | PR | 72061 | C42S1 | N | 0 | PR72015 | BDL72031 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72064 | 08 | 32 | 3" | PR | 72064 | C42S1 | N | 0 | TP-017 (PR720132) | BDL72069 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | II | MOD.A2 | Y | 7 | Y | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72065 | 08 | 32 | 3/4" | PR | 72065 | C42S1 | N | 0 | TP-019 (PR720130) | BDL72071 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52C | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PR72066 | 08 | 32 | 2" | PR | 72066 | C42S1 | N | 0 | TP-018 (PR720115) | BDL72070 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | II | MOD.A2 | Y | 7 | Y | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72069 | 08 | 32 | 1" | PR | 72069 | C42S1 | N | 0 | PR72064 | BDL72069 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | Art 4.3 | NA | N | 7 | N | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72070 | 08 | 32 | 1" | PR | 72070 | C42S1 | N | 0 | PR72066 | BDL72070 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | Art 4.3 | NA | N | 7 | N | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72072 | 08 | 32 | 1" | PR | 72072 | C42S1 | N | 0 | PR72066 | BDL72070 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | Art 4.3 | NA | N | 7 | N | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
VZ66004 | 08 | 32 | 1" | VZ | 66004 | B4S2 | HH | 30 | 32-D-6600 | - | 3.5 | 180.0 | 0.0 | 30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 233 | 23,25
VZ71007 | 08 | 32 | 3/4" | VZ | 71007 | QXC25S1 | ET | 30 | 32-S-7100B | - | 38.3 | 120.0 | 28.0 | 40.0 |  | 57.45 | 74.4 | H | VESSEL TRIM | G | - | - | >1.5 | 40 | sh.49 | 1 | Art 4.3 | NA | N | NR | N | 32-P-006-03 |  | G | N | 041 | N | 327 | ,10
VZ72024 | 08 | 32 | 1-1/2" | VZ | 72024 | C42S1 | N | 0 | 32-T-7201 | - | 43.7/43.7 | 150.0/-45.0 | 25.0 | 61.0 |  | 65.56 | 76.65 | H | VESSEL TRIM | L | - | - | >1.5 | 61 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 413 | ,15
VZ72025 | 08 | 32 | 1" | VZ | 72025 | C42S1 | N | 0 | 32-T-7203 | PR72022 | 43.7/43.7 | 150.0/-45.0 | 23.5 | 40.0 |  | 65.56 | 76.65 | H | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 431 | ,15
VZ73007 |  | 32 | 1" | VZ | 73007 | B32S1 | HE | 30 | 32-D-7302 | 32-D-7302 | 14.0/14.0 | 80.0/-7.0 | 5.0 | 50.0 |  | 21 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 50 | sh.55 | 1 | I | MOD.A | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 730 | 15
VZ92002 | 08 | 32 | 4" | VZ | 92002 | 1CS2 | N | 0 | 32-D-9005 | 32-D-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | NR | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
BDL31027 | 08 | 32 | 3/4" | BDL | 31027 | B32S1 | N | 0 | P31012 | BDL34016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31041 | 08 | 32 | 1" | BDL | 31041 | B32S1 | N | 0 | HCM31015 | BDL31030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32023 | 08 | 32 | 1/2" | BDL | 32023 | B32S1 | N | 0 | HCM32027 | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32037 | 08 | 32 | 2" | BDL | 32037 | B32S1 | N | 0 | TP-04B (32-D-3202B) | BDL32036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24G | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL33001 | 08 | 32 | 10" | BDL | 33001 | B32S1 | N | 0 | PR33002 | BDL33002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33002 | 08 | 32 | 1" | BDL | 33002 | B32S1 | N | 0 | BDL33001 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33007 | 08 | 32 | 4" | BDL | 33007 | B32S1 | N | 0 | PR33006 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33009 | 08 | 32 | 3/4" | BDL | 33009 | B32S1 | N | 0 | 32-P-3300A | BDL33013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
LA84011 |  | 32 | 3/4" | LA | 84011 | 4CS2 | ET | 30 | 32-D-8402 | 32-P-8402A | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 601
LA84011 |  | 32 | 1-1/2" | LA | 84011 | 4CS2 | ET | 30 | 32-D-8402 | 32-P-8402A | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 601
LA84013 |  | 32 | 3/4" | LA | 84013 | 4CS2 | ET | 30 | 32-P-8403 | 32-D-8402 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84040 |  | 32 | 1" | LA | 84040 | 4CS2 | ET | 30 | LA84010 | 32-S-8402B | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LC00C01 |  | 32 | 4" | LC | 00C01 | B-5 | P | 50 | LC63034 | LC91B01 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 19-U-002-01 |  | E | N | 000 | N | 136
LC02001 |  | 32 | 1" | LC | 02001 | B-5 | HB | 40 | LC72002 | LC63059 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
BDL23047 | 08 | 32 | 6" | BDL | 23047 | B32S1 | N | 0 | HCM23046 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
N36011 | 08 | 32 | 1" | N | 36011 | B4S1 | N | 0 | TP-169 (CYLINDER 1, STAGE 1, PACKING 1, C94) | TP-181 (32-D-3609) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36014 | 08 | 32 | 1" | N | 36014 | B4S1 | N | 0 | TP-174 (CYLINDER 3, STAGE 1, PACKING 3, C79) | N36012 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N40003 | 08 | 32 | 1" | N | 40003 | B-1 | N | 0 | NITROGEN CONNECTION | P40026 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-049-01 |  | E | N | 000 | N | 140
N43002 | 08 | 32 | 1" | N | 43002 | B-1 | N | 0 | NITROGEN CONNECTION | PR43037 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-03 |  | E | N | 000 | N | 140
N50001 | 08 | 32 | 1" | N | 50001 | B-1 | N | 0 | NITROGEN CONNECTION | LS50006 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-01 |  | E | N | 000 | N | 140
N51006 | 08 | 32 | 1" | N | 51006 | B-1 | N | 0 | N2 FLUSH CONNECTION | TP-N7 (PN32205) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.36A | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-03 |  | E | N | 000 | N | 140
N52036 | 08 | 32 | 1/2" | N | 52036 | 1CS2 | N | 0 | N67045 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N52036 | 08 | 32 | 1" | N | 52036 | 1CS2 | N | 0 | N67045 | 32-PK-8001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-03 |  | M | N | 000 | N | 166
N53002 | 08 | 32 | 1" | N | 53002 | B-1 | N | 0 | N | TP-010, PR530109 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.39A | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-05 |  | E | N | 000 | N | 140
N65001 | 08 | 32 | 1/2" | N | 65001 | B-1 | N | 0 | N67078 | TUBING Ø1/4" | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-01 |  | E | N | 000 | N | 140
LS630AW |  | 32 | 1-1/2" | LS | 630AW | B-5 | HB | 70 | LS63193 | PR31023 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AX |  | 32 | 1" | LS | 630AX | B-5 | HB | 70 | LS63193 | PR24032 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BB |  | 32 | 1/2" | LS | 630BB | B-5 | HB | 60 | LS63193 | HCM23066 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BD | 08 | 32 | 1" | LS | 630BD | B-5 | HB | 70 | LS6300U | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BE |  | 32 | 1" | LS | 630BE | B-5 | HB | 70 | LS63193 | JLS23008 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BE |  | 32 | 1-1/2" | LS | 630BE | B-5 | HB | 70 | LS63193 | JLS23008 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BF |  | 32 | 3/4" | LS | 630BF | B-5 | HB | 60 | LS63193 | HCM23064 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63102 |  | 32 | 3/4" | LS | 63102 | B-5 | HB | 60 | LC36101 | LC36101 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63103 |  | 32 | 3/4" | LS | 63103 | B-5 | HB | 60 | LS01001 | 32-US-1111-001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63133 |  | 32 | 1" | LS | 63133 | B-5 | HB | 70 | LS01001 | LS63034 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63137 | 08 | 32 | 1-1/2" | LS | 63137 | B-5 | HB | 70 | LS63193 | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63138 |  | 32 | 3/4" | LS | 63138 | B-5 | HB | 60 | LS63178 | 32-D-1301 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63138 |  | 32 | 1" | LS | 63138 | B-5 | HB | 70 | LS63178 | 32-D-1301 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63138 |  | 32 | 1-1/2" | LS | 63138 | B-5 | HB | 70 | LS63178 | 32-D-1301 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N01001 | 08 | 32 | 1/2" | N | 01001 | B-1 | N | 0 | NT400003 OSBL LINE | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.2 | 2 | I | MOD.A | Y | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N01006 | 08 | 32 | 1" | N | 01006 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | PR24007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-046-02 |  | E | N | 000 | N | 140
N01010 | 08 | 32 | 1" | N | 01010 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | BU01003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-001-01 |  | E | N | 000 | N | 140
N01215 | 08 | 32 | 1" | N | 01215 | B-1 | N | 0 | N67070 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N02003 | 08 | 32 | 3/4" | N | 02003 | B-1 | N | 0 | N67013 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N11017 | 08 | 32 | 1" | N | 11017 | B-1 | N | 0 | NITROGEN CONNECTION | FO11007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.47 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 000 | N | 140
N12004 | 08 | 32 | 3/4" | N | 12004 | 1CS2 | N | 0 | N67055 | 32-D-1200C | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-022-01 |  | M | N | 000 | N | 166
N12015 | 08 | 32 | 1/2" | N | 12015 | 1CS2 | N | 0 | N12009 | DRUM | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12016 | 08 | 32 | 1" | N | 12016 | 1CS2 | N | 0 | N12004 | 32-D-1200A | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-022-01 |  | M | N | 000 | N | 154
N12018 | 08 | 32 | 3/4" | N | 12018 | 1CS2 | N | 0 | END CAP | 32-LT-1201 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12019 | 08 | 32 | 1" | N | 12019 | 1CS2 | N | 0 | N12004 | 32-D-1200B | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-022-01 |  | M | N | 000 | N | 154
N12021 | 08 | 32 | 2" | N | 12021 | 1CS2 | N | 0 | 32-D-1200B | N12009 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
TEA10001 | 08 | 32 | 1/2" | TEA | 10001 | 3DS3 | N | 0 | 32-D-1001 | 32-D-1100 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA10001 | 08 | 32 | 1-1/2" | TEA | 10001 | 3DS3 | N | 0 | 32-D-1001 | 32-D-1100 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA10007 | 08 | 32 | 2" | TEA | 10007 | 3DS3 | N | 0 | 32-D-1001 | FO10010 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11001 | 08 | 32 | 1/2" | TEA | 11001 | 3DS3 | N | 0 | 32-D-1100 | 32-S-1100 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11002 | 08 | 32 | 1/2" | TEA | 11002 | 3DS3 | N | 0 | TEA11001 | TEA15B02 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11002 | 08 | 32 | 1" | TEA | 11002 | 3DS3 | N | 0 | TEA11001 | TEA15B02 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11006 | 08 | 32 | 1/2" | TEA | 11006 | 3FS3 | N | 0 | DO12017 | DO12017 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.11 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
TEA11008 | 08 | 32 | 1" | TEA | 11008 | 3DS3 | N | 0 | TEA11013 | TEA11026 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11009 | 08 | 32 | 1" | TEA | 11009 | 3FS3 | N | 0 | TEA11012 | 32-P-1100A | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
TEA11013 | 08 | 32 | 1/2" | TEA | 11013 | 3DS3 | N | 0 | FO11012 | TEA11001 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11014 | 08 | 32 | 3/4" | TEA | 11014 | 3DS3 | N | 0 | 32-S-1100 | FO11013 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11026 | 08 | 32 | 1/2" | TEA | 11026 | 3DS3 | N | 0 | 32-S-1100 | TEA11012 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11210 | 08 | 32 | 1/2" | TEA | 11210 | 3FS3 | N | 0 | TEA11026 | 32-P-1100B | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
FW68D05 | 08 | 45 | 1" | FW | 68D05 | B-13 | N | 0 | 45-XV-6818A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68E03 | 08 | 32 | 3/4" | FW | 68E03 | B-7 | N | 0 | FW68E13 | AIR RELIEF VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E03 | 08 | 32 | 2" | FW | 68E03 | B-7 | N | 0 | FW68E13 | AIR RELIEF VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E07 | 08 | 32 | 3/4" | FW | 68E07 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E07 | 08 | 32 | 2" | FW | 68E07 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
LS60002 |  | 32 | 1/2" | LS | 60002 | B-5 | HB | 60 | 32-D-6001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60006 |  | 32 | 1-1/2" | LS | 60006 | B-5 | HB | 70 | 32-D-6011 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-02 |  | E | N | 000 | N | 90
LS6300N |  | 32 | 1" | LS | 6300N | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300U |  | 32 | 1" | LS | 6300U | B-5 | HB | 70 | LS63183 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63018 |  | 32 | 1" | LS | 63018 | B-5 | HB | 70 | LS63013 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63025 |  | 32 | 2" | LS | 63025 | B-5 | HB | 80 | LS01001 | LS43010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01,32-P-047-03 |  | E | N | 000 | N | 90
LS63039 |  | 32 | 3/4" | LS | 63039 | B-5 | HB | 60 | LS63199 | 32-D-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63039 |  | 32 | 1-1/2" | LS | 63039 | B-5 | HB | 70 | LS63199 | 32-D-3100 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63047 |  | 32 | 1" | LS | 63047 | B-5 | HB | 70 | LS63206 | BDH60006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63047 |  | 32 | 2" | LS | 63047 | B-5 | HB | 80 | LS63206 | BDH60006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
BDH21004 | 08 | 32 | 4" | BDH | 21004 | C42S2 | N | 0 | SL21002 | BDH21001 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH60004 | 08 | 32 | 8" | BDH | 60004 | C42S2 | N | 0 | 32-D-6011 | FL60004 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.41 | 1 | III | MOD.G | Y | 1 | Y | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDL01009 | 08 | 32 | 3" | BDL | 01009 | B32S1 | N | 0 | BDL61001 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
FW68P14 | 08 | 32 | 2" | FW | 68P14 | B-13 | N | 0 | FW68P17 | FW68P17 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68Q02 | 08 | 32 | 3" | FW | 68Q02 | B-13 | N | 0 | FW68C09 | FW68Q05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q03 | 08 | 32 | 1-1/2" | FW | 68Q03 | B-13 | N | 0 | FW68Q06 | FW68Q06 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
PCW89009 | 08 | 32 | 18" | PCW | 89009 | 4CS2 | P | 100 | 32-Z-8906 | TP-N50401 (A-8900) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | SL | - | - | <1.5 | 60 | sh.68K | 2 | I | MOD.A | Y | 5 | N | 32-P-070-07 |  | M | N | 110 | N | 451 | 3,6
PCW89011 | 08 | 32 | 16" | PCW | 89011 | 1CS2 | P | 100 | TP-N50802 (S-8910A/B) | TP-N50901 (E-8900A) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
HD01001 | 08 | 32 | 3/4" | HD | 01001 | 3FS4 | N | 0 | HD700002 | 32-S-0101 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01001 | 08 | 32 | 1-1/2" | HD | 01001 | 3FS4 | N | 0 | HD700002 | 32-S-0101 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01001 | 08 | 32 | 2" | HD | 01001 | 3FS4 | N | 0 | HD700002 | 32-S-0101 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | Y | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HD01002 | 08 | 32 | 1" | HD | 01002 | 3FS4 | N | 0 | 32-S-0101 | ET22007 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.1 | 1 | II | MOD.A2 | Y | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
VZ11002 | 08 | 32 | 4" | VZ | 11002 | 3DS3 | N | 0 | 32-D-1100 | - | 12.0 | 150.0 | 0.05 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 263 | 8,29
VZ11004 | 08 | 32 | 1/2" | VZ | 11004 | B4S2 | N | 0 | 32-D-1102 | - | 0.5 | 150.0 | 0.01 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.47 | 2 | NA | NA | NA | 1 | N | 32-P-020-01 |  | E | N | 110 | N | 213 | 23,25
VZ11004 | 08 | 32 | 3/4" | VZ | 11004 | B4S2 | N | 0 | 32-D-1102 | - | 0.5 | 150.0 | 0.01 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.47 | 2 | NA | NA | NA | 1 | N | 32-P-020-01 |  | E | N | 110 | N | 213 | 23,25
VZ11004 | 08 | 32 | 1" | VZ | 11004 | B4S2 | N | 0 | 32-D-1102 | - | 0.5 | 150.0 | 0.01 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.47 | 2 | NA | NA | NA | 1 | N | 32-P-020-01 |  | E | N | 110 | N | 213 | 23,25
VZ11004 | 08 | 32 | 1-1/2" | VZ | 11004 | B4S2 | N | 0 | 32-D-1102 | - | 0.5 | 150.0 | 0.01 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.47 | 2 | NA | NA | NA | 1 | N | 32-P-020-01 |  | E | N | 110 | N | 213 | 23,25
VZ12008 | 08 | 32 | 3/4" | VZ | 12008 | 1CS2 | N | 0 | 32-S-1201 | 32-S-1201 | 5.0 | 150.0 | 2.0 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 271 | 23,25
VZ12009 |  | 32 | 1/2" | VZ | 12009 | 1CS2 | ET | 30 | 32-D-1200A | 32-D-1200A | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12009 |  | 32 | 1" | VZ | 12009 | 1CS2 | ET | 30 | 32-D-1200A | 32-D-1200A | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12010 |  | 32 | 1/2" | VZ | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-D-1200B | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
PW50016 | 08 | 32 | 1/2" | PW | 50016 | B4S2 | N | 0 | 32-T-5001 | PW50017 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50016 | 08 | 32 | 2" | PW | 50016 | B4S2 | N | 0 | 32-T-5001 | PW50017 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50017 |  | 32 | 2" | PW | 50017 | B4S2 | P | 50 | 32-T-5001 | PW50018 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50018 |  | 32 | 2" | PW | 50018 | B4S2 | P | 50 | 32-T-5001 | ACW | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50020 |  | 32 | 6" | PW | 50020 | B4S2 | HB | 30 | 32-T-5001 | 32-P-5001 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50021 | 08 | 32 | 8" | PW | 50021 | B4S2 | N | 0 | PW50020 | PW52015 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50023 |  | 32 | 3/4" | PW | 50023 | B4S2 | HB | 30 | 32-P-5001 | 32-T-5001 | 9.0 | 180.0 | 4.0 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | I | MOD.A | Y | 20 | N | 32-P-050-02 |  | E | N | 140 | N | 31
PW50023 |  | 32 | 4" | PW | 50023 | B4S2 | HB | 30 | 32-P-5001 | 32-T-5001 | 9.0 | 180.0 | 4.0 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | I | MOD.A | Y | 20 | N | 32-P-050-02 |  | E | N | 140 | N | 31
PW50025 |  | 32 | 2" | PW | 50025 | B4S2 | P | 50 | 32-T-5001 | 32-D-5202 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50026 | 08 | 32 | 3/4" | PW | 50026 | B4S2 | N | 0 | 32-D-5002 | PR50011 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW51010 | 08 | 32 | 1" | PW | 51010 | B4S1 | N | 0 | 32-D-5102 | (TRENCH) | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51010 | 08 | 32 | 2" | PW | 51010 | B4S1 | N | 0 | 32-D-5102 | (TRENCH) | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ80005 | 08 | 32 | 3" | VZ | 80005 | 4CS9 | HA | 30 | 32-D-8002A | 32-D-8002A | 0.2/-0.005 | 100.0/100.0 | 0.12 | 90.0 |  | 0 | 0 | V | VESSEL TRIM | GS | - | - | >1.5 | 90 | sh.58 | 1 | NA | NA | NA | 27 | N | 32-P-060-01 |  | G-2 | N | 110 | N | 444 | 6,23,10,11,25,28,13
SA81011 | 08 | 32 | 6" | SA | 81011 | 1CS2 | N | 0 | PK-8101 | 32-ZF-8108 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.60 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-03 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81012 | 08 | 32 | 6" | SA | 81012 | 1CS2 | N | 0 | PK-8101 | 32-ZF-8108 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.60 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-03 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81014 | 08 | 32 | 6" | SA | 81014 | 1CS2 | N | 0 | 32-V-8105 | TP-N11204 (32-H-8901) | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.61 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-03 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81015 | 08 | 32 | 8" | SA | 81015 | 1CS2 | N | 0 | 810330 | 32-ZF-8108 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81018 | 08 | 32 | 3/4" | SA | 81018 | 1CS2 | N | 0 | IA89010 | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81018 | 08 | 32 | 2" | SA | 81018 | 1CS2 | N | 0 | IA89010 | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81019 | 08 | 32 | 1/2" | SA | 81019 | 1CS2 | N | 0 | IA89015 | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
BDL34014 | 08 | 32 | 1" | BDL | 34014 | B4S1 | N | 0 | BDL31030 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34018 | 08 | 32 | 3/4" | BDL | 34018 | B4S1 | N | 0 | BDL34013 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL34018 | 08 | 32 | 14" | BDL | 34018 | B4S1 | N | 0 | BDL34013 | BDL60035 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL36014 | 08 | 32 | 2" | BDL | 36014 | B32S1 | N | 0 | TP-110 (32-D-3604) | BDL36015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40025 | 08 | 32 | 2" | BDL | 40025 | B32S1 | N | 0 | PR40032 | BDL60037 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
JWR33001 | 08 | 32 | 1" | JWR | 33001 | C3S1 | N | 0 | 32-E-3300 | JWR33002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR33001 | 08 | 32 | 3" | JWR | 33001 | C3S1 | N | 0 | 32-E-3300 | JWR33002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
BDL23057 | 08 | 32 | 1/2" | BDL | 23057 | B32S1 | N | 0 | HCM23071 | BDL23055 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23065 | 08 | 32 | 3/4" | BDL | 23065 | B32S1 | N | 0 | 32-Z-2303B | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.15 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24065 | 08 | 32 | 3/4" | BDL | 24065 | B32S1 | N | 0 | HCM24074 | BDL24067 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24068 | 08 | 32 | 3/4" | BDL | 24068 | B32S1 | N | 0 | BDL24076 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24089 | 08 | 32 | 3/4" | BDL | 24089 | B32S1 | N | 0 | HCM24080 | BDL60026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL26004 | 08 | 32 | 1/2" | BDL | 26004 | B32S1 | N | 0 | CO26029 | BDL26003 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.22 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31039 | 08 | 32 | 3/4" | BDL | 31039 | B32S1 | N | 0 | HCM31012 | BDL31038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32016 | 08 | 32 | 1" | BDL | 32016 | B32S1 | N | 0 | HCM32034 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
N6700S | 08 | 32 | 3/4" | N | 6700S | B-1 | N | 0 | N67004 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67010 | 08 | 32 | 1" | N | 67010 | B-1 | N | 0 | N67028 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67012 | 08 | 32 | 3/4" | N | 67012 | B-1 | N | 0 | N67046 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67023 | 08 | 32 | 3/4" | N | 67023 | B-1 | N | 0 | N67028 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67043 | 08 | 32 | 1" | N | 67043 | B-1 | N | 0 | N67045 | N52033 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67083 | 08 | 32 | 3/4" | N | 67083 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67093 | 08 | 32 | 1" | N | 67093 | B-1 | N | 0 | N67028 | BDL60041 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N670AB | 08 | 32 | 1" | N | 670AB | B-1 | N | 0 | N67005 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67100 | 08 | 32 | 1" | N | 67100 | B-1 | N | 0 | N67029 | BDL60049 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67104 | 08 | 32 | 3/4" | N | 67104 | B-1 | N | 0 | N67029 | N67091 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
CO26038 | 08 | 32 | 1/2" | CO | 26038 | 1IS5 | N | 0 | 2 ND. EMERGENCY KILLER SYSTEM | CO26030 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26039 | 08 | 32 | 1/2" | CO | 26039 | 1IS5 | N | 0 | 2 ND. EMERGENCY KILLER SYSTEM | CO26030 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
LS63141 |  | 32 | 1/2" | LS | 63141 | B-5 | HB | 60 | LS630BF | JLS23011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63146 |  | 32 | 1/2" | LS | 63146 | B-5 | HB | 60 | LS63193 | JLS23019 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63147 |  | 32 | 1/2" | LS | 63147 | B-5 | HB | 60 | LS630BE | HCM23070 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63149 |  | 32 | 1" | LS | 63149 | B-5 | HB | 70 | LS01001 | LC36101 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63160 |  | 32 | 3/4" | LS | 63160 | B-5 | HB | 60 | LS63177 | TP-002 (LS720155) | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63162 |  | 32 | 1" | LS | 63162 | B-5 | HB | 70 | LS63177 | JLS73005 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63177 |  | 32 | 3/4" | LS | 63177 | B-5 | HB | 60 | LS01001 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63178 |  | 32 | 3/4" | LS | 63178 | B-5 | HB | 60 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63179 |  | 32 | 1" | LS | 63179 | B-5 | HB | 70 | LS63178 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63183 |  | 32 | 3" | LS | 63183 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63185 |  | 32 | 3/4" | LS | 63185 | B-5 | HB | 60 | LS01001 | LC63076 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63186 |  | 32 | 3/4" | LS | 63186 | B-5 | HB | 60 | LS63183 | LC63075 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63190 |  | 32 | 2" | LS | 63190 | B-5 | HB | 80 | LS01001 | 32-1121-S-001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63194 |  | 32 | 3/4" | LS | 63194 | B-5 | HB | 60 | LS63206 | LC63086 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63196 |  | 32 | 3/4" | LS | 63196 | B-5 | HB | 60 | LS63197 | 32-US-1113-001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N12024 | 08 | 32 | 1-1/2" | N | 12024 | 1CS2 | N | 0 | 32-D-1200C | N12009 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N12026 | 08 | 32 | 1/2" | N | 12026 | 1CS2 | N | 0 | N12030 | 32-LT-1206 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N12027 | 08 | 32 | 1/2" | N | 12027 | 1CS2 | N | 0 | N67056 | N12018 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
PA01001 | 08 | 32 | 3/4" | PA | 01001 | B-1 | N | 0 | PA300003 OSBL LINE | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA02009 | 08 | 32 | 3/4" | PA | 02009 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
TEA20002 |  | 32 | 1/2" | TEA | 20002 | 3FS3 | CF | 25 | 32-Z-2004 | 32-R-2000 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.11 | 1 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | F | N | 343 | N | 266 | 8,29
TEA20004 |  | 32 | 3/4" | TEA | 20004 | 3FS3 | ET | 30 | 32-R-2000 | FO20003 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.11 | 1 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | F | N | 343 | N | 266 | 8,29
VA00002 | 08 | 32 | 4" | VA | 00002 | B-1 | N | 0 | 1114-ACW-SM-045 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00003 | 08 | 32 | 4" | VA | 00003 | B-1 | N | 0 | 1114-ACW-SM-048 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00005 | 08 | 32 | 4" | VA | 00005 | B-1 | N | 0 | 1114-ACW-SM-073 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00006 | 08 | 32 | 4" | VA | 00006 | B-1 | N | 0 | 1121-ACW-SM-037 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00008 | 08 | 32 | 4" | VA | 00008 | B-1 | N | 0 | 1123-ACW-DM-004 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00009 | 08 | 32 | 4" | VA | 00009 | B-1 | N | 0 | 1123-ACW-SM-023 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00017 | 08 | 32 | 4" | VA | 00017 | B-1 | N | 0 | 1211-AW-SM-109 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00019 | 08 | 32 | 4" | VA | 00019 | B-1 | N | 0 | 1211-ACW-SM-117 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00020 | 08 | 32 | 4" | VA | 00020 | B-1 | N | 0 | 1211-CW-BS-002A | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00025 | 08 | 32 | 4" | VA | 00025 | B-1 | N | 0 | 2121-ACW-SM-123 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
LS63065 |  | 32 | 3/4" | LS | 63065 | B-5 | HB | 60 | LS6300K | JLS20001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63073 |  | 32 | 3/4" | LS | 63073 | B-5 | HB | 60 | LS01001 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | I | MOD.A | Y | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS63073 |  | 32 | 6" | LS | 63073 | B-5 | HB | 90 | LS01001 | LS24012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | I | MOD.A | Y | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS63087 |  | 32 | 1" | LS | 63087 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AQ |  | 32 | 1" | LS | 630AQ | B-5 | HB | 70 | LS63193 | PR31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63160 |  | 32 | 1-1/2" | LS | 63160 | B-5 | HB | 70 | LS63177 | TP-002 (LS720155) | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63175 |  | 32 | 1/2" | LS | 63175 | B-5 | HB | 60 | LS01001 | LC63060 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63175 |  | 32 | 3/4" | LS | 63175 | B-5 | HB | 60 | LS01001 | LC63060 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.2 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
FW68Q12 | 08 | 32 | 1-1/2" | FW | 68Q12 | B-13 | N | 0 | FW68Q09 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68R04 | 08 | 45 | 1" | FW | 68R04 | B-13 | N | 0 | 45-XV-6821A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68R07 | 08 | 45 | 3/4" | FW | 68R07 | B-7 | N | 0 | FW68B50 | FW68R09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R07 | 08 | 45 | 8" | FW | 68R07 | B-7 | N | 0 | FW68B50 | FW68R09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
HD22006 | 08 | 32 | 1/2" | HD | 22006 | 3FS4 | N | 0 | HD01002 | PR21009 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.13 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HN21003 | 08 | 32 | 1-1/2" | HN | 21003 | C6S1 | N | 0 | NITROGEN CONNECTION | PR21013 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.12 | 2 | I | MOD.A | Y | 1 | N | 32-P-042-01 |  | E | N | 000 | N | 170
HN21006 | 08 | 32 | 1-1/2" | HN | 21006 | C6S1 | N | 0 | NITROGEN CONNECTION | PR21012 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.12 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-02 |  | E | N | 000 | N | 170
HN67002 | 08 | 32 | 1-1/2" | HN | 67002 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67003 | 08 | 32 | 3/4" | HN | 67003 | C6S1 | N | 0 | HN67011 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67005 | 08 | 32 | 3/4" | HN | 67005 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67010 | 08 | 32 | 3/4" | HN | 67010 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67010 | 08 | 32 | 1-1/2" | HN | 67010 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67022 | 08 | 32 | 3/4" | HN | 67022 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN71005 | 08 | 32 | 1" | HN | 71005 | C6S1 | N | 0 | NITROGEN CONNECTION | ET71049 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-02 |  | E | N | 000 | N | 170
VZ12010 |  | 32 | 3/4" | VZ | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-D-1200B | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12010 |  | 32 | 2" | VZ | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-D-1200B | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12011 |  | 32 | 3/4" | VZ | 12011 | 1CS2 | ET | 30 | 32-D-1200C | 32-D-1200C | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12012 | 08 | 32 | 3/4" | VZ | 12012 | 1CS2 | ET | 30 | 32-S-1200A | DRAIN | 5.0 | 150.0 | 0.1 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 273 | 23,25
VZ12014 | 08 | 32 | 3/4" | VZ | 12014 | 1CS2 | ET | 30 | 32-S-1200C | DRAIN | 5.0 | 150.0 | 0.1 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 273 | 23,25
VZ13005 |  | 32 | 1/2" | VZ | 13005 | B4S2 | HH | 30 | 32-D-1301 | 32-D-1301 | 0.5 | 180.0 | 0.05/0.05 | 70.0/100.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 222 | 23,25
CHWS14006 |  | 32 | 1/2" | CHWS | 14006 | B-1 | CF | 25 | CHWS14002 | CAP | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14006 |  | 32 | 1" | CHWS | 14006 | B-1 | CF | 25 | CHWS14002 | CAP | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14007 |  | 32 | 1/2" | CHWS | 14007 | B-1 | CF | 25 | JLS14001 | CHW1523 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14009 |  | 32 | 3/4" | CHWS | 14009 | B-1 | HA | 30 | 32-P-1400A | 32-E-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14009 |  | 32 | 2" | CHWS | 14009 | B-1 | HA | 30 | 32-P-1400A | 32-E-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14010 |  | 32 | 1" | CHWS | 14010 | B-1 | HA | 30 | CHWS14015 | 32-P-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14012 |  | 32 | 3/4" | CHWS | 14012 | B-1 | HA | 30 | 32-D-1400A | CHWS14008 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14012 |  | 32 | 1-1/2" | CHWS | 14012 | B-1 | HA | 30 | 32-D-1400A | CHWS14008 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14021 |  | 32 | 1/2" | CHWS | 14021 | B-1 | CF | 25 | CHWS14002 | 32-D-1401A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14021 |  | 32 | 1" | CHWS | 14021 | B-1 | CF | 25 | CHWS14002 | 32-D-1401A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20002 |  | 32 | 1" | CHWS | 20002 | B-1 | CF | 25 | 32-P-2000 | JLS20001 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
O13002 | 08 | 32 | 1" | O | 13002 | 1CS2 | N | 0 | O13025 | O13026 | 6.0 | 200.0 | 5.0 | 100.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 100 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-025-01 |  | A | N | 010 | N | 231 | 23,25
O13011 | 7A | 32 | 1" | O | 13011 | 1CS2 | P | 50 | O13020 | 32-D-1200B | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13022 |  | 32 | 3/4" | O | 13022 | 1CS2 | ST | 30 | 32-P-1300 | 32-S-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13025 |  | 32 | 3/4" | O | 13025 | 1CS2 | ST | 30 | 32-S-1300 | O13022 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13025 |  | 32 | 1" | O | 13025 | 1CS2 | ST | 30 | 32-S-1300 | O13022 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13038 |  | 32 | 2" | O | 13038 | B4S2 | ET | 30 | O13017 | O13037 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O13039 |  | 32 | 1-1/2" | O | 13039 | 1CS2 | ET | 30 | O66040 | 32-D-1602 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O14002 |  | 32 | 1" | O | 14002 | 1FS4 | ET | 30 | 32-HX-1431 | O14003 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O14009 |  | 32 | 1" | O | 14009 | 1FS4 | ET | 30 | 32-D-1401A | O14001 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O14010 |  | 32 | 3/4" | O | 14010 | 1CS2 | ET | 30 | O15003 | 32-Z-1400A | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-01 |  | M | N | 110 | N | 236 | 23,25
VZ84005 | 08 | 32 | 1/2" | VZ | 84005 | 4CS2 | ET | 30 | 32-D-8402 | - | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | VESSEL TRIM | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 607
VZ84005 | 08 | 32 | 3/4" | VZ | 84005 | 4CS2 | ET | 30 | 32-D-8402 | - | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | VESSEL TRIM | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 607
VZ84005 | 08 | 32 | 3/4" | VZ | 84005 | 4CS2 | N | 0 | 32-D-8402 | - | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | VESSEL TRIM | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 607
VZ84005 | 08 | 32 | 1" | VZ | 84005 | 4CS2 | ET | 30 | 32-D-8402 | - | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | VESSEL TRIM | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 607
VZ84005 | 08 | 32 | 2" | VZ | 84005 | 4CS2 | ET | 30 | 32-D-8402 | - | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | VESSEL TRIM | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 607
VZ84006 | 08 | 32 | 3/4" | VZ | 84006 | 4CS2 | ET | 30 | 32-S-8402A | - | 6.0 | 150.0 | 5.0 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 608
VZ84007 | 08 | 32 | 3/4" | VZ | 84007 | 4CS2 | ET | 30 | 32-S-8402B | - | 6.0 | 150.0 | 5.0 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 608
VZ89001 | 08 | 32 | 3/4" | VZ | 89001 | 3CS6 | N | 0 | 32-S-8905 | - | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | VESSEL TRIM | G | - | - | >1.5 | 100 | sh.68N | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-07 |  | M | N | 000 | N | 91
VZ91016 | 08 | 32 | 2" | VZ | 91016 | 5CS7 | N | 0 | 32-H-9001C | - | 0.1/-0.01 | 100.0/100.0 | 0.01/0.01 | 60.0/80.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 60 | sh.70 | 1 | NA | NA | NA | NR | N | 32-P-082-03 |  | M | N | 110 | N | 447 | 6,25,23
WW00001 | 08 | 32 | 1" | WW | 00001 | B4S2 | N | 0 | 32-AH-0001 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.109 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-009-01 |  | E | N | 000 | N | 87
JWR33001 | 08 | 32 | 3/4" | JWR | 33001 | C3S1 | N | 0 | 32-E-3300 | JWR33002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR37004 | 08 | 32 | 3/4" | JWR | 37004 | B-1 | N | 0 | 32-Z-3300B | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52005 | 08 | 32 | 1-1/2" | JWR | 52005 | B-1 | N | 0 | 32-E-5252B | JWR52004 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWS24010 | 08 | 32 | 6" | JWS | 24010 | D20S1 | N | 0 | JWS64051 | 32-E-2400 | 49.0/49.0 | -45.0/150.0 | 5.0 | 30.0 |  | 73.51 | 128.56 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.20 | 2 | II | MOD.A2 | Y | 1 | Y | 32-U-022-01 |  | M | N | 000 | N | 1020
JWR37008 | 08 | 32 | 3/4" | JWR | 37008 | B-1 | N | 0 | 32-Z-7300 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52001 | 08 | 32 | 1" | JWR | 52001 | B-1 | N | 0 | 32-E-5201 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52004 | 08 | 32 | 1-1/2" | JWR | 52004 | B-1 | N | 0 | 32-E-5252A | JWR64047 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR61003 | 08 | 32 | 1-1/2" | JWR | 61003 | B-1 | N | 0 | TP-007 (JWR610201) | JWR61002 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.42C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR63001 | 08 | 32 | 3/4" | JWR | 63001 | B-1 | N | 0 | 32-E-6300 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR63001 | 08 | 32 | 8" | JWR | 63001 | B-1 | N | 0 | 32-E-6300 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
BDL32016 | 08 | 32 | 6" | BDL | 32016 | B32S1 | N | 0 | HCM32034 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL33003 | 08 | 32 | 1/2" | BDL | 33003 | B32S1 | N | 0 | PR33027 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33004 | 08 | 32 | 3/4" | BDL | 33004 | B32S1 | N | 0 | PR33014 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33016 | 08 | 32 | 3/4" | BDL | 33016 | B32S1 | N | 0 | 32-P-3300B | BDL33014 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33017 | 08 | 32 | 1" | BDL | 33017 | B32S1 | N | 0 | PR33022 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL35010 | 08 | 32 | 1" | BDL | 35010 | B32S1 | N | 0 | PR35019 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36013 | 08 | 32 | 2" | BDL | 36013 | B32S1 | N | 0 | TP-101,32-D-3601 | BDL36018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36022 | 08 | 32 | 3" | BDL | 36022 | B32S1 | P | 50 | PR36032 | BDL36018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36022 | 08 | 32 | 6" | BDL | 36022 | B32S1 | P | 50 | PR36032 | BDL36018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36023 | 08 | 32 | 2" | BDL | 36023 | B32S1 | N | 0 | TP-179 (32-D-3608) | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
CO42003 | 08 | 32 | 3/4" | CO | 42003 | 1IS5 | N | 0 | CO42017 | 32-R-4001 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42021 | 08 | 32 | 1/2" | CO | 42021 | 1IS5 | N | 0 | REACTOR EMERGENCY KILLER | CO42018 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CT14001 |  | 32 | 1" | CT | 14001 | QXC25S1 | CF | 25 | 32-D-1400A | 32-S-1400A | 20.0 | 190.0 | 10.0/0.03 | 6.0/70.0 |  | 31.64 | 74.4 | H | DRY CATALYST | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-03 |  | M | N | 231 | N | 284
CT15001 | 08 | 32 | 3/8" | CT | 15001 | 3FS3 | JP | 0 | CT15002 | CT20001 | 70.0 | 100.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-04 |  | A | N | 232 | N | 282 | 23,29,25
CT15003 | 08 | 32 | 1/2" | CT | 15003 | 3FS3 | CF | 25 | CT14004 | CT15011 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
CT15003 | 08 | 32 | 3/4" | CT | 15003 | 3FS3 | CF | 25 | CT14004 | CT15011 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.9A | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
LS63198 |  | 32 | 3/4" | LS | 63198 | B-5 | HB | 60 | LS63197 | CAP | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63199 |  | 32 | 4" | LS | 63199 | B-5 | HB | 90 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63203 |  | 32 | 2" | LS | 63203 | B-5 | HB | 80 | LS01001 | LS63074 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63206 |  | 32 | 3" | LS | 63206 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS65001 |  | 32 | 1" | LS | 65001 | B-5 | HB | 70 | 32-D-6500 | LC65002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.45 | 2 | Art 4.3 | NA | N | NR | N | 32-P-031-01 |  | E | N | 000 | N | 90
LS65003 |  | 32 | 1/2" | LS | 65003 | B-5 | HB | 60 | LS63064 | LC65001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.45 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS66001 |  | 32 | 3/4" | LS | 66001 | B-5 | HB | 60 | JLS66001 | LC66001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.46 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-03 |  | E | N | 000 | N | 90
LS66001 |  | 32 | 1-1/2" | LS | 66001 | B-5 | HB | 70 | JLS66001 | LC66001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.46 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-03 |  | E | N | 000 | N | 90
LS66003 |  | 32 | 1-1/2" | LS | 66003 | B-5 | HB | 70 | LS66002 | JLS66001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.46 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-03 |  | E | N | 000 | N | 90
LS71010 |  | 32 | 3/4" | LS | 71010 | C6S1 | HB | 50 | LS63059 | 32-E-7101 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS71010 |  | 32 | 3" | LS | 71010 | C6S1 | HB | 60 | LS63059 | 32-E-7101 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | Y | 32-U-052-01 |  | E | N | 141 | N | 1092
LS71011 |  | 32 | 3/4" | LS | 71011 | B-5 | HB | 60 | LS63059 | LC71001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.48 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS71012 |  | 32 | 1" | LS | 71012 | C6S1 | HB | 50 | 32-E-7101 | LC71002 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS72002 |  | 32 | 6" | LS | 72002 | D1S1 | HB | 70 | LS72129 | 32-E-7201 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.51 | 1 | III | MOD.G | Y | 20 | Y | 32-U-052-01 |  | E | N | 041 | N | 1090
PA12010 | 08 | 32 | 1/2" | PA | 12010 | B-1 | N | 0 | PA62075 | 32-P-1201 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-022-01 |  | E | N | 000 | N | 190
PA14001 | 08 | 32 | 1/2" | PA | 14001 | B-1 | N | 0 | PA62001 | 32-Z-1402 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.7 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62004 | 08 | 32 | 1" | PA | 62004 | B-1 | N | 0 | PA01001 | 32-P-6101 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62034 | 08 | 32 | 3/4" | PA | 62034 | B-1 | N | 0 | PA62036 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62035 | 08 | 32 | 3/4" | PA | 62035 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62037 | 08 | 32 | 3/4" | PA | 62037 | B-1 | N | 0 | PA62038 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62038 | 08 | 32 | 1" | PA | 62038 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62045 | 08 | 32 | 1" | PA | 62045 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62047 | 08 | 32 | 3/4" | PA | 62047 | B-1 | N | 0 | PA62045 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62048 | 08 | 32 | 3/4" | PA | 62048 | B-1 | N | 0 | PA62045 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62053 | 08 | 32 | 1" | PA | 62053 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62057 | 08 | 32 | 3/4" | PA | 62057 | B-1 | N | 0 | PA62072 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62058 | 08 | 32 | 3/4" | PA | 62058 | B-1 | N | 0 | PA62072 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62061 | 08 | 32 | 3/4" | PA | 62061 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62063 | 08 | 32 | 3/4" | PA | 62063 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62067 | 08 | 32 | 3/4" | PA | 62067 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62069 | 08 | 32 | 3/4" | PA | 62069 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62072 | 08 | 32 | 1-1/2" | PA | 62072 | B-1 | N | 0 | PA01001 | PA62055 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
VA00027 | 08 | 32 | 4" | VA | 00027 | B-1 | N | 0 | 2121-ACW-SM-096 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00032 | 08 | 32 | 4" | VA | 00032 | B-1 | N | 0 | 2121-ACW-SM-114 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
JWS52002 | 08 | 32 | 1-1/2" | JWS | 52002 | B-1 | N | 0 | JWS52001 | Seal Pot | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
LS63193 |  | 32 | 4" | LS | 63193 | B-5 | HB | 90 | LS01001 | LS63045 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS66001 |  | 32 | 1" | LS | 66001 | B-5 | HB | 70 | JLS66001 | LC66001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.46 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-03 |  | E | N | 000 | N | 90
LS71012 |  | 32 | 1/2" | LS | 71012 | C6S1 | HB | 50 | 32-E-7101 | LC71002 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS71012 |  | 32 | 3/4" | LS | 71012 | C6S1 | HB | 50 | 32-E-7101 | LC71002 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS71012 |  | 32 | 1-1/2" | LS | 71012 | C6S1 | HB | 50 | 32-E-7101 | LC71002 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.48 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
BDL32034 | 08 | 32 | 2" | BDL | 32034 | B32S1 | N | 0 | TP-32A, (32-D-3203) | BDL32031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL33006 | 08 | 32 | 3/4" | BDL | 33006 | B32S1 | N | 0 | PR33023 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL33021 | 08 | 32 | 3/4" | BDL | 33021 | B32S1 | N | 0 | PR33032 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL34013 | 08 | 32 | 8" | BDL | 34013 | B4S1 | N | 0 | PR34001 | BDL34018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL35011 | 08 | 32 | 3/4" | BDL | 35011 | B32S1 | N | 0 | VZ35002 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.27 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36010 | 08 | 32 | 6" | BDL | 36010 | B32S1 | N | 0 | BDL36018 | BDL60031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
N80015 | 08 | 32 | 3/4" | N | 80015 | 1CS2 | N | 0 | N67077 | 32-S-8000 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80015 | 08 | 32 | 1" | N | 80015 | 1CS2 | N | 0 | N67077 | 32-S-8000 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80020 | 08 | 32 | 3/4" | N | 80020 | 1CS2 | N | 0 | N67074 | 32-V-8000A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80021 | 08 | 32 | 3/4" | N | 80021 | 1CS2 | N | 0 | N67076 | 32-V-8000B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N81048 | 08 | 32 | 3/4" | N | 81048 | 1CS2 | N | 0 | N89051 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-03 |  | M | N | 000 | N | 166
N81050 | 08 | 32 | 3/4" | N | 81050 | 1CS2 | N | 0 | N89050 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-03 |  | M | N | 000 | N | 166
N89011 | 08 | 32 | 1/2" | N | 89011 | B-1 | N | 0 | N89034 | N89010 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89054 | 08 | 32 | 3/4" | N | 89054 | B-1 | N | 0 | N89067 | TP-019 (32-S-8120) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
CHWS20003 |  | 32 | 1" | CHWS | 20003 | B-1 | CF | 25 | JLS20001 | 32-R-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20003 |  | 32 | 4" | CHWS | 20003 | B-1 | CF | 25 | JLS20001 | 32-R-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS21003 |  | 32 | 3/4" | CHWS | 21003 | B-1 | CF | 25 | 32-P-2101 | CHWS21004 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS21003 |  | 32 | 6" | CHWS | 21003 | B-1 | CF | 40 | 32-P-2101 | CHWS21004 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS21006 |  | 32 | 4" | CHWS | 21006 | D3S1 | CF | 25 | CHWS61023 | 32-E-2100 | 55.0 | 150.0 | 4.0 | 2.0 |  | 82.51 | 153.15 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.12 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 1050
CHWS61015 |  | 32 | 3/4" | CHWS | 61015 | B-1 | CF | 25 | CHWS61002 | CHWR61005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61015 |  | 32 | 6" | CHWS | 61015 | B-1 | CF | 40 | CHWS61002 | CHWR61005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61015 |  | 32 | 10" | CHWS | 61015 | B-1 | CF | 40 | CHWS61002 | CHWR61005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61020 |  | 32 | 3/4" | CHWS | 61020 | B-1 | CF | 25 | CHWS61027 | TP-N10 (CHWS510109) | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61024 |  | 32 | 1-1/2" | CHWS | 61024 | B-1 | CF | 25 | CHWS61002 | CHWR21006 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61024 |  | 32 | 3" | CHWS | 61024 | B-1 | CF | 25 | CHWS61002 | CHWR21006 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CO26027 | 08 | 32 | 1/2" | CO | 26027 | 1IS5 | N | 0 | 32-R-2300 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26027 | 08 | 32 | 1" | CO | 26027 | 1IS5 | N | 0 | 32-R-2300 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26028 | 08 | 32 | 3/4" | CO | 26028 | 1IS5 | N | 0 | CO26029 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26034 | 08 | 32 | 1/2" | CO | 26034 | 1IS5 | N | 0 | 1 ST. EMERGENCY KILLER SYSTEM | CO26025 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
O15005 |  | 32 | 1/2" | O | 15005 | 1CS2 | ET | 30 | 32-S-1501 | SP 1505 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 236 | 23,25
O15015 |  | 32 | 1/2" | O | 15015 | B4S2 | ET | 30 | 32-D-1501 | 32-D-1401A | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O20007 |  | 32 | 1/2" | O | 20007 | 1FS4 | ET | 30 | O20001 | 32-Z-2002B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O31016 | 08 | 32 | 1-1/2" | O | 31016 | B4S2 | N | 0 | O31014 | O31010 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
O66015 |  | 32 | 3/4" | O | 66015 | 1CS2 | ET | 30 | 32-S-6601 | O66023 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66015 |  | 32 | 1-1/2" | O | 66015 | 1CS2 | ET | 30 | 32-S-6601 | O66023 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66021 |  | 32 | 1-1/2" | O | 66021 | 1CS2 | ET | 30 | O66020 | O66022 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66025 |  | 32 | 2" | O | 66025 | B4S2 | ET | 30 | O66024 | O66027 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66027 |  | 32 | 1" | O | 66027 | B4S2 | ET | 30 | O66025 | 32-P-6601 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66027 |  | 32 | 3" | O | 66027 | B4S2 | ET | 30 | O66025 | 32-P-6601 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66040 |  | 32 | 3/4" | O | 66040 | 1CS2 | ET | 30 | O66015 | O13014 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
OG72001 | 08 | 32 | 2" | OG | 72001 | C42S1 | N | 0 | PR72017 | OG01004 | 42.0/42.0 | -45.0/150.0 | 4.0 | 70.0 |  | 63.01 | 76.65 | H | OFF GAS | G | - | - | >1.5 | 70 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-U-034-01 |  | G | N | 141 | N | 502 | ,10
P23026 |  | 32 | 3/4" | P | 23026 | C42S5 | HB | 30 | 32-D-2301 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23026 |  | 32 | 14" | P | 23026 | C42S5 | HB | 40 | 32-D-2301 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
WW45001 | 08 | 45 | 2" | WW | 45001 | B4S2 | N | 0 | 45-P-4511 | WW45002 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-050-01 |  | E | N | 000 | N | 87
WW45001 | 08 | 45 | 4" | WW | 45001 | B4S2 | N | 0 | 45-P-4511 | WW45002 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-050-01 |  | E | N | 000 | N | 87
WW45002 | 08 | 45 | 4" | WW | 45002 | UGB-1PE | N | 0 | WW45001 | BURN PIT | 9.0 | 80.0 | 3.0 | 50.0 |  | 13.5 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 50 | sh.106 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-050-01 |  | E | N | 000 | N | 95
WW52010 | 08 | 32 | 1-1/2" | WW | 52010 | B4S2 | N | 0 | LC52006 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.37 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW52011 | 08 | 32 | 1-1/2" | WW | 52011 | B4S2 | N | 0 | LC52007 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.37 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW62001 | 08 | 32 | 1" | WW | 62001 | B4S2 | N | 0 | COMPRESSOR SKID | TO PORTABLE POT | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64001 | 08 | 32 | 6" | WW | 64001 | B4S2 | N | 0 | JWR64003 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.44 | 2 | I | MOD.A | Y | 1 | N | 32-U-023-02 |  | E | N | 000 | N | 87
WW64002 | 08 | 32 | 1-1/2" | WW | 64002 | B4S2 | N | 0 | FROM LC-50010 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64005 | 08 | 32 | 1-1/2" | WW | 64005 | B4S2 | N | 0 | FROM LC-23033 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64010 | 08 | 32 | 1-1/2" | WW | 64010 | B4S2 | N | 0 | FROM LC-23039 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64011 | 08 | 32 | 1-1/2" | WW | 64011 | B4S2 | N | 0 | FROM LC-31030 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW66004 | 08 | 32 | 12" | WW | 66004 | B4S2 | N | 0 | CONCRETE CURB | 4131-ACW-300-CS-206 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.46 | 2 | I | MOD.A | Y | 1 | N | 32-P-021-03 |  | E | N | 000 | N | 87
WW69001 | 08 | 32 | 2" | WW | 69001 | B4S2 | N | 0 | 32-ES-6907 | TO ACC | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.89 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW71001 | 08 | 32 | 1" | WW | 71001 | B4S2 | N | 0 | COMPRESSOR SKID | TO PORTABLE POT | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.50A | 2 | Art 4.3 | NA | N | 1 | N | 32-P-006-04 |  | E | N | 000 | N | 87
WW72001 | 08 | 32 | 1" | WW | 72001 | B4S2 | ET | 30 | 32-PK-7200/TP 010 | - | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.52B | 2 | Art 4.3 | NA | N | 20 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
JWS64049 | 08 | 32 | 1-1/2" | JWS | 64049 | B-1 | N | 0 | JWS64054 | 32-E-2401 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64049 | 08 | 32 | 20" | JWS | 64049 | B-1 | N | 0 | JWS64054 | 32-E-2401 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64065 | 08 | 32 | 3/4" | JWS | 64065 | B-1 | N | 0 | JWS64056 | 32-Z-3300B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64077 | 08 | 32 | 3/4" | JWS | 64077 | B-1 | N | 0 | JWS64054 | 32-E-1450B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-01 |  | E | N | 000 | N | 10
JWS89001 | 08 | 32 | 3" | JWS | 89001 | B-1 | N | 0 | TP-N60101 (32-P-8906A) | TP-N30601 (32-E-8921A HEATING BARREL) | 10.0 | 120.0 | 7.0 | 50.0 |  | 15 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 50 | sh.68F | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 802
LA16003 |  | 32 | 1/2" | LA | 16003 | 4CS2 | HH | 30 | 32-P-1601 | 32-S-1601 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16003 |  | 32 | 1" | LA | 16003 | 4CS2 | HH | 30 | 32-P-1601 | 32-S-1601 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16010 |  | 32 | 1/2" | LA | 16010 | 1FS4 | ET | 30 | 32-P-1600A | LA16025 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16010 |  | 32 | 1" | LA | 16010 | 1FS4 | ET | 30 | 32-P-1600A | LA16025 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
JCHW14001 | 08 | 32 | 2" | JCHW | 14001 | B-1 | CF | 25 | CHWS14021 | CHWR15001 | 9.0 | 100.0 | 6.0 | 3.0 |  | 13.5 | 29.4 | H | JACKET REFR.WATER CHILLED | L | - | - | <1.5 | 3 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-03 |  | E | N | 000 | N | 65
JWR63002 | 08 | 32 | 3/4" | JWR | 63002 | B-1 | N | 0 | 32-E-6350A | JWR63003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64004 | 08 | 32 | 3/4" | JWR | 64004 | B-1 | N | 0 | 32-D-6400 | JWR64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64004 | 08 | 32 | 2" | JWR | 64004 | B-1 | N | 0 | 32-D-6400 | JWR64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64008 | 08 | 32 | 1-1/2" | JWR | 64008 | B-1 | N | 0 | JWR64006 | 32-E-6400C | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR67003 | 08 | 32 | 2" | JWR | 67003 | B-1 | N | 0 | JWR23003 | Blind Flange | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR67003 | 08 | 32 | 4" | JWR | 67003 | B-1 | N | 0 | JWR23003 | Blind Flange | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71001 | 08 | 32 | 3" | JWR | 71001 | B-1 | N | 0 | TP-13, JWR710101 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR72004 | 08 | 32 | 4" | JWR | 72004 | D20S1 | N | 0 | 32-E-7203 | JWR72002 | 33.7/33.7 | 245.0/-45.0 | 5.0 | 40.0 |  | 52.54 | 150.8 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-U-022-02 |  | M | N | 141 | N | 1031
JWS24010 | 08 | 32 | 3" | JWS | 24010 | D20S1 | N | 0 | JWS64051 | 32-E-2400 | 49.0/49.0 | -45.0/150.0 | 5.0 | 30.0 |  | 73.51 | 128.56 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-01 |  | M | N | 000 | N | 1020
BDL43015 | 08 | 32 | 3/4" | BDL | 43015 | B32S1 | N | 0 | PR43028 | BDL31026 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL50001 |  | 32 | 4" | BDL | 50001 | B4S1 | ST | 30 | PR50015 | FL60001 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.34 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
LS63042 |  | 32 | 1-1/2" | LS | 63042 | B-5 | HB | 70 | LS63193 | LS63044 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AE |  | 32 | 3/4" | LS | 630AE | B-5 | HB | 60 | LS63002 | LC5001A | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BF |  | 32 | 1/2" | LS | 630BF | B-5 | HB | 60 | LS63193 | HCM23064 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63192 |  | 32 | 2" | LS | 63192 | B-5 | HB | 80 | LS63189 | 32-1121-S-003 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63199 |  | 32 | 2" | LS | 63199 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63201 |  | 32 | 2" | LS | 63201 | B-5 | HB | 80 | LS01001 | LS6300W | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63203 |  | 32 | 1" | LS | 63203 | B-5 | HB | 70 | LS01001 | LS63074 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS65001 |  | 32 | 3/4" | LS | 65001 | B-5 | HB | 60 | 32-D-6500 | LC65002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.45 | 2 | Art 4.3 | NA | N | NR | N | 32-P-031-01 |  | E | N | 000 | N | 90
LS65001 |  | 32 | 1-1/2" | LS | 65001 | B-5 | HB | 70 | 32-D-6500 | LC65002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.45 | 2 | Art 4.3 | NA | N | NR | N | 32-P-031-01 |  | E | N | 000 | N | 90
LS65003 |  | 32 | 1" | LS | 65003 | B-5 | HB | 70 | LS63064 | LC65001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.45 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
OG43001 | 08 | 32 | 2" | OG | 43001 | C42S1 | N | 0 | PR43028 | OG01004 | 42.0/42.0 | -45.0/150.0 | 4.0 | 70.0 |  | 63.01 | 76.65 | H | OFF GAS | G | - | - | >1.5 | 70 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-U-034-01 |  | G | N | 141 | N | 502 | ,10
OG53003 | 08 | 32 | 3" | OG | 53003 | B4S1 | N | 0 | PR53005 | OG01004 | 7.0 | 165.0 | 5.0 | 10.0 |  | 10.52 | 29.4 | H | OFF GAS | G | - | - | >1.5 | 10 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-U-034-01 |  | C | Y | 141 | N | 526 | 10
P23017 | 08 | 32 | 3/4" | P | 23017 | C42S2 | HB | 30 | P23030 | P31008 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P23017 | 08 | 32 | 4" | P | 23017 | C42S2 | HB | 30 | P23030 | P31008 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P23018 | 7A | 32 | 1" | P | 23018 | 1FS4 | HB | 30 | 32-Z-2300A | P23016 | 42.0/42.0 | -40.0/200.0 | 30.0 | 100.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.17 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 141 | N | 521 | 10
P23019 | 7A | 32 | 1" | P | 23019 | 1FS4 | HB | 30 | 32-Z-2300B | P23015 | 42.0/42.0 | -40.0/200.0 | 30.0 | 100.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.17 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 141 | N | 521 | 10
P23020 |  | 32 | 2" | P | 23020 | C42S5 | HB | 30 | 32-S-2300 | BDL23027 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23021 |  | 32 | 10" | P | 23021 | C42S5 | HB | 40 | P23025 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23022 |  | 32 | 36" | P | 23022 | C42S5 | WS | 50 | 32-R-2300 | TP-1 (P240100) | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 66.72 | 70.15 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.14 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23024 | 08 | 32 | 36" | P | 23024 | C42S5 | WS | 50 | TP-2 (P240101) | 32-E-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 66.72 | 70.15 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23026 |  | 32 | 12" | P | 23026 | C42S5 | HB | 40 | 32-D-2301 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23027 |  | 32 | 30" | P | 23027 | C42S5 | HB | 40 | 32-E-2300 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 66.72 | 68.64 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
PA62077 | 08 | 32 | 1" | PA | 62077 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
IW64076 | 08 | 32 | 3/4" | IW | 64076 | B-1 | N | 0 | IW64003 | 32-US-1124-005 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89022 | 08 | 32 | 3/4" | IW | 89022 | B-1 | N | 0 | IW89020 | US-5111-01 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89023 | 08 | 32 | 3/4" | IW | 89023 | B-1 | N | 0 | IW01001 | 32-US-1211-10 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89024 | 08 | 32 | 3/4" | IW | 89024 | B-1 | N | 0 | IW89023 | 32-US-1211-07 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89025 | 08 | 32 | 3/4" | IW | 89025 | B-1 | N | 0 | IW89023 | 32-US-1211-08 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89028 | 08 | 32 | 1" | IW | 89028 | B-1 | N | 0 | IW01001 | IW89029 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89033 | 08 | 32 | 3/4" | IW | 89033 | B-1 | N | 0 | IW89020 | US-3211-04 EL.10000 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89038 | 08 | 32 | 3/4" | IW | 89038 | B-1 | N | 0 | IW01001 | 32-US-1211-01 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89040 | 08 | 32 | 3/4" | IW | 89040 | B-1 | N | 0 | PA89050 | PA89050 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89043 | 08 | 32 | 3/4" | IW | 89043 | B-1 | N | 0 | IW01001 | 32-US-7112-02 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
ET71039 | 08 | 32 | 2" | ET | 71039 | C3S1 | N | 0 | 32-S-7100A | ET40007 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71049 | 7A | 32 | 3/4" | ET | 71049 | C3S1 | HB | 60 | 32-T-7110B | BDL71025 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71049 | 7A | 32 | 4" | ET | 71049 | C3S1 | HB | 70 | 32-T-7110B | BDL71025 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | Y | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
ET71050 | 7A | 32 | 3" | ET | 71050 | C3S1 | HA | 70 | N72008 | ET71049 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
VA14001 | 08 | 32 | 3" | VA | 14001 | B4S2 | N | 0 | CHWS14012 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.7 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA14005 | 08 | 32 | 2" | VA | 14005 | B4S2 | N | 0 | N14005 | TO SAFE LOCATION OUT SIDE CATALYST BUILDING | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.8 | 2 | NA | NA | NA | 6 | N | 32-P-026-02 |  | E | N | 000 | N | 183
VA14006 | 08 | 32 | 3" | VA | 14006 | B4S2 | N | 0 | CHWS14015 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.8 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA14012 | 08 | 32 | 2" | VA | 14012 | B4S2 | N | 0 | N14020 | TO SAFE LOCATION OUTSIDE BUILDING | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.8 | 2 | NA | NA | NA | 6 | N | 32-P-026-02 |  | E | N | 000 | N | 183
VA16001 | 08 | 32 | 2" | VA | 16001 | B4S2 | N | 0 | 32-D-1602 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.10 | 2 | NA | NA | NA | 6 | N | 32-P-024-01 |  | E | N | 000 | N | 183
VA21004 | 08 | 32 | 3" | VA | 21004 | B4S2 | N | 0 | 32-R-2100 | 32-R-2100 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.12 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA23006 | 08 | 32 | 3" | VA | 23006 | B4S2 | P | 50 | TP 18 (LO230132) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.16B | 2 | NA | NA | NA | 6 | N | 32-P-044-03 |  | E | N | 000 | N | 183
VA24001 | 08 | 32 | 1" | VA | 24001 | B4S2 | N | 0 | CHWR24003 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.19 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA24011 | 08 | 32 | 1" | VA | 24011 | B4S2 | N | 0 | JWR24007 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.20 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
N67003 | 08 | 32 | 1-1/2" | N | 67003 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N6700A | 08 | 32 | 3/4" | N | 6700A | B-1 | N | 0 | N01001 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700U | 08 | 32 | 3/4" | N | 6700U | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67014 | 08 | 32 | 3" | N | 67014 | B-1 | N | 0 | NITROGEN CONNECTION | D-6701A (32-PK-6701) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.103 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N67041 | 08 | 32 | 1" | N | 67041 | B-1 | N | 0 | N67029 | JWR13171 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67046 | 08 | 32 | 1/2" | N | 67046 | B-1 | N | 0 | N01001 | N2 FILTER, N710146 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67046 | 08 | 32 | 2" | N | 67046 | B-1 | N | 0 | N01001 | N2 FILTER, N710146 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
BDL36019 | 08 | 32 | 2" | BDL | 36019 | B32S1 | N | 0 | TP-115 (32-D-3605) | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36021 | 08 | 32 | 2" | BDL | 36021 | B32S1 | N | 0 | TP-120 (32-D-3606) | BDL36015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40028 | 08 | 32 | 3/4" | BDL | 40028 | B32S1 | N | 0 | HD40006 | BDL40036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40036 | 08 | 32 | 8" | BDL | 40036 | B32S1 | N | 0 | BDL40037 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40039 | 08 | 32 | 3/4" | BDL | 40039 | B32S1 | N | 0 | P40034 | BDL40042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40046 | 08 | 32 | 6" | BDL | 40046 | B32S1 | N | 0 | ET40007 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.30 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43020 | 08 | 32 | 1/2" | BDL | 43020 | B32S1 | N | 0 | 32-E-4303 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | I | MOD.A | Y | 1 | N | 32-P-047-03 |  | G | N | 141 | N | 460 | 10
BDL43020 | 08 | 32 | 1-1/2" | BDL | 43020 | B32S1 | N | 0 | 32-E-4303 | BDL43023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | I | MOD.A | Y | 1 | N | 32-P-047-03 |  | G | N | 141 | N | 460 | 10
CO31003 | 08 | 32 | 3/4" | CO | 31003 | 1IS5 | N | 0 | EMERGENCY KILLER SYSTEM CO 10% IN NITROGEN | CO31002 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO42018 | 08 | 32 | 3/4" | CO | 42018 | 1IS5 | N | 0 | CO42019 | CO42017 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42018 | 08 | 32 | 1" | CO | 42018 | 1IS5 | N | 0 | CO42019 | CO42017 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42022 | 08 | 32 | 1/2" | CO | 42022 | 1IS5 | N | 0 | REACTOR EMERGENCY KILLER | CO42018 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
P23029 | 08 | 32 | 3" | P | 23029 | C42S2 | HB | 30 | 32-R-2300 | BDL23071 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P34003 |  | 32 | 8" | P | 34003 | C42S2 | P | 75 | P40038 | 32-S-3400 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.26 | 1 | III | MOD.G | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P34003 |  | 32 | 10" | P | 34003 | C42S2 | P | 100 | P40038 | 32-S-3400 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.26 | 1 | III | MOD.G | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40026 |  | 32 | 1/2" | P | 40026 | QXC25S2 | ST | 30 | 32-Z-4004B | P40040 | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P40026 |  | 32 | 1" | P | 40026 | QXC25S2 | ST | 30 | 32-Z-4004B | P40040 | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P40031 |  | 32 | 1/2" | P | 40031 | C42S3 | WS | 50 | 32-R-4001 | TP-1 (P400100) | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40031 |  | 32 | 3/4" | P | 40031 | C42S3 | ET | 30 | 32-R-4001 | TP-1 (P400100) | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40031 |  | 32 | 32" | P | 40031 | C42S3 | WS | 50 | 32-R-4001 | TP-1 (P400100) | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40031 |  | 32 | 36" | P | 40031 | C42S3 | WS | 50 | 32-R-4001 | TP-1 (P400100) | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40034 |  | 32 | 2" | P | 40034 | C42S2 | ET | 30 | 32-R-4001 | P40037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40034 |  | 32 | 3" | P | 40034 | C42S2 | ET | 30 | 32-R-4001 | P40037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40036 |  | 32 | 3" | P | 40036 | C42S2 | ET | 30 | 32-R-4001 | P40037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40037 |  | 32 | 8" | P | 40037 | C42S2 | P | 75 | P40034 | P40038 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40040 |  | 32 | 1" | P | 40040 | C42S2 | P | 50 | P40025 | P40037 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P40040 |  | 32 | 2" | P | 40040 | C42S2 | P | 50 | P40025 | P40037 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P50017 | 08 | 32 | 4" | P | 50017 | 1CR9 | N | 0 | 32-J-5001 | 32-D-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
WW89002 | 08 | 32 | 4" | WW | 89002 | B4S2 | N | 0 | WW89001 | TP-N52802 (32-Z-8902) | 6.0 | 85.0 | 4.0/0.0 | 60.0/60.0 |  | 4 | 29.4 | N | WASTE WATER | L | - | - | <1.5 | 60 | sh.68P | 2 | Art 4.3 | NA | N | 1 | N | 32-U-046-01 |  | E | N | 000 | N | 5420
CWR94005 | 08 | 32 | 3/4" | CWR | 94005 | B-1 | N | 0 | 32-E-9002 | CWR94004 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR94005 | 08 | 32 | 2" | CWR | 94005 | B-1 | N | 0 | 32-E-9002 | CWR94004 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
LA31001 |  | 32 | 1/2" | LA | 31001 | 1FS4 | ET | 30 | LA23006 | PR24047 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.16 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA84008 |  | 32 | 1" | LA | 84008 | 4CS2 | ET | 30 | 32-S-8402A | TP-N11216 (32-H-8901) | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84012 |  | 32 | 1/2" | LA | 84012 | 4CS2 | ET | 30 | DRUM | 32-P-8403 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84012 |  | 32 | 1-1/2" | LA | 84012 | 4CS2 | ET | 30 | DRUM | 32-P-8403 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84039 |  | 32 | 1/2" | LA | 84039 | 4CS2 | ET | 30 | 32-P-8402B | 32-Z-8402B | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84039 |  | 32 | 3/4" | LA | 84039 | 4CS2 | ET | 30 | 32-P-8402B | 32-Z-8402B | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LC24012 |  | 32 | 3/4" | LC | 24012 | B-5 | HB | 30 | LS24014 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-046-01 |  | E | Y | 000 | N | 130
LC31005 |  | 32 | 3/4" | LC | 31005 | B-5 | HB | 30 | LS31024 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31008 |  | 32 | 3/4" | LC | 31008 | B-5 | HB | 30 | LS31021 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31033 | 08 | 32 | 1" | LC | 31033 | B-5 | P | 50 | LS31038 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50007 |  | 32 | 1-1/2" | LC | 50007 | B-5 | P | 50 | P50015 | TO TRENCH | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-01 |  | E | Y | 000 | N | 133 | 77
VZ15004 |  | 32 | 3/4" | VZ | 15004 | B4S2 | EH | 30 | 32-D-1501 | 32-D-1501 | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | NA | NA | NA | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 239 | 23,25
VZ16007 |  | 32 | 3/4" | VZ | 16007 | 4CS2 | ET | 30 | 32-D-1600 | 32-D-1600 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 400
VZ16007 |  | 32 | 1" | VZ | 16007 | 4CS2 | ET | 30 | 32-D-1600 | 32-D-1600 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 400
VZ35002 | 08 | 32 | 1/2" | VZ | 35002 | B4S1 | N | 0 | 32-D-3500 | 32-D-3500 | 5.0 | 120.0 | 0.5 | 45.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | G | - | - | >1.5 | 45 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 378 | ,10
VZ40006 |  | 32 | 1" | VZ | 40006 | C42S2 | HB | 30 | 32-R-4001 | 32-R-4001 | 20.0/20.0 | 120.0/-40.0 | 14.0/14.0 | 110.0/80.0 |  | 30 | 76.65 | H | VESSEL TRIM | GS | - | - | >1.5 | 80 | sh.31 | 1 | Art 4.3 | NA | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 428 | 10,11,13,39
VZ51006 | 08 | 32 | 1/2" | VZ | 51006 | B4S1 | ST | 30 | 32-D-5101 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ51006 | 08 | 32 | 3/4" | VZ | 51006 | B4S1 | ST | 30 | 32-D-5101 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ51006 | 08 | 32 | 1" | VZ | 51006 | B4S1 | ST | 30 | 32-D-5101 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ66004 | 08 | 32 | 2" | VZ | 66004 | B4S2 | HH | 30 | 32-D-6600 | - | 3.5 | 180.0 | 0.0 | 30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 233 | 23,25
VZ80006 | 08 | 32 | 3" | VZ | 80006 | 4CS9 | HA | 30 | 32-D-8002B | 32-D-8002B | 0.2/-0.005 | 100.0/100.0 | 0.12 | 90.0 |  | 0 | 0 | V | VESSEL TRIM | GS | - | - | >1.5 | 90 | sh.58 | 1 | NA | NA | NA | 27 | N | 32-P-060-01 |  | G-2 | N | 110 | N | 444 | 6,23,10,11,25,28,13
WW45001 | 08 | 45 | 3" | WW | 45001 | B4S2 | N | 0 | 45-P-4511 | WW45002 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-050-01 |  | E | N | 000 | N | 87
LS71011 |  | 32 | 1/2" | LS | 71011 | B-5 | HB | 60 | LS63059 | LC71001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.48 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS72004 |  | 32 | 2" | LS | 72004 | D1S1 | HB | 50 | 32-E-7201 | LS72003 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.51 | 1 | II | MOD.A2 | Y | 20 | Y | 32-U-052-01 |  | E | N | 041 | N | 1090
LS89036 |  | 32 | 3/4" | LS | 89036 | B-5 | HB | 60 | LS89035 | US-..... | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LO32002 | 08 | 32 | 1/2" | LO | 32002 | QXB-55 | N | 0 | TP-18A, LO320115 (LO320315) | TP-17A, PK-3600 | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO32002 | 08 | 32 | 1-1/2" | LO | 32002 | QXB-55 | N | 0 | TP-18A, LO320115 (LO320315) | TP-17A, PK-3600 | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO32010 | 08 | 32 | 1/2" | LO | 32010 | QXB-55 | N | 0 | TP 12B (32-PK-3200 B)) | TP 13B (LO320106) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
P23028 |  | 32 | 3" | P | 23028 | C42S5 | HB | 30 | 32-D-2301 | P23027 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23029 | 08 | 32 | 2" | P | 23029 | C42S2 | HB | 30 | 32-R-2300 | BDL23071 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P23030 | 08 | 32 | 4" | P | 23030 | C42S2 | HB | 30 | 32-R-2300 | BDL23068 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P23031 | 08 | 32 | 4" | P | 23031 | C42S2 | HB | 30 | 32-R-2300 | BDL23067 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P23032 | 08 | 32 | 4" | P | 23032 | C42S2 | HB | 30 | 32-R-2300 | BDL23069 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P31007 |  | 32 | 8" | P | 31007 | C42S2 | P | 75 | P31012 | P34003 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P31009 |  | 32 | 4" | P | 31009 | C42S2 | P | 50 | P31012 | 32-R-4001 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
P31010 |  | 32 | 1" | P | 31010 | QXC25S2 | P | 50 | 32-Z-3100A | BDL31026 | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P31012 |  | 32 | 2-1/2" | P | 31012 | C42S2 | P | 50 | 32-S-3100 | P31007 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P31016 | 08 | 32 | 1" | P | 31016 | QXC25S2 | N | 0 | CD31004 | 32-Z-3100B | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P40024 |  | 32 | 30" | P | 40024 | C42S3 | HB | 40 | 32-E-4001 | 32-R-4001 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 37.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40025 |  | 32 | 3/4" | P | 40025 | C42S1 | HB | 30 | P40030 | P40032 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
P40025 |  | 32 | 2" | P | 40025 | C42S1 | HB | 30 | P40030 | P40032 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
VA32002 | 08 | 32 | 2" | VA | 32002 | B4S2 | N | 0 | JWR32005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.24 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA32003 | 08 | 32 | 2" | VA | 32003 | B4S2 | N | 0 | 32-D-3204 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.24E | 2 | NA | NA | NA | 6 | N | 32-P-047-04 |  | E | N | 000 | N | 183
VA33001 | 08 | 32 | 1/2" | VA | 33001 | B4S2 | N | 0 | LS33001 | AT SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.25 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA33002 | 08 | 32 | 2" | VA | 33002 | B4S2 | N | 0 | JWR33001 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.25 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA33003 | 08 | 32 | 1" | VA | 33003 | B-1 | N | 0 | TO ATMOSPHERE | 32-P-3300A | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.25 | 2 | NA | NA | NA | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 181
N67068 | 08 | 32 | 1/2" | N | 67068 | B-1 | N | 0 | N67003 | TP-009 (N720148) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67073 | 08 | 32 | 1" | N | 67073 | B-1 | N | 0 | N67020 | TP-6 (N240173) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67092 | 08 | 32 | 3/4" | N | 67092 | B-1 | N | 0 | N67028 | BDL60042 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67096 | 08 | 32 | 3/4" | N | 67096 | B-1 | N | 0 | N67029 | BDL60046 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67096 | 08 | 32 | 1" | N | 67096 | B-1 | N | 0 | N67029 | BDL60046 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67101 | 08 | 32 | 3/4" | N | 67101 | B-1 | N | 0 | N67029 | BDL60050 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67103 | 08 | 32 | 1" | N | 67103 | B-1 | N | 0 | N67029 | BDL60052 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67110 | 08 | 32 | 1" | N | 67110 | B-1 | N | 0 | N67046 | BDL60055 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67111 | 08 | 32 | 1" | N | 67111 | B-1 | N | 0 | N67013 | BDL60056 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N67114 | 08 | 32 | 1" | N | 67114 | B-1 | N | 0 | N67039 | BDL60059 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
BDL43023 | 08 | 32 | 3/4" | BDL | 43023 | B32S1 | N | 0 | 32-P-4300 | BDL43019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL51009 |  | 32 | 2" | BDL | 51009 | B4S1 | ST | 30 | BDL50002 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL51023 | 08 | 32 | 3/4" | BDL | 51023 | B4S1 | N | 0 | PR51017 | BDL60038 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.28A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL60020 | 08 | 32 | 10" | BDL | 60020 | B32S1 | N | 0 | BDL33002 | FL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL60020 | 08 | 32 | 18" | BDL | 60020 | B32S1 | N | 0 | BDL33002 | FL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL60023 | 08 | 32 | 1-1/2" | BDL | 60023 | B32S1 | N | 0 | BDL14001 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60041 | 08 | 32 | 1" | BDL | 60041 | B32S1 | N | 0 | N67093 | BDL60033 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60048 | 08 | 32 | 1" | BDL | 60048 | B32S1 | N | 0 | N67105 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60063 | 08 | 32 | 1" | BDL | 60063 | B32S1 | N | 0 | N6700Y | BDL60062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61007 | 08 | 32 | 8" | BDL | 61007 | B32S1 | N | 0 | TP-018 (32-PSV-6169) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42C | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61015 | 08 | 32 | 2" | BDL | 61015 | B32S1 | N | 0 | TP-028 (32-D-6108) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61023 | 08 | 32 | 3" | BDL | 61023 | B32S1 | N | 0 | PR61006 | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61023 | 08 | 32 | 6" | BDL | 61023 | B32S1 | N | 0 | PR61006 | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42E | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL65002 | 08 | 32 | 2" | BDL | 65002 | B4S1 | N | 0 | 32-D-6500 | BDL65003 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 1 | N | 32-P-031-01 |  | G | N | 141 | N | 470 | ,10
BDL71021 | 08 | 32 | 3/4" | BDL | 71021 | B4S1 | N | 0 | ET71037 | BDL71034 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
IA62002 | 08 | 32 | 1-1/2" | IA | 62002 | C3S1 | N | 0 | TP-2 (IA620102) | 32-D-6200 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA6200H | 08 | 32 | 1" | IA | 6200H | B-13 | N | 0 | IA6200K | 32-IAM-112 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200K | 08 | 32 | 1-1/2" | IA | 6200K | B-13 | N | 0 | IA62077 | 32-IAM-043 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200T | 08 | 32 | 1" | IA | 6200T | B-13 | N | 0 | IA62078 | 32-IAM-008 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62053 | 08 | 32 | 1/2" | IA | 62053 | B-13 | N | 0 | IA62076 | TP-126(32-PCV-3698) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62058 | 08 | 32 | 1" | IA | 62058 | B-13 | N | 0 | IA62077 | TO PROPYLENE DRYING TOWERS T-7202A/B AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62074 | 08 | 32 | 1" | IA | 62074 | B-13 | N | 0 | IA62001 | IA62012 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62077 | 08 | 32 | 2" | IA | 62077 | B-13 | N | 0 | IA62001 | IA6200K | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62097 | 08 | 32 | 3/4" | IA | 62097 | B-13 | N | 0 | IA62076 | 20 LTR TANK | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620AU | 08 | 32 | 3/4" | IA | 620AU | B-13 | N | 0 | IA62080 | 32-IAT-067 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA68C05 | 08 | 32 | 3/4" | IA | 68C05 | B-13 | N | 0 | 20 LTR TANK | IA68C02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-18 |  | - | N | 000 | - | 200
IA68C05 | 08 | 32 | 1-1/2" | IA | 68C05 | B-13 | N | 0 | 20 LTR TANK | IA68C02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-18 |  | - | N | 000 | - | 200
CWS64001 | 08 | 32 | 1-1/2" | CWS | 64001 | B-1 | N | 0 | CWS01010 | 32-E-6400A | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64001 | 08 | 32 | 20" | CWS | 64001 | B-1 | N | 0 | CWS01010 | 32-E-6400A | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64002 | 08 | 32 | 14" | CWS | 64002 | B-1 | N | 0 | CWS01010 | 32-E-6400B | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64003 | 08 | 32 | 1-1/2" | CWS | 64003 | B-1 | N | 0 | CWS01010 | 32-E-6400C | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64003 | 08 | 32 | 20" | CWS | 64003 | B-1 | N | 0 | CWS01010 | 32-E-6400C | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-01 |  | E | N | 000 | N | 12
CWS64012 | 08 | 32 | 3/4" | CWS | 64012 | B-1 | N | 0 | CWS64006 | 32-E-9002 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
LC63032 |  | 32 | 3/4" | LC | 63032 | B-5 | P | 50 | LC63031 | 32-P-6300A | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 136
LC63032 |  | 32 | 3" | LC | 63032 | B-5 | P | 50 | LC63031 | 32-P-6300A | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 136
LC63034 |  | 32 | 1-1/2" | LC | 63034 | B-5 | P | 50 | 32-P-6300B | LC63035 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63036 |  | 32 | 3/4" | LC | 63036 | B-5 | P | 50 | LC63034 | LC63037 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63036 |  | 32 | 3" | LC | 63036 | B-5 | P | 50 | LC63034 | LC63037 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63042 |  | 32 | 3" | LC | 63042 | B-5 | P | 50 | LC63041 | 32-P-6300B | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 136
LC63059 |  | 32 | 3/4" | LC | 63059 | B-5 | P | 50 | LC01001 | 32-D-6300 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | I | MOD.A | Y | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63059 |  | 32 | 6" | LC | 63059 | B-5 | P | 50 | LC01001 | 32-D-6300 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | I | MOD.A | Y | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
PX86018 |  | 32 | 1/2" | PX | 86018 | QXC25S1 | JP | 0 | PX86022 | TP-N11212 (32-H-8901) | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86019 |  | 32 | 1/2" | PX | 86019 | QXC25S1 | JP | 0 | PX86024 | PX86037 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86020 |  | 32 | 1/2" | PX | 86020 | QXC25S1 | JP | 0 | PX86021 | PX86002 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86021 |  | 32 | 1/2" | PX | 86021 | QXC25S1 | JP | 0 | 32-P-8600A | 32-Z-8600A | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86022 |  | 32 | 1/2" | PX | 86022 | QXC25S1 | ET | 30 | O67010 | PX86018 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
ET22010 | 08 | 32 | 3/4" | ET | 22010 | 1FS4 | N | 0 | ET71035 | ET22007 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
ET22010 | 08 | 32 | 1-1/2" | ET | 22010 | 1FS4 | N | 0 | ET71035 | ET22007 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
WW64006 | 08 | 32 | 1-1/2" | WW | 64006 | B4S2 | N | 0 | FROM LC-50005 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64012 | 08 | 32 | 1-1/2" | WW | 64012 | B4S2 | N | 0 | FROM LC-23053 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
BDL01021 | 08 | 32 | 3/4" | BDL | 01021 | B32S1 | N | 0 | PR01003 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01039 | 08 | 32 | 1" | BDL | 01039 | B32S1 | N | 0 | BDL01003 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
LO89007 | 08 | 32 | 3/4" | LO | 89007 | QXB-55 | N | 0 | TP-N20351 (32-Z-8900) | TP-N20451 (32-P-8902A) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LO89007 | 08 | 32 | 6" | LO | 89007 | QXB-55 | N | 0 | TP-N20351 (32-Z-8900) | TP-N20451 (32-P-8902A) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
N02001 | 08 | 32 | 3/4" | N | 02001 | B-1 | N | 0 | N67013 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N12004 | 08 | 32 | 1" | N | 12004 | 1CS2 | N | 0 | N67055 | 32-D-1200C | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-022-01 |  | M | N | 000 | N | 166
N12017 | 08 | 32 | 1-1/2" | N | 12017 | 1CS2 | N | 0 | 32-D-1200A | N12009 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12017 | 08 | 32 | 2" | N | 12017 | 1CS2 | N | 0 | 32-D-1200A | N12009 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12024 | 08 | 32 | 2" | N | 12024 | 1CS2 | N | 0 | 32-D-1200C | N12009 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N12030 | 08 | 32 | 3/4" | N | 12030 | 1CS2 | N | 0 | N12025 | 32-LT-1205 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N14022 | 08 | 32 | 1/2" | N | 14022 | 1CS2 | N | 0 | N14021 | CATALYST DRUM | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N14026 | 08 | 32 | 1/2" | N | 14026 | 1CS2 | N | 0 | CT14005 | VA14003 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14026 | 08 | 32 | 1-1/2" | N | 14026 | 1CS2 | N | 0 | CT14005 | VA14003 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
N14026 | 08 | 32 | 2" | N | 14026 | 1CS2 | N | 0 | CT14005 | VA14003 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.7 | 2 | NA | NA | NA | 5 | N | 32-P-026-01 |  | M | N | 000 | N | 154
CD34019 | 08 | 32 | 1/2" | CD | 34019 | 1CS2 | ET | 30 | NITROGEN CONNECTION | CD34009 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD36001 | 08 | 32 | 1" | CD | 36001 | 1CS2 | N | 0 | FX-3601 | PR36016 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.28 | 2 | Art 4.3 | NA | N | NR | N | 32-P-048-02 |  | F | N | 100 | N | 288
CHWR21007 |  | 32 | 1-1/2" | CHWR | 21007 | B-1 | CF | 25 | CHWR21006 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21007 |  | 32 | 4" | CHWR | 21007 | B-1 | CF | 25 | CHWR21006 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR24003 |  | 32 | 6" | CHWR | 24003 | C42S1 | CF | 40 | 32-E-2404 | CHWR24004 | 42.0/42.0 | 150.0/-45.0 | 2.0 | 7.0 |  | 63.01 | 76.65 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 7 | sh.19 | 2 | II | MOD.A2 | Y | 20 | Y | 32-U-023-02 |  | M | N | 010 | N | 1054
CHWR61006 | 08 | 32 | 6" | CHWR | 61006 | B-1 | N | 0 | CHWR61014 | CHWR61007 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
P40025 |  | 32 | 4" | P | 40025 | C42S1 | HB | 30 | P40030 | P40032 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
P40028 |  | 32 | 1/2" | P | 40028 | QXC25S2 | ST | 30 | P40030 | 32-Z-4004A | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P40029 |  | 32 | 1/2" | P | 40029 | QXC25S2 | ET | 30 | 32-Z-4004A | P40040 | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P40029 |  | 32 | 1" | P | 40029 | QXC25S2 | ST | 30 | 32-Z-4004A | P40040 | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P40031 |  | 32 | 3/4" | P | 40031 | C42S3 | WS | 50 | 32-R-4001 | TP-1 (P400100) | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40032 |  | 32 | 6" | P | 40032 | C42S2 | ET | 30 | P40041 | VZ40006 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
JCHW14001 | 08 | 32 | 1/2" | JCHW | 14001 | B-1 | CF | 25 | CHWS14021 | CHWR15001 | 9.0 | 100.0 | 6.0 | 3.0 |  | 13.5 | 29.4 | H | JACKET REFR.WATER CHILLED | L | - | - | <1.5 | 3 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-03 |  | E | N | 000 | N | 65
JCHW14002 |  | 32 | 1/2" | JCHW | 14002 | B-1 | CF | 25 | CT14009 | CT14004 | 9.0 | 100.0 | 6.0 | 3.0 |  | 13.5 | 29.4 | H | JACKET REFR.WATER CHILLED | L | - | - | <1.5 | 3 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-03 |  | E | N | 000 | N | 65
JCHW15001 | 08 | 32 | 1" | JCHW | 15001 | B-1 | CF | 25 | - | CHWR20001 | 9.0 | 100.0 | 6.0 | 3.0 |  | 13.5 | 29.4 | H | JACKET REFR.WATER CHILLED | L | - | - | <1.5 | 3 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-04 |  | E | N | 000 | N | 65
JCW86011 |  | 32 | 1-1/2" | JCW | 86011 | B-1 | HB | 30 | JCW86012 | PX86018 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86013 |  | 32 | 1-1/2" | JCW | 86013 | B-1 | HB | 30 | JCW86016 | JCW86012 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
LO32003 | 08 | 32 | 1-1/2" | LO | 32003 | QXB-55 | N | 0 | LO32004 | TP-16A, LO320108 (LO320308) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO32005 | 08 | 32 | 2" | LO | 32005 | QXB-55 | N | 0 | TP-12A, PK-3600, C40, NEA STANDARD COARSE STRAINER | TP-13A, 32-P-3202A | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO32008 | 08 | 32 | 1-1/2" | LO | 32008 | QXB-55 | N | 0 | TP-15B (32-P-3201B) | TP-16B (LO320108) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LO32009 | 08 | 32 | 2" | LO | 32009 | QXB-55 | N | 0 | LO32010 | TP 14B (P3201B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
FL60001 |  | 32 | 1/2" | FL | 60001 | B32S1 | HB | 30 | BDL60002 | 32-D-6001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | III | MOD.G | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 490 | 10
FL60001 |  | 32 | 6" | FL | 60001 | B32S1 | HB | 30 | BDL60002 | 32-D-6001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | III | MOD.G | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 490 | 10
FO35015 | 08 | 32 | 1/2" | FO | 35015 | B4S2 | N | 0 | FO11007 | 32-D-6500 | 6.0 | 180.0 | 0.5/0.5 | 40.0/50.0 |  | 9.03 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.45 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 210 | 23,25
VA64003 | 08 | 32 | 1" | VA | 64003 | B4S2 | N | 0 | CWR64016 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.44 | 2 | NA | NA | NA | 6 | N | 32-U-021-01 |  | E | N | 000 | N | 183
VA66002 |  | 32 | 2" | VA | 66002 | B4S2 | HB | 40 | 32-D-6600 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.46 | 2 | NA | NA | NA | 20 | N | 32-P-021-03 |  | E | N | 000 | N | 183
VA71006 | 08 | 32 | 1" | VA | 71006 | B4S2 | N | 0 | LS71010 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.48 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA71008 | 08 | 32 | 1" | VA | 71008 | B4S2 | N | 0 | VA710116 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.50A | 2 | NA | NA | NA | 6 | N | 32-P-006-04 |  | E | N | 000 | N | 183
VA72002 | 08 | 32 | 3" | VA | 72002 | B4S2 | N | 0 | JWR72007 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.51 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA72003 | 08 | 32 | 1" | VA | 72003 | B4S2 | N | 0 | LS72002 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.51 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA80010 | 08 | 32 | 1" | VA | 80010 | B4S2 | N | 0 | CWR80005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.57 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
VA80011 | 08 | 32 | 1" | VA | 80011 | B4S2 | N | 0 | CWR80006 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.57 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
VA81014 | 08 | 32 | 4" | VA | 81014 | B-1 | N | 0 | TP-022 (PSV-8104A) | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.60A | 2 | NA | NA | NA | 1 | N | 32-P-061-02 |  | E | N | 000 | N | 181
VA81015 | 08 | 32 | 4" | VA | 81015 | B-1 | N | 0 | 32-PSV-8104B | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.60 | 2 | NA | NA | NA | 1 | N | 32-P-061-02 |  | E | N | 000 | N | 181
HCM24056 |  | 32 | 4" | HCM | 24056 | D20S1 | P | 50 | HCM24094 | 32-T-4300 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24061 | 08 | 32 | 1/2" | HCM | 24061 | 3FS4 | HB | 30 | TP-2 (HCM240161) | HCM24098 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM24061 | 08 | 32 | 1" | HCM | 24061 | 3FS4 | HB | 30 | TP-2 (HCM240161) | HCM24098 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM24061 | 08 | 32 | 1-1/2" | HCM | 24061 | 3FS4 | HB | 30 | TP-2 (HCM240161) | HCM24098 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM24063 |  | 32 | 4" | HCM | 24063 | 3FS4 | HB | 40 | 32-T-2401 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 122.48 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 27 | Y | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24063 |  | 32 | 6" | HCM | 24063 | 3FS4 | HB | 40 | 32-T-2401 | 32-E-2404 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 122.48 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 27 | Y | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24064 |  | 32 | 1/2" | HCM | 24064 | 3FS4 | CF | 25 | 32-E-2404 | HCM24055 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24064 |  | 32 | 1" | HCM | 24064 | 3FS4 | CF | 25 | 32-E-2404 | HCM24055 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24064 |  | 32 | 2" | HCM | 24064 | 3FS4 | CF | 25 | 32-E-2404 | HCM24055 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24067 |  | 32 | 10" | HCM | 24067 | C42S1 | HB | 40 | 32-T-2401 | BDL24063 | 42.0/42.0 | -45.0/100.0 | 35.0/35.0 | 75.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 20 | Y | 32-P-045-01 |  | G | Y | 141 | N | 529 | 10
HCM24070 |  | 32 | 2" | HCM | 24070 | D20S1 | HB | 30 | HCM24057 | BDL24070 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24072 |  | 32 | 3/4" | HCM | 24072 | D20S1 | P | 50 | 32-S-2400 | HCM24073 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24072 |  | 32 | 8" | HCM | 24072 | D20S1 | P | 75 | 32-S-2400 | HCM24073 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24073 |  | 32 | 4" | HCM | 24073 | D20S1 | P | 50 | HCM24072 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24073 |  | 32 | 8" | HCM | 24073 | D20S1 | P | 75 | HCM24072 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24076 |  | 32 | 1-1/2" | HCM | 24076 | D20S1 | HB | 30 | 32-T-2400 | BDL24079 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
IA68D05 | 08 | 45 | 1-1/2" | IA | 68D05 | B-13 | N | 0 | 20 LTR TANK | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68H17 | 08 | 32 | 1" | IA | 68H17 | B-13 | N | 0 | IA68H24 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I32 | 08 | 32 | 1" | IA | 68I32 | B-13 | N | 0 | IA68I20 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68K08 | 08 | 32 | 1/2" | IA | 68K08 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68M08 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68K08 | 08 | 32 | 1" | IA | 68K08 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68M08 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M07 | 08 | 32 | 1" | IA | 68M07 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M11 | 08 | 32 | 1" | IA | 68M11 | B-13 | N | 0 | IA68N35 | IA68N36 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68M39 | 08 | 32 | 1" | IA | 68M39 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68P03 | 08 | 32 | 1" | IA | 68P03 | B-13 | N | 0 | IA68P02 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P09 | 08 | 32 | 1" | IA | 68P09 | B-13 | N | 0 | IA68P06 | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P11 | 08 | 32 | 1/2" | IA | 68P11 | B-13 | N | 0 | IA68P10 | IA68P10 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P11 | 08 | 32 | 1" | IA | 68P11 | B-13 | N | 0 | IA68P10 | IA68P10 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P13 | 08 | 32 | 1" | IA | 68P13 | B-13 | N | 0 | IA68P12 | IA68P12 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Q02 | 08 | 32 | 1" | IA | 68Q02 | B-13 | N | 0 | IA68Q04 | IA68Q04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
PCW89015 | 08 | 32 | 12" | PCW | 89015 | 1CS2 | P | 100 | TP-N51705 (XV-8941) | PCW89012 | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
VZ43002 | 08 | 32 | 2" | VZ | 43002 | C42S1 | HB | 30 | 32-T-4300 | - | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
VZ50007 | 08 | 32 | 4" | VZ | 50007 | 1CR9 | ST | 40 | 32-D-5011 | 32-J-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 0 | 0 | V | VESSEL TRIM | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-2 | N | 141 | N | 442 | ,16,10,11,13
VZ50008 |  | 32 | 1" | VZ | 50008 | 1CR9 | HB | 30 | 32-D-5001 | 32-D-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | VESSEL TRIM | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-2 | N | 141 | N | 441 | 16,10,11,13
VZ50008 |  | 32 | 2" | VZ | 50008 | 1CR9 | HB | 40 | 32-D-5001 | 32-D-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | VESSEL TRIM | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-2 | N | 141 | N | 441 | 16,10,11,13
VZ50009 |  | 32 | 2" | VZ | 50009 | 3CS6 | HB | 80 | 32-S-5001 | 32-S-5001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 11.02 | 28.5 | H | VESSEL TRIM | G | - | - | >1.5 | 200 | sh.34 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | M | N | 000 | N | 99
VZ50010 | 08 | 32 | 1" | VZ | 50010 | B4S2 | N | 0 | 32-D-5002 | FLANGE | 5.0/-1.0 | 180.0/180.0 | 0.2 | 80.0 |  | 7.52 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 80 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 29
VZ50011 |  | 32 | 1-1/2" | VZ | 50011 | B4S2 | HB | 30 | 32-T-5001 | 32-T-5001 | 5.0/-1.0 | 180.0/180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 28
VZ51004 | 08 | 32 | 1" | VZ | 51004 | B4S1 | ST | 30 | 32-D-5102 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ51007 | 08 | 32 | 3/4" | VZ | 51007 | B4S1 | ST | 30 | 32-D-5104 | 32-D-5104 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 0 | 0 | V | VESSEL TRIM | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
CWS86019 | 08 | 32 | 3/4" | CWS | 86019 | B-1 | N | 0 | CWS86017 | CWS86018 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89035 | 08 | 32 | 1" | CWS | 89035 | B-1 | N | 0 | CWS64010 | TP-N21105 (E-8903) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
JWR33002 | 08 | 32 | 3" | JWR | 33002 | B-1 | N | 0 | JWR33001 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR37006 | 08 | 32 | 3/4" | JWR | 37006 | B-1 | N | 0 | 32-Z-4300 | JWR40003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR43002 | 08 | 32 | 4" | JWR | 43002 | B-1 | N | 0 | JWR43001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
PX86023 |  | 32 | 1/2" | PX | 86023 | QXC25S1 | JP | 0 | PX86021 | PX86020 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86023 |  | 32 | 1" | PX | 86023 | QXC25S1 | JP | 0 | PX86021 | PX86020 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86024 |  | 32 | 1/2" | PX | 86024 | QXC25S1 | JP | 0 | PX86025 | PX86020 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86025 |  | 32 | 1/2" | PX | 86025 | QXC25S1 | JP | 0 | PX86027 | JCW86017 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86026 |  | 32 | 1/2" | PX | 86026 | QXC25S1 | JP | 0 | PX86027 | PX86025 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86027 | 08 | 32 | 1/2" | PX | 86027 | QXC25S1 | N | 0 | 32-P-8600B | 32-Z-8600B | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86028 | 08 | 32 | 3/4" | PX | 86028 | QXC25S1 | N | 0 | 32-D-8600 | CONCRETE CURB | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86029 | 08 | 32 | 3/4" | PX | 86029 | QXC25S1 | N | 0 | PX86030 | 32-P-8600A | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86030 | 08 | 32 | 3/4" | PX | 86030 | QXC25S1 | N | 0 | PX86032 | CWR86001 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86031 | 08 | 32 | 3/4" | PX | 86031 | QXC25S1 | N | 0 | PX86030 | 32-P-8600B | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86032 | 08 | 32 | 1/2" | PX | 86032 | QXC25S1 | N | 0 | 32-D-8600 | PX86030 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86034 | 08 | 32 | 1/2" | PX | 86034 | QXC25S1 | N | 0 | PORTABLE CONTAINER | 32-P-8601 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86035 | 08 | 32 | 1/2" | PX | 86035 | QXC25S1 | N | 0 | 32-P-8601 | PX86036 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86037 | 08 | 32 | 1/2" | PX | 86037 | QXC25S1 | N | 0 | PX86019 | PX86002 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
ET71036 | 08 | 32 | 3/4" | ET | 71036 | D1S1 | ST | 30 | ET71035 | ET71037 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 153.15 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 20 | N | 32-P-006-03 |  | C | N | 041 | N | 325 | ,10
ET71036 | 08 | 32 | 2" | ET | 71036 | D1S1 | ST | 30 | ET71035 | ET71037 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 153.15 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-006-03 |  | C | N | 041 | N | 325 | ,10
LO32003 | 08 | 32 | 1/2" | LO | 32003 | QXB-55 | N | 0 | LO32004 | TP-16A, LO320108 (LO320308) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO32004 | 08 | 32 | 2" | LO | 32004 | QXB-55 | N | 0 | TP-15A, 32-P-3201A | TP-14A, 32-P-3201A | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO32008 | 08 | 32 | 2" | LO | 32008 | QXB-55 | N | 0 | TP-15B (32-P-3201B) | TP-16B (LO320108) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LPN10001 | 08 | 32 | 1/2" | LPN | 10001 | 1CS2 | N | 0 | LPN02001 | LPN10014 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN10001 | 08 | 32 | 1" | LPN | 10001 | 1CS2 | N | 0 | LPN02001 | LPN10014 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN11002 | 08 | 32 | 1-1/2" | LPN | 11002 | 3DS3 | N | 0 | LPN11010 | 32-D-1100 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LS13001 |  | 32 | 3/4" | LS | 13001 | B-5 | HB | 60 | LS63069 | LS13002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13003 |  | 32 | 3/4" | LS | 13003 | B-5 | HB | 60 | LS13002 | JLS13001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23021 |  | 32 | 3/4" | LS | 23021 | B-5 | HB | 60 | JLS23008 | LC23020 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
CHWR14005 |  | 32 | 3/4" | CHWR | 14005 | B-1 | CF | 25 | 32-D-1401A | VA14008 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR14006 |  | 32 | 3/4" | CHWR | 14006 | B-1 | CF | 25 | 32-D-1401B | VA14007 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15003 | 08 | 32 | 1/2" | CHWR | 15003 | B-1 | CF | 25 | CT15012 | CHWR15002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61007 | 08 | 32 | 2" | CHWR | 61007 | B-1 | N | 0 | VENT | WW61001 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
CHWS14004 |  | 32 | 1-1/2" | CHWS | 14004 | B-1 | HA | 30 | 32-P-1400B | 32-E-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14008 |  | 32 | 3/4" | CHWS | 14008 | B-1 | HA | 30 | CHWS14012 | 32-P-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14008 |  | 32 | 2" | CHWS | 14008 | B-1 | HA | 30 | CHWS14012 | 32-P-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14015 |  | 32 | 3/4" | CHWS | 14015 | B-1 | HA | 30 | 32-D-1400B | CHWS14010 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS14015 |  | 32 | 1-1/2" | CHWS | 14015 | B-1 | HA | 30 | 32-D-1400B | CHWS14010 | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 52
CHWS15001 | 08 | 32 | 1/2" | CHWS | 15001 | B-1 | CF | 25 | CHWS14007 | CHW1525 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWR65001 |  | 32 | 3/4" | CHWR | 65001 | B-1 | CF | 25 | 32-D-6500 | CHWR65003 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWS14022 |  | 32 | 1-1/2" | CHWS | 14022 | B-1 | HA | 30 | 32-E-1400A | 32-D-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14022 |  | 32 | 4" | CHWS | 14022 | B-1 | HA | 30 | 32-E-1400A | 32-D-1400A | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS21004 | 08 | 32 | 6" | CHWS | 21004 | B-5 | N | 0 | JLS21002 | CHWS21005 | 9.0 | 280.0 | 6.0/6.0 | 10.0/170.0 |  | 14.51 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 10 | sh.12 | 2 | I | MOD.A | Y | 6 | N | 32-U-023-01 |  | A | N | 010 | N | 56
CHWS61001 |  | 32 | 1" | CHWS | 61001 | B-1 | CF | 25 | 32-D-6100 | 32-P-6100A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61001 |  | 32 | 10" | CHWS | 61001 | B-1 | CF | 40 | 32-D-6100 | 32-P-6100A | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61013 |  | 32 | 8" | CHWS | 61013 | B-1 | CF | 40 | CHWS61001 | 32-P-6100B | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61022 |  | 32 | 3/4" | CHWS | 61022 | B-1 | CF | 25 | CHWS61029 | CHWS20005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61026 |  | 32 | 1" | CHWS | 61026 | B-1 | CF | 25 | CHWS61027 | 32-D-6500 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61030 | 08 | 32 | 3/4" | CHWS | 61030 | C42S1 | CF | 25 | TP-010, E-6102 | TP-032 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 5.5 | 2.0 |  | 28.05 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42E | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | M | N | 010 | N | 1057
CHWS61030 | 08 | 32 | 8" | CHWS | 61030 | C42S1 | CF | 40 | TP-010, E-6102 | TP-032 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 5.5 | 2.0 |  | 28.05 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42E | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | M | N | 010 | N | 1057
CO26032 | 08 | 32 | 1" | CO | 26032 | 1IS5 | N | 0 | CO26030 | CO26029 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
LO32010 | 08 | 32 | 2" | LO | 32010 | QXB-55 | N | 0 | TP 12B (32-PK-3200 B)) | TP 13B (LO320106) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LO36002 | 08 | 32 | 1-1/2" | LO | 36002 | QXB-55 | N | 0 | TP-144 (LO360128) | TP-143 (PK3600) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.28D | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 110 | N | 800
LO36005 | 08 | 32 | 3" | LO | 36005 | QXB-55 | N | 0 | LO36006 | 32-P-3601 | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.28D | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 110 | N | 800
LO40001 | 08 | 32 | 1-1/2" | LO | 40001 | QXB-55 | N | 0 | TP-20 (LO400117) | TP-21 (LO400120) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.30B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-049-03 |  | M | N | 110 | N | 800
LO40003 | 08 | 32 | 1-1/2" | LO | 40003 | QXB-55 | P | 50 | TP-14 (32-D-4002) | TP-15 (32-D-4001) | 15.0/16.0 | 120.0/80.0 | 2.0 | 65.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 65 | sh.30B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-049-03 |  | M | N | 110 | N | 801
LS13007 |  | 32 | 1/2" | LS | 13007 | B-5 | HB | 60 | JLS13002 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13007 |  | 32 | 3/4" | LS | 13007 | B-5 | HB | 60 | JLS13002 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13008 |  | 32 | 1" | LS | 13008 | B-5 | HB | 70 | LS63004 | 32-E-1300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-P-025-01 |  | E | N | 000 | N | 90
LS14002 |  | 32 | 1/2" | LS | 14002 | B-5 | HB | 60 | 32-E-1400B | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS14003 |  | 32 | 1/2" | LS | 14003 | B-5 | HB | 60 | JLS14001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS20001 |  | 32 | 1/2" | LS | 20001 | B-5 | HB | 60 | JLS20001 | LC20001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS24012 |  | 32 | 3/4" | LS | 24012 | D1S1 | HB | 50 | LS63073 | 32-E-2402 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.20 | 1 | III | MOD.G | Y | 20 | N | 32-P-046-01 |  | E | N | 041 | N | 1090
LS24012 |  | 32 | 8" | LS | 24012 | D1S1 | HB | 70 | LS63073 | 32-E-2402 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | E | N | 041 | N | 1090
LS24012 |  | 32 | 10" | LS | 24012 | D1S1 | HB | 80 | LS63073 | 32-E-2402 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | E | N | 041 | N | 1090
LS24013 |  | 32 | 3" | LS | 24013 | D1S1 | HB | 60 | 32-E-2402 | LS24014 | 49.0/-1.0/33.7/-1.0 | 250.0/250.0/250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 76.71 | 153.15 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | E | N | 041 | N | 1090
LS31017 | 08 | 32 | 1/2" | LS | 31017 | B-5 | HB | 60 | PR31015 | LC31010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.68N | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31025 |  | 32 | 1/2" | LS | 31025 | B-5 | HB | 60 | 32-S-3100 | LC31013 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31025 |  | 32 | 1" | LS | 31025 | B-5 | HB | 70 | 32-S-3100 | LC31013 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31026 |  | 32 | 3/4" | LS | 31026 | B-5 | HB | 60 | 32-D-3100 | LC31015 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
FW68E17 | 08 | 32 | 3" | FW | 68E17 | B-7 | N | 0 | FW68E26 | FW68E27 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E19 | 08 | 32 | 3" | FW | 68E19 | B-7 | N | 0 | FW68E27 | FW68E26 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68F18 | 08 | 32 | 3/4" | FW | 68F18 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F25 | 08 | 32 | 3/4" | FW | 68F25 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F25 | 08 | 32 | 2" | FW | 68F25 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68G08 | 08 | 45 | 2" | FW | 68G08 | B-13 | N | 0 | FW68D08 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G22 | 08 | 45 | 1" | FW | 68G22 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68G22 | 08 | 45 | 3" | FW | 68G22 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
VA81016 | 08 | 32 | 4" | VA | 81016 | B-1 | N | 0 | 32-PSV-8104C | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.60 | 2 | NA | NA | NA | 1 | N | 32-P-061-02 |  | E | N | 000 | N | 181
VA81017 | 08 | 32 | 4" | VA | 81017 | B-1 | N | 0 | 32-PSV-8104D | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.61 | 2 | NA | NA | NA | 1 | N | 32-P-061-02 |  | E | N | 000 | N | 181
VA81020 | 08 | 32 | 8" | VA | 81020 | 1CS2 | N | 0 | 32-S-8106 | TO SAFE LOCATION WITH BIRD SCREEN | 0.5 | 80.0 | 0.05 | 40.0 |  | .55 | 25.65 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.62 | 2 | NA | NA | NA | NR | N | 32-P-061-04 |  | M | N | 000 | N | 182
VA81023 | 08 | 32 | 8" | VA | 81023 | B4S2 | N | 0 | 32-C-8123 | OUTDOOR TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.61 | 2 | NA | NA | NA | 6 | N | 32-P-061-02 |  | E | N | 000 | N | 183
VA89003 | 08 | 32 | 24" | VA | 89003 | 1CS2 | N | 0 | TP-N50403 (N50403 A-8900) | TP-N60801 (C-8901) | 0.5 | 80.0 | 0.05 | 40.0 |  | .55 | 25.65 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.68M | 2 | NA | NA | NA | NR | N | 32-P-070-07 |  | M | N | 000 | N | 182
VA89016 | 08 | 32 | 2" | VA | 89016 | B4S2 | N | 0 | LN89007 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.85 | 2 | NA | NA | NA | 6 | N | 32-U-003-06 |  | E | N | 000 | N | 183
VA89019 | 08 | 32 | 2" | VA | 89019 | B4S2 | N | 0 | TP-N60247 (32-D-8908) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.68R | 2 | NA | NA | NA | 6 | N | 32-P-070-05 |  | E | N | 000 | N | 183
HCM24083 | 08 | 32 | 3/4" | HCM | 24083 | D20S1 | N | 0 | 32-E-2403 | PR24037 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24083 | 08 | 32 | 1-1/2" | HCM | 24083 | D20S1 | N | 0 | 32-E-2403 | PR24037 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24083 | 08 | 32 | 4" | HCM | 24083 | D20S1 | N | 0 | 32-E-2403 | PR24037 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24088 |  | 32 | 3/4" | HCM | 24088 | D20S1 | P | 50 | 32-T-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24088 |  | 32 | 1-1/2" | HCM | 24088 | D20S1 | P | 50 | 32-T-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24088 |  | 32 | 3" | HCM | 24088 | D20S1 | P | 50 | 32-T-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24094 |  | 32 | 1" | HCM | 24094 | D20S1 | P | 50 | HCM24085 | HCM24025 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 328 | 15
HCM24094 |  | 32 | 2" | HCM | 24094 | D20S1 | P | 50 | HCM24085 | HCM24025 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 328 | 15
HCM24094 |  | 32 | 3" | HCM | 24094 | D20S1 | P | 50 | HCM24085 | HCM24025 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 328 | 15
HCM24099 |  | 32 | 6" | HCM | 24099 | D20S1 | ST | 30 | 32-T-2400 | BDL24098 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM31012 |  | 32 | 3" | HCM | 31012 | C42S1 | HB | 30 | 32-S-3100 | 32-S-3101A | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31012 |  | 32 | 6" | HCM | 31012 | C42S1 | HB | 30 | 32-S-3100 | 32-S-3101A | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31014 |  | 32 | 1/2" | HCM | 31014 | C42S1 | ST | 30 | HN31001 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31014 |  | 32 | 1" | HCM | 31014 | C42S1 | ST | 30 | HN31001 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31015 |  | 32 | 1/2" | HCM | 31015 | C42S1 | ST | 30 | 32-D-3100 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31015 |  | 32 | 1" | HCM | 31015 | C42S1 | ST | 30 | 32-D-3100 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31015 |  | 32 | 2" | HCM | 31015 | C42S1 | ST | 40 | 32-D-3100 | 32-S-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31016 | 08 | 32 | 2" | HCM | 31016 | C42S1 | N | 0 | 32-D-3100 | BDL31030 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
BU73084 | 08 | 32 | 1/2" | BU | 73084 | B32S1 | N | 0 | 32-S-7302B | BDL73050 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73084 | 08 | 32 | 1" | BU | 73084 | B32S1 | N | 0 | 32-S-7302B | BDL73050 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73086 | 08 | 32 | 1/2" | BU | 73086 | B32S1 | N | 0 | 32-S-7302A | BDL73049 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73086 | 08 | 32 | 1" | BU | 73086 | B32S1 | N | 0 | 32-S-7302A | BDL73049 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73087 | 08 | 32 | 1" | BU | 73087 | B32S1 | N | 0 | 32-D-7302 | BDL73040 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73087 | 08 | 32 | 2" | BU | 73087 | B32S1 | N | 0 | 32-D-7302 | BDL73040 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
CHWR15004 | 08 | 32 | 1/2" | CHWR | 15004 | B-1 | CF | 25 | CHW1524 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21006 |  | 32 | 3" | CHWR | 21006 | B-1 | CF | 25 | 32-R-2100 | 32-P-2101 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR21006 |  | 32 | 4" | CHWR | 21006 | B-1 | CF | 25 | 32-R-2100 | 32-P-2101 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
PG61001 | 08 | 32 | 3/4" | PG | 61001 | 1CS2 | N | 0 | 32-P-6101 | 32-D-6100 | 10.0 | 60.0 | 5.0 | 20.0 |  | 15 | 28.5 | H | PROPYLENE GLYCOL | L | - | - | <1.5 | 20 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-023-01 |  | M | N | 010 | N | 80
PG61001 | 08 | 32 | 1-1/2" | PG | 61001 | 1CS2 | N | 0 | 32-P-6101 | 32-D-6100 | 10.0 | 60.0 | 5.0 | 20.0 |  | 15 | 28.5 | H | PROPYLENE GLYCOL | L | - | - | <1.5 | 20 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-023-01 |  | M | N | 010 | N | 80
PJW23004 |  | 32 | 1-1/2" | PJW | 23004 | B-1 | HB | 30 | 32-E-2300 | 32-P-2300 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.16 | 2 | III | MOD.G | Y | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PN52024 | 7A | 32 | 3/4" | PN | 52024 | 1CS2 | HB | 30 | PN52027 | PN52025 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52025 | 7A | 32 | 8" | PN | 52025 | 1CS2 | HB | 40 | PN52024 | VA52012 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52026 | 7A | 32 | 8" | PN | 52026 | 1CS2 | HB | 40 | PN52023 | VA52010 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52027 | 7A | 32 | 1/2" | PN | 52027 | 1CS2 | HB | 30 | 32-Z-5202A | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52027 | 7A | 32 | 14" | PN | 52027 | 1CS2 | HB | 40 | 32-Z-5202A | PN52018 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
VZ62002 | 08 | 32 | 1-1/2" | VZ | 62002 | C3S1 | N | 0 | 32-D-6200 | - | 28.0 | 150.0 | 25.0 | 30.0 |  | 37.24 | 68.99 | P | VESSEL TRIM | G | - | - | >1.5 | 30 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-023-02 |  | E | N | 000 | N | 204
VZ62002 | 08 | 32 | 2" | VZ | 62002 | C3S1 | N | 0 | 32-D-6200 | - | 28.0 | 150.0 | 25.0 | 30.0 |  | 37.24 | 68.99 | P | VESSEL TRIM | G | - | - | >1.5 | 30 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 204
VZ63004 | 08 | 32 | 2" | VZ | 63004 | B-5 | P | 50 | 32-D-6300 | - | 3.5 | 180.0 | 0.01 | 100.0 |  | 5.26 | 29.4 | H | VESSEL TRIM | LG | - | - | >1.5 | 100 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 135
VZ65003 |  | 32 | 1" | VZ | 65003 | B4S2 | ET | 30 | 32-D-6500 | 32-D-6500 | 3.5 | 180.0 | 0.05/0.05 | 100.0/30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 230 | 23,25
VZ65003 |  | 32 | 1-1/2" | VZ | 65003 | B4S2 | ET | 30 | 32-D-6500 | 32-D-6500 | 3.5 | 180.0 | 0.05/0.05 | 100.0/30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 230 | 23,25
VZ66004 | 08 | 32 | 1/2" | VZ | 66004 | B4S2 | HH | 30 | 32-D-6600 | - | 3.5 | 180.0 | 0.0 | 30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 233 | 23,25
JWR61001 | 08 | 32 | 1-1/2" | JWR | 61001 | C3S1 | N | 0 | TP-014 (JWR610203) | PSV-6177, VM-61167 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.42D | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR61001 | 08 | 32 | 8" | JWR | 61001 | C3S1 | N | 0 | TP-014 (JWR610203) | PSV-6177, VM-61167 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.42D | 2 | II | MOD.A2 | Y | 1 | Y | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR62001 | 08 | 32 | 4" | JWR | 62001 | B-1 | N | 0 | TP-14, (JWR620101) | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64003 |  | 32 | 2" | JWR | 64003 | B-1 | HB | 30 | ACW | WW64001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64042 | 08 | 32 | 12" | JWR | 64042 | B-1 | N | 0 | HEADER | JWR64006 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64042 | 08 | 32 | 20" | JWR | 64042 | B-1 | N | 0 | HEADER | JWR64006 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64047 | 08 | 32 | 1" | JWR | 64047 | B-1 | N | 0 | JWR32003 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71003 | 08 | 32 | 3" | JWR | 71003 | B-1 | N | 0 | JWR71002 | JWR71001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.48 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR89001 | 08 | 32 | 3/4" | JWR | 89001 | B-1 | N | 0 | TP-N30602 (32-E-8921A HEATING BARREL) | TP-N60102 (32-E-8906) | 10.0 | 120.0 | 7.0 | 50.0 |  | 15 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 50 | sh.68F | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 803
JWR89001 | 08 | 32 | 3" | JWR | 89001 | B-1 | N | 0 | TP-N30602 (32-E-8921A HEATING BARREL) | TP-N60102 (32-E-8906) | 10.0 | 120.0 | 7.0 | 50.0 |  | 15 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 50 | sh.68F | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 803
JWS32001 | 08 | 32 | 3/4" | JWS | 32001 | C3S1 | N | 0 | JWS64019 | 32-E-3200 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS32001 | 08 | 32 | 3" | JWS | 32001 | C3S1 | N | 0 | JWS64019 | 32-E-3200 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS61001 | 08 | 32 | 8" | JWS | 61001 | C3S1 | N | 0 | JWS64061 | TI-6176 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.42D | 2 | II | MOD.A2 | Y | 1 | Y | 32-U-022-01 |  | E | N | 000 | N | 1010
LS23036 |  | 32 | 3/4" | LS | 23036 | B-5 | HB | 60 | HCM23057 | LC23052 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS24014 |  | 32 | 1" | LS | 24014 | B-5 | HB | 70 | LS24013 | LC24011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-P-046-01 |  | E | N | 000 | N | 90
LS31018 | 08 | 32 | 1/2" | LS | 31018 | B-5 | HB | 60 | JLS31006 | LC31011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31024 |  | 32 | 3/4" | LS | 31024 | B-5 | HB | 60 | JLS31007 | LC31019 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31027 |  | 32 | 3/4" | LS | 31027 | B-5 | HB | 60 | LS63041 | JLS31012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31027 |  | 32 | 1-1/2" | LS | 31027 | B-5 | HB | 70 | LS63041 | JLS31012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS32003 |  | 32 | 1/2" | LS | 32003 | B-5 | HB | 60 | 32-D-3200 | LC32003 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.24 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS32003 |  | 32 | 3/4" | LS | 32003 | B-5 | HB | 60 | 32-D-3200 | LC32003 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.24 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS33002 |  | 32 | 1" | LS | 33002 | C6S1 | HA | 50 | 32-E-3301 | LC33001 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-052-01 |  | E | N | 141 | N | 1092
LS34006 |  | 32 | 1/2" | LS | 34006 | B-5 | HB | 60 | 32-D-3400 | LC34001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS34006 |  | 32 | 1-1/2" | LS | 34006 | B-5 | HB | 70 | 32-D-3400 | LC34001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS43010 |  | 32 | 3" | LS | 43010 | C6S1 | HB | 60 | LS63025 | 32-E-4303 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.33 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-03 |  | E | N | 141 | N | 1092
LS50001 |  | 32 | 3/4" | LS | 50001 | 3CS6 | HB | 50 | LS50002 | LS50006 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50001 |  | 32 | 4" | LS | 50001 | 3CS6 | HB | 70 | LS50002 | LS50006 | 5.0/-1.0 | 250.0/160.0 | 3.5 | 200.0 |  | 8.48 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-01 |  | M | N | 000 | N | 93
LS50006 |  | 32 | 3/4" | LS | 50006 | 3CS6 | HB | 30 | LS50001 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50006 |  | 32 | 1-1/2" | LS | 50006 | 3CS6 | HB | 30 | LS50001 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50006 |  | 32 | 6" | LS | 50006 | 3CS6 | HB | 40 | LS50001 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
CHWS24002 |  | 32 | 3/4" | CHWS | 24002 | C42S1 | CF | 25 | CHWS61025 | 32-E-2404 | 42.0/42.0 | 150.0/-45.0 | 2.0 | 2.0 |  | 63.01 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.19 | 2 | II | MOD.A2 | Y | 20 | N | 32-U-023-01 |  | M | N | 010 | N | 1053
CHWS24002 |  | 32 | 6" | CHWS | 24002 | C42S1 | CF | 40 | CHWS61025 | 32-E-2404 | 42.0/42.0 | 150.0/-45.0 | 2.0 | 2.0 |  | 63.01 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.19 | 2 | II | MOD.A2 | Y | 20 | Y | 32-U-023-01 |  | M | N | 010 | N | 1053
CHWS43010 |  | 32 | 3" | CHWS | 43010 | C42S1 | CF | 25 | CHWS61029 | 32-E-4302 | 28.0/28.0 | 180.0/-45.0 | 2.0 | 2.0 |  | 42.12 | 76.65 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 2 | sh.33 | 2 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | M | N | 010 | N | 1051
CHWS61002 |  | 32 | 1/2" | CHWS | 61002 | B-1 | CF | 25 | 32-P-6100B | CHWS61015 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61002 |  | 32 | 1" | CHWS | 61002 | B-1 | CF | 25 | 32-P-6100B | CHWS61015 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61002 |  | 32 | 8" | CHWS | 61002 | B-1 | CF | 40 | 32-P-6100B | CHWS61015 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61003 |  | 32 | 3/4" | CHWS | 61003 | B-1 | CF | 25 | CHWS61028 | CHWS14008 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61003 |  | 32 | 2" | CHWS | 61003 | B-1 | CF | 25 | CHWS61028 | CHWS14008 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61004 |  | 32 | 1" | CHWS | 61004 | B-1 | CF | 25 | CHWS61028 | CHWS14010 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61014 |  | 32 | 3/4" | CHWS | 61014 | B-1 | CF | 25 | 32-P-6100A | CHWS623 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61014 |  | 32 | 8" | CHWS | 61014 | B-1 | CF | 40 | 32-P-6100A | CHWS623 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61014 |  | 32 | 10" | CHWS | 61014 | B-1 | CF | 40 | 32-P-6100A | CHWS623 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61017 | 08 | 32 | 1-1/2" | CHWS | 61017 | B-1 | CF | 25 | TP-033 | 32-D-6100 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61017 | 08 | 32 | 10" | CHWS | 61017 | B-1 | CF | 40 | TP-033 | 32-D-6100 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61021 |  | 32 | 3/4" | CHWS | 61021 | B-1 | CF | 25 | CHWS61029 | 32-Z-2004 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
N80018 | 08 | 32 | 2" | N | 80018 | B-1 | N | 0 | N89010 | N80024 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N80023 | 08 | 32 | 3/4" | N | 80023 | 1CS2 | N | 0 | N67075 | 32-V-8001A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N81018 | 08 | 32 | 1/2" | N | 81018 | 1CS2 | N | 0 | N89002 | 32-PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81030 | 08 | 32 | 2" | N | 81030 | 1CS2 | N | 0 | TP-001 (N80024) | 32-D-8002A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | I | MOD.A | Y | 5 | N | 32-P-060-01_B |  | M | N | 000 | N | 166
N81043 | 08 | 32 | 1/2" | N | 81043 | 1CS2 | N | 0 | N89059 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
VZ12011 |  | 32 | 1/2" | VZ | 12011 | 1CS2 | ET | 30 | 32-D-1200C | 32-D-1200C | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12011 |  | 32 | 1" | VZ | 12011 | 1CS2 | ET | 30 | 32-D-1200C | 32-D-1200C | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ16006 | 08 | 32 | 1/2" | VZ | 16006 | 4CS2 | ET | 30 | 32-D-1601 | 32-D-1601 | 0.5 | 180.0 | 0.05 | 50.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 404
VZ23004 | 08 | 32 | 1" | VZ | 23004 | C42S1 | N | 0 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 0 | 0 | V | VESSEL TRIM | LG | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 517 | 10
VZ24009 |  | 32 | 1-1/2" | VZ | 24009 | D20S1 | HB | 30 | 32-E-2402 | BDL24085 | 49.0/49.0 | -45.0/250.0 | 32.18/32.18 | 74.0/73.9 |  | 76.71 | 153.15 | H | VESSEL TRIM | LG | - | - | >1.5 | 73.9 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 510 | 15
VZ50009 |  | 32 | 3/4" | VZ | 50009 | 3CS6 | HB | 60 | 32-S-5001 | 32-S-5001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 11.02 | 28.5 | H | VESSEL TRIM | G | - | - | >1.5 | 200 | sh.34 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | M | N | 000 | N | 99
HCM23081 | 08 | 32 | 1-1/2" | HCM | 23081 | C42S1 | N | 0 | PR24047 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM24062 |  | 32 | 1-1/2" | HCM | 24062 | 3FS4 | CF | 25 | HCM24064 | TP-1 (HCM240162) | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | N | 141 | N | 367 | 15,36,5
HCM24065 |  | 32 | 1" | HCM | 24065 | 3FS4 | HB | 30 | HCM24098 | HCM24063 | 42.0/42.0 | -40.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-01 |  | H | Y | 141 | N | 519 | 15,36,5
HCM24066 | 08 | 32 | 1/2" | HCM | 24066 | C42S1 | N | 0 | 32-T-2401 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24066 | 08 | 32 | 1" | HCM | 24066 | C42S1 | N | 0 | 32-T-2401 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24066 | 08 | 32 | 2" | HCM | 24066 | C42S1 | N | 0 | 32-T-2401 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
P40035 |  | 32 | 2" | P | 40035 | C42S2 | ET | 30 | 32-R-4001 | P40037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40047 |  | 32 | 1/2" | P | 40047 | QXC25S2 | ST | 30 | 32-Z-4004A | BDL40032 | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P50016 |  | 32 | 1-1/2" | P | 50016 | 1CR9 | HB | 30 | 32-D-5001 | LC50005 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | I | MOD.A | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
P52012 | 7A | 32 | 12" | P | 52012 | 4CS9 | HB | 40 | 32-A-5200 | TP-010 (32-V-8000A/B) | 0.5 | 120.0 | 0.1 | 90.0 |  | .75 | 28.5 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.37 | 1 | NA | NA | NA | NR | N | 32-P-050-01 |  | G-4 | N | 110 | N | 440 | 6,10,13,18
IA6200N | 08 | 32 | 1" | IA | 6200N | B-13 | N | 0 | IA62077 | 32-IAM-045 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200X | 08 | 32 | 1/2" | IA | 6200X | B-13 | N | 0 | IA62001 | 45-IAT-001 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
PW51017 |  | 32 | 2" | PW | 51017 | B4S1 | ST | 30 | FLANGE HEADER | FLANGE HEADER | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51017 |  | 32 | 3" | PW | 51017 | B4S1 | ST | 30 | FLANGE HEADER | FLANGE HEADER | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW52012 | 08 | 32 | 1" | PW | 52012 | B4S2 | N | 0 | 32-E-5201 | 32-T-5200 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52012 | 08 | 32 | 4" | PW | 52012 | B4S2 | N | 0 | 32-E-5201 | 32-T-5200 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52012 | 08 | 32 | 8" | PW | 52012 | B4S2 | N | 0 | 32-E-5201 | 32-T-5200 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52013 | 08 | 32 | 1/2" | PW | 52013 | B4S2 | N | 0 | 32-P-5200A | 32-E-5201 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52013 | 08 | 32 | 1" | PW | 52013 | B4S2 | N | 0 | 32-P-5200A | 32-E-5201 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52013 | 08 | 32 | 6" | PW | 52013 | B4S2 | N | 0 | 32-P-5200A | 32-E-5201 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52015 | 08 | 32 | 6" | PW | 52015 | B4S2 | N | 0 | PW52016 | 32-P-5200B | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PW52015 | 08 | 32 | 8" | PW | 52015 | B4S2 | N | 0 | PW52016 | 32-P-5200B | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PX86029 | 08 | 32 | 1/2" | PX | 86029 | QXC25S1 | N | 0 | PX86030 | 32-P-8600A | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PR72017 | 08 | 32 | 3/4" | PR | 72017 | C42S1 | N | 0 | 32-T-7201 | BDL72036 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72017 | 08 | 32 | 1" | PR | 72017 | C42S1 | N | 0 | 32-T-7201 | BDL72036 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72017 | 08 | 32 | 2" | PR | 72017 | C42S1 | N | 0 | 32-T-7201 | BDL72036 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72017 | 08 | 32 | 6" | PR | 72017 | C42S1 | N | 0 | 32-T-7201 | BDL72036 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72021 | 08 | 32 | 6" | PR | 72021 | C42S1 | N | 0 | PR72015 | PR72022 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72027 | 08 | 32 | 3/4" | PR | 72027 | C42S1 | N | 0 | HEADER | BDL72030 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72027 | 08 | 32 | 1-1/2" | PR | 72027 | C42S1 | N | 0 | HEADER | BDL72030 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72027 | 08 | 32 | 3" | PR | 72027 | C42S1 | N | 0 | HEADER | BDL72030 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72028 | 08 | 32 | 3/4" | PR | 72028 | C42S1 | N | 0 | 32-D-7200 | PR72018 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72028 | 08 | 32 | 1-1/2" | PR | 72028 | C42S1 | N | 0 | 32-D-7200 | PR72018 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72038 | 08 | 32 | 3/4" | PR | 72038 | C42S1 | N | 0 | PR72009 | BDL72023 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72038 | 08 | 32 | 3" | PR | 72038 | C42S1 | N | 0 | PR72009 | BDL72023 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72039 | 08 | 32 | 2" | PR | 72039 | C42S1 | N | 0 | PR72015 | BDL72034 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72040 | 08 | 32 | 1" | PR | 72040 | C42S1 | N | 0 | PR72009 | BDL72020 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72041 | 08 | 32 | 1-1/2" | PR | 72041 | C42S1 | N | 0 | 32-S-7201B | BDL72047 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72052 | 08 | 32 | 1" | PR | 72052 | C42S1 | N | 0 | PR72014 | BDL72052 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PW50015 |  | 32 | 2" | PW | 50015 | B4S2 | HB | 30 | 32-T-5001 | 32-D-5002 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 30
VZ65003 |  | 32 | 3/4" | VZ | 65003 | B4S2 | ET | 30 | 32-D-6500 | 32-D-6500 | 3.5 | 180.0 | 0.05/0.05 | 100.0/30.0 |  | 5.26 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 230 | 23,25
VZ66005 | 08 | 32 | 3/4" | VZ | 66005 | 1CS2 | EH | 30 | 32-S-6601 | 32-S-6601 | 7.0 | 180.0 | 4.0 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-03 |  | M | N | 110 | N | 234 | 23,25
VZ73007 | 08 | 32 | 1-1/2" | VZ | 73007 | B32S1 | N | 0 | 32-D-7302 | 32-D-7302 | 14.0/14.0 | 80.0/-7.0 | 5.0 | 50.0 |  | 21 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 50 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 730 | 15
BDH21001 | 08 | 32 | 1" | BDH | 21001 | C42S2 | N | 0 | 32-R-2100 | 32-D-6011 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH21001 | 08 | 32 | 4" | BDH | 21001 | C42S2 | N | 0 | 32-R-2100 | 32-D-6011 | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.12 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDH60001 |  | 32 | 4" | BDH | 60001 | C42S2 | P | 50 | 32-D-6011 | CONTAINER | 20.0/20.0 | -45.0/185.0 | 10.0 | 80.0 |  | 30.1 | 76.65 | H | HP BLOW DOWN | GS | - | - | >1.5 | 80 | sh.41 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-02 |  | F-2 | N | 141 | N | 482 | 6,15,11,13
BDL43019 | 08 | 32 | 2" | BDL | 43019 | B32S1 | N | 0 | BDL24095 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60042 | 08 | 32 | 1" | BDL | 60042 | B32S1 | N | 0 | N67092 | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60059 | 08 | 32 | 1" | BDL | 60059 | B32S1 | N | 0 | N67114 | BDL60023 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61004 | 08 | 32 | 3/4" | BDL | 61004 | B32S1 | N | 0 | TP-035 (32-D-6103) | BDL61015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61010 | 08 | 32 | 3" | BDL | 61010 | B32S1 | N | 0 | TP-022 (32-PSV-6180) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61012 | 08 | 32 | 1" | BDL | 61012 | B32S1 | N | 0 | TP-027 (32-E-6101) | BDL61015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
BDL61016 | 08 | 32 | 1" | BDL | 61016 | B32S1 | N | 0 | TP-046 (32-D-6108) | BDL61015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL72001 | 08 | 32 | 1" | BDL | 72001 | B32S1 | N | 0 | PR72016 | BDL72029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72023 | 08 | 32 | 2" | BDL | 72023 | B32S1 | N | 0 | PR72038 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72029 | 08 | 32 | 3/4" | BDL | 72029 | B32S1 | N | 0 | BDL72026 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
ET22008 | 08 | 32 | 1/2" | ET | 22008 | 1FS4 | N | 0 | HN22002 | ET22009 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | Art 4.3 | NA | N | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
ET22008 | 08 | 32 | 1" | ET | 22008 | 1FS4 | N | 0 | HN22002 | ET22009 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.13 | 1 | Art 4.3 | NA | N | NR | N | 32-P-006-03 |  | G | N | 041 | N | 324 | ,10
IA68N39 | 08 | 32 | 1" | IA | 68N39 | B-13 | N | 0 | IA68M11 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA89065 | 08 | 32 | 1" | IA | 89065 | B-13 | N | 0 | IA89027 | 32-IAM-103 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
HTF89007 | 08 | 32 | 1" | HTF | 89007 | C-2 | HA | 80 | HOS89002 | COLLECTION DRUM | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | DIATHERMIC OIL/HOT THERMAL FLUID | L | - | - | <1.5 | 280 | sh.68R | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 207
IA02009 | 08 | 32 | 1" | IA | 02009 | B-13 | N | 0 | IA02002 | 32-IAM-128 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62054 | 08 | 32 | 3/4" | IA | 62054 | B-13 | N | 0 | IA62001 | TO C-4001 COMPRESSOR AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62054 | 08 | 32 | 1" | IA | 62054 | B-13 | N | 0 | IA62001 | TO C-4001 COMPRESSOR AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62089 | 08 | 32 | 2" | IA | 62089 | B-13 | N | 0 | IA62001 | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62092 | 08 | 32 | 3" | IA | 62092 | B-13 | N | 0 | IA01001 | VA62003 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620AS | 08 | 32 | 3/4" | IA | 620AS | B-13 | N | 0 | IA620AT | 32-IAT-130 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
LC6300B |  | 32 | 3/4" | LC | 6300B | B-5 | HB | 30 | LS6300B | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300P |  | 32 | 1-1/2" | LC | 6300P | B-5 | HB | 40 | 32-1115-R-012 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300T |  | 32 | 3/4" | LC | 6300T | B-5 | HB | 30 | 32-1115-S-012 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63030 |  | 32 | 1-1/2" | LC | 63030 | B-5 | P | 50 | 32-D-6300 | LC63040 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63037 |  | 32 | 3/4" | LC | 63037 | B-5 | P | 50 | LC63036 | SC500001 OSBL LINE | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63037 |  | 32 | 4" | LC | 63037 | B-5 | P | 50 | LC63036 | SC500001 OSBL LINE | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | I | MOD.A | Y | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LC63038 |  | 32 | 3/4" | LC | 63038 | B-5 | P | 50 | 32-D-6300 | 32-D-6300 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63038 |  | 32 | 2" | LC | 63038 | B-5 | P | 50 | 32-D-6300 | 32-D-6300 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63079 |  | 32 | 1-1/2" | LC | 63079 | B-5 | HB | 40 | 32-1121-R-003 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65002 |  | 32 | 1" | LC | 65002 | B-5 | HB | 40 | LS65001 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65005 |  | 32 | 1/2" | LC | 65005 | B-5 | HB | 30 | LS65003 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LN81016 | 08 | 32 | 1/2" | LN | 81016 | 1CS2 | N | 0 | LN89006 | 32-V-8107 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.62 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 175
LO89006 | 08 | 32 | 3/4" | LO | 89006 | QXB-55 | N | 0 | TP-N20453 (32-E-8902) | TP-N20353 (32-Z-8900) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LO89006 | 08 | 32 | 3" | LO | 89006 | QXB-55 | N | 0 | TP-N20453 (32-E-8902) | TP-N20353 (32-Z-8900) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LPN10006 | 08 | 32 | 1/2" | LPN | 10006 | 3DS3 | N | 0 | N10005 | LPN11004 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10008 | 08 | 32 | 1/2" | LPN | 10008 | 1CS2 | N | 0 | LPN02005 | HOSE CONNECTION | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN10008 | 08 | 32 | 1" | LPN | 10008 | 1CS2 | N | 0 | LPN02005 | HOSE CONNECTION | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-U-002-01 |  | F | N | 343 | N | 167 | 8,29,23,25
CWR94004 | 08 | 32 | 3/4" | CWR | 94004 | B-1 | N | 0 | CWR94005 | VA94002 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.74 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
N40005 | 08 | 32 | 1" | N | 40005 | B-1 | N | 0 | NITROGEN CONNECTION | PR40022 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N52042 | 08 | 32 | 2" | N | 52042 | 1CS2 | N | 0 | N52041 | N52043 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | NA | NA | NA | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 154
O14003 |  | 32 | 1" | O | 14003 | B4S2 | ET | 30 | O13014 | 32-D-1501 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O15002 |  | 32 | 3/4" | O | 15002 | 1FS4 | ET | 30 | O15007 | 32-HX-1431 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15007 |  | 32 | 3/4" | O | 15007 | 1FS4 | ET | 30 | 32-P-1501A | O15009 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15018 | 08 | 32 | 1/2" | O | 15018 | 1CS2 | N | 0 | 32-S-1500 | N15003 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-026-05 |  | M | N | 110 | N | 236 | 23,25
O20001 |  | 32 | 3/4" | O | 20001 | 1FS4 | ET | 30 | O15008 | 32-Z-2001B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O31013 |  | 32 | 1/2" | O | 31013 | B4S2 | ET | 30 | O66037 | O31011 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
O66022 |  | 32 | 2" | O | 66022 | 1CS2 | ET | 30 | O66021 | 32-P-6600 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
P23018 | 7A | 32 | 1/2" | P | 23018 | 1FS4 | HB | 30 | 32-Z-2300A | P23016 | 42.0/42.0 | -40.0/200.0 | 30.0 | 100.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.17 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 141 | N | 521 | 10
P23027 |  | 32 | 1" | P | 23027 | C42S5 | HB | 30 | 32-E-2300 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 66.72 | 68.64 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P31007 |  | 32 | 4" | P | 31007 | C42S2 | P | 50 | P31012 | P34003 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 1 | Y | 32-P-048-01 |  | G-2 | N | 141 | N | 419 | ,10,6,11,13,38,39
P40042 | 08 | 32 | 1" | P | 40042 | C42S3 | N | 0 | N40002 | P40024 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
PA02007 | 08 | 32 | 3/4" | PA | 02007 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PR43044 | 08 | 32 | 3/4" | PR | 43044 | C42S1 | N | 0 | 32-T-4300 | 32-E-4302 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43044 | 08 | 32 | 3" | PR | 43044 | C42S1 | N | 0 | 32-T-4300 | 32-E-4302 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR50015 |  | 32 | 3" | PR | 50015 | B4S1 | P | 50 | PR50010 | BDL50001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
PR72002 | 08 | 32 | 1" | PR | 72002 | C42S1 | N | 0 | 32-S-7201A | 32-D-3300 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
VZ72023 | 08 | 32 | 3/4" | VZ | 72023 | C42S1 | N | 0 | 32-D-7201 | 32-D-7201 | 43.7/43.7 | 100.0/-45.0 | 0.1 | 30.0 |  | 65.55 | 76.65 | H | VESSEL TRIM | L | - | - | >1.5 | 30 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 320 | 15
WW69A01 | 08 | 32 | 2" | WW | 69A01 | B4S2 | N | 0 | 32-ES-6908 | TO ACC | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.89 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
BDL23024 | 08 | 32 | 2" | BDL | 23024 | B32S1 | N | 0 | HCM23018 | BDL23016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24062 | 08 | 32 | 1/2" | BDL | 24062 | B32S1 | N | 0 | BDL01037 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24063 | 08 | 32 | 3/4" | BDL | 24063 | B32S1 | N | 0 | HCM24092 | HCM24092 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24064 | 08 | 32 | 1" | BDL | 24064 | B32S1 | N | 0 | HCM24069 | BDL24062 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24082 | 08 | 32 | 3/4" | BDL | 24082 | B32S1 | N | 0 | HCM24078 | BDL43016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24096 | 08 | 32 | 3/4" | BDL | 24096 | B32S1 | N | 0 | HCM24083 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
VZ50010 | 08 | 32 | 1/2" | VZ | 50010 | B4S2 | N | 0 | 32-D-5002 | FLANGE | 5.0/-1.0 | 180.0/180.0 | 0.2 | 80.0 |  | 7.52 | 29.4 | H | VESSEL TRIM | L | - | - | >1.5 | 80 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 29
VZ51004 | 08 | 32 | 3/4" | VZ | 51004 | B4S1 | ST | 30 | 32-D-5102 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ51004 | 08 | 32 | 1-1/2" | VZ | 51004 | B4S1 | ST | 30 | 32-D-5102 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
VZ52004 | 08 | 32 | 2" | VZ | 52004 | 1CR9 | HB | 30 | 32-A-5200 | - | 0.5 | 120.0 | 0.1 | 90.0 |  | 0 | 0 | V | VESSEL TRIM | GS | - | - | >1.5 | 90 | sh.37 | 1 | NA | NA | NA | NR | N | 32-P-052-01 |  | F-4 | N | 141 | N | 438 | 10,16,18,13
VZ72025 | 08 | 32 | 3/4" | VZ | 72025 | C42S1 | N | 0 | 32-T-7203 | PR72022 | 43.7/43.7 | 150.0/-45.0 | 23.5 | 40.0 |  | 65.56 | 76.65 | H | VESSEL TRIM | L | - | - | >1.5 | 40 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 431 | ,15
VZ91014 | 08 | 32 | 2" | VZ | 91014 | 5CS7 | N | 0 | 32-H-9001A | - | 0.1/-0.01 | 100.0/100.0 | 0.01/0.01 | 60.0/80.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 60 | sh.70 | 1 | NA | NA | NA | NR | N | 32-P-082-01 |  | M | N | 110 | N | 447 | 6,25,23
WW64001 | 08 | 32 | 12" | WW | 64001 | B4S2 | N | 0 | JWR64003 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.44 | 2 | I | MOD.A | Y | 1 | N | 32-U-023-02 |  | E | N | 000 | N | 87
WW88008 | 08 | 32 | 1/2" | WW | 88008 | B4S2 | N | 0 | 32-S-8010 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.67 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-080-02 |  | E | N | 000 | N | 87
FW68H03 | 08 | 32 | 1-1/2" | FW | 68H03 | B-13 | N | 0 | FW68H33 | FW68H02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H34 | 08 | 32 | 2" | FW | 68H34 | B-13 | N | 0 | FW68H33 | FW68H39 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I04 | 08 | 32 | 1" | FW | 68I04 | B-13 | N | 0 | MSN-003 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
PA62004 | 08 | 32 | 1/2" | PA | 62004 | B-1 | N | 0 | PA01001 | 32-P-6101 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62040 | 08 | 32 | 3/4" | PA | 62040 | B-1 | N | 0 | PA62053 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62041 | 08 | 32 | 3/4" | PA | 62041 | B-1 | N | 0 | PA62053 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62056 | 08 | 32 | 3/4" | PA | 62056 | B-1 | N | 0 | PA62072 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62068 | 08 | 32 | 3/4" | PA | 62068 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62087 | 08 | 32 | 3/4" | PA | 62087 | B-1 | N | 0 | PA62088 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89032 | 08 | 32 | 3/4" | PA | 89032 | B-1 | N | 0 | PA01001 | 32-US-1211-10 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89048 | 08 | 32 | 3/4" | PA | 89048 | B-1 | N | 0 | PA89021 | US-3211-03 AT GRADE | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89050 |  | 32 | 3/4" | PA | 89050 | B-1 | HB | 30 | PA01001 | 32-US-1211-01 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89051 |  | 32 | 3/4" | PA | 89051 | B-1 | HB | 30 | PA01001 | 32-US-1211-03 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-091-01 |  | E | N | 000 | N | 190
SA81018 | 08 | 32 | 1/2" | SA | 81018 | 1CS2 | N | 0 | IA89010 | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81018 | 08 | 32 | 1" | SA | 81018 | 1CS2 | N | 0 | IA89010 | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
PW50015 |  | 32 | 3" | PW | 50015 | B4S2 | HB | 30 | 32-T-5001 | 32-D-5002 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW51013 |  | 32 | 1-1/2" | PW | 51013 | B4S1 | ST | 30 | 32-D-5101 | BDL51017 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW52018 | 08 | 32 | 8" | PW | 52018 | B4S2 | N | 0 | 32-T-5200 | 32-D-5202 | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PX86018 | 08 | 32 | 1/2" | PX | 86018 | QXC25S1 | N | 0 | PX86022 | TP-N11212 (32-H-8901) | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86030 |  | 32 | 3/4" | PX | 86030 | QXC25S1 | JP | 0 | PX86032 | CWR86001 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86033 | 08 | 32 | 4" | PX | 86033 | QXC25S1 | N | 0 | CONTAINEMENT SUMP | PIT | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-021-02 |  | M | N | 1X4 | N | 605 | 7
BDH60002 |  | 32 | 2" | BDH | 60002 | C42S1 | HB | 50 | BDH60003 | 32-D-6011 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-02 |  | F | N | 141 | N | 483 | 15
BDH60006 |  | 32 | 1/2" | BDH | 60006 | C42S1 | HB | 40 | LS63047 | LS60004 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | F | N | 141 | N | 483 | 15
BDH60006 |  | 32 | 2" | BDH | 60006 | C42S1 | HB | 50 | LS63047 | LS60004 | 20.0/20.0 | -45.0/250.0 | 7.0 | 170.0 |  | 31.31 | 76.65 | H | HP BLOW DOWN | G | - | - | >1.5 | 170 | sh.41 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | F | N | 141 | N | 483 | 15
BDL01006 | 08 | 32 | 3/4" | BDL | 01006 | B32S1 | N | 0 | OG01004 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01011 | 08 | 32 | 3/4" | BDL | 01011 | B4S1 | N | 0 | HD01001 | BDL01009 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL01016 | 08 | 32 | 3/4" | BDL | 01016 | B32S1 | N | 0 | BU01003 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01016 | 08 | 32 | 1" | BDL | 01016 | B32S1 | N | 0 | BU01003 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01043 | 08 | 32 | 1" | BDL | 01043 | B32S1 | N | 0 | BDL01035 | BDL01042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL22020 | 08 | 32 | 3/4" | BDL | 22020 | B32S1 | N | 0 | BDL43021 | BDL24095 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL72041 | 08 | 32 | 3/4" | BDL | 72041 | B32S1 | N | 0 | VZ72025 | BDL72042 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL73044 | 08 | 32 | 3/4" | BDL | 73044 | B4S1 | N | 0 | 32-P-7300 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.55 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BDL73048 | 08 | 32 | 2" | BDL | 73048 | B4S1 | N | 0 | BU73081 | BDL60020 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 470 | ,10
BU73040 | 08 | 32 | 2" | BU | 73040 | D20S1 | N | 0 | JW73001 | JW73001 | 46.6/46.6 | 100.0/-7.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-001-02 |  | A | N | 140 | N | 722 | 15
BU73041 | 08 | 32 | 4" | BU | 73041 | D20S1 | N | 0 | JW73001 | 32-D-7302 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 141.72 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73044 |  | 32 | 1" | BU | 73044 | B32S1 | HB | 30 | JLS73005 | 32-D-7302 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.55 | 1 | I | MOD.A | Y | 20 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73085 | 08 | 32 | 1/2" | BU | 73085 | B32S1 | N | 0 | 32-S-7302A | BDL73049 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73085 | 08 | 32 | 1" | BU | 73085 | B32S1 | N | 0 | 32-S-7302A | BDL73049 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
IA89038 | 08 | 32 | 1" | IA | 89038 | B-13 | N | 0 | IA62006 | CAP | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89041 | 08 | 32 | 1" | IA | 89041 | B-13 | N | 0 | IA89037 | 32-IAM-101 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89061 | 08 | 32 | 1" | IA | 89061 | B-13 | N | 0 | IA89027 | 32-IAM-106 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
FO11019 |  | 32 | 1/2" | FO | 11019 | 1CS2 | ET | 30 | FO11003 | LPN11004 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO20003 | 08 | 32 | 1" | FO | 20003 | B4S2 | N | 0 | TEA20004 | FO20001 | 6.0 | 100.0 | 3.0 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 212 | 23,25
IA68C12 | 08 | 32 | 1/2" | IA | 68C12 | B-13 | N | 0 | 32-XV-6808A | IA68O07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68H11 | 08 | 32 | 1" | IA | 68H11 | B-13 | N | 0 | IA68C09 | IA68H13 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I03 | 08 | 32 | 1" | IA | 68I03 | B-13 | N | 0 | IA68I10 | IA68I13 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
HCM24071 | 08 | 32 | 8" | HCM | 24071 | C42S1 | N | 0 | HCM24069 | 32-T-2401 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
IA68K01 | 08 | 32 | 1" | IA | 68K01 | B-13 | N | 0 | IA68K11 | IA68K04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-17 |  | - | N | 000 | - | 200
VA00010 | 08 | 32 | 4" | VA | 00010 | B-1 | N | 0 | 1123-ACW-SM-035 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00026 | 08 | 32 | 4" | VA | 00026 | B-1 | N | 0 | 2121-ACW-SM-095 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00041 | 08 | 32 | 4" | VA | 00041 | B-1 | N | 0 | 2131-ACW-SM-060 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00082 | 08 | 32 | 4" | VA | 00082 | B-1 | N | 0 | 4221-ACW-SM-104 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00084 | 08 | 32 | 4" | VA | 00084 | B-1 | N | 0 | 2121-ACW-SM-094 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00088 | 08 | 32 | 4" | VA | 00088 | B-1 | N | 0 | 6111-ACW-SM-054 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00101 | 08 | 32 | 4" | VA | 00101 | B-1 | N | 0 | 6111-ACW-SM-079 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00104 | 08 | 32 | 4" | VA | 00104 | B-1 | N | 0 | 7111-ACW-SM-082 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA14002 | 08 | 32 | 2" | VA | 14002 | B4S2 | N | 0 | N14023 | SAFE LOCATION OUTSIDE CATALYST BUILDING | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.7 | 2 | NA | NA | NA | 6 | N | 32-P-026-01 |  | E | N | 000 | N | 183
VA14007 | 08 | 32 | 1" | VA | 14007 | B4S2 | N | 0 | CHWR14006 | AT SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.8 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
LO32001 | 08 | 32 | 1/2" | LO | 32001 | QXB-55 | N | 0 | TP-20A, LO320114 (LO320313) | TP-19A, PK-3600, COMPRESSOR INTERNAL PIPE | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
IW64001 | 08 | 32 | 3/4" | IW | 64001 | B-1 | N | 0 | IW64002 | 32-US-1129-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64004 | 08 | 32 | 3/4" | IW | 64004 | B-1 | N | 0 | IW64003 | 32-US-1123-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64022 | 08 | 32 | 3/4" | IW | 64022 | B-1 | N | 0 | IW64016 | 32-US-1121-06 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64025 | 08 | 32 | 1" | IW | 64025 | B-1 | N | 0 | IW01001 | IW64028 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64028 | 08 | 32 | 3/4" | IW | 64028 | B-1 | N | 0 | IW64025 | 32-US-1121-08 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64029 | 08 | 32 | 3/4" | IW | 64029 | B-1 | N | 0 | IW64025 | 32-US-1121-09 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64043 | 08 | 32 | 3/4" | IW | 64043 | B-1 | N | 0 | IW64025 | TO TRENCH | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
N6700R | 08 | 32 | 1/2" | N | 6700R | B-1 | N | 0 | N67020 | 32-AFR-5211 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67078 | 08 | 32 | 1/2" | N | 67078 | B-1 | N | 0 | N67017 | 32-D-6500 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67079 | 08 | 32 | 2" | N | 67079 | B-1 | N | 0 | N67029 | N67075 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67105 | 08 | 32 | 1" | N | 67105 | B-1 | N | 0 | N67029 | BDL60048 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67112 | 08 | 32 | 1" | N | 67112 | B-1 | N | 0 | N67013 | BDL60057 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N71017 | 08 | 32 | 3" | N | 71017 | B4S2 | P | 30 | N72007 | TP001 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.48 | 2 | Art 4.3 | NA | N | 7 | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N73004 | 08 | 32 | 1" | N | 73004 | B-1 | N | 0 | NITROGEN CONNECTION | BU01001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.54 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | E | N | 000 | N | 140
N81021 | 08 | 32 | 1/2" | N | 81021 | 1CS2 | N | 0 | N89007 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N89048 | 08 | 32 | 1" | N | 89048 | B-1 | N | 0 | N01001 | IW89027 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
PR72002 | 08 | 32 | 2" | PR | 72002 | C42S1 | N | 0 | 32-S-7201A | 32-D-3300 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72008 | 08 | 32 | 6" | PR | 72008 | C42S1 | N | 0 | PR01001 | PR72009 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72044 | 08 | 32 | 1" | PR | 72044 | C42S1 | N | 0 | 32-S-7201A | BDL72045 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72046 | 08 | 32 | 1" | PR | 72046 | C42S1 | N | 0 | 32-S-7201A | BDL72046 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72063 | 08 | 32 | 3/4" | PR | 72063 | C42S1 | N | 0 | PR720131 | BDL72068 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52C | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PW50017 |  | 32 | 1" | PW | 50017 | B4S2 | P | 50 | 32-T-5001 | PW50018 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50021 | 08 | 32 | 6" | PW | 50021 | B4S2 | N | 0 | PW50020 | PW52015 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW51015 | 08 | 32 | 2" | PW | 51015 | B4S1 | N | 0 | 32-D-5102 | BDL51009 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51016 |  | 32 | 3/4" | PW | 51016 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51016 |  | 32 | 1-1/2" | PW | 51016 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5101 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW52014 | 08 | 32 | 1/2" | PW | 52014 | B4S2 | N | 0 | 32-P-5200B | PW52010 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52014 | 08 | 32 | 4" | PW | 52014 | B4S2 | N | 0 | 32-P-5200B | PW52010 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52014 | 08 | 32 | 6" | PW | 52014 | B4S2 | N | 0 | 32-P-5200B | PW52010 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | I | MOD.A | Y | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
PW52016 | 08 | 32 | 2" | PW | 52016 | B4S2 | N | 0 | 32-D-5202 | 32-P-5200A | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PW52016 | 08 | 32 | 8" | PW | 52016 | B4S2 | N | 0 | 32-D-5202 | 32-P-5200A | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
BDL32029 | 08 | 32 | 3" | BDL | 32029 | B32S1 | HB | 30 | HCM32044, PSV-3280 | BDL60030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL51024 | 08 | 32 | 3" | BDL | 51024 | B4S1 | ST | 30 | TP-N12 (BDL510124) | 32-D-5104 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 20 | N | 32-P-050-04 |  | G | N | 141 | N | 470 | ,10
BDL60024 | 08 | 32 | 2" | BDL | 60024 | B32S1 | N | 0 | BDL60058 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL61009 | 08 | 32 | 2" | BDL | 61009 | B32S1 | N | 0 | TP-020 (32-PSV-6177) | BDL61001 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61025 | 08 | 32 | 3/4" | BDL | 61025 | B32S1 | N | 0 | PR610114 | BDL61015 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
BDL72027 | 08 | 32 | 3/4" | BDL | 72027 | B32S1 | N | 0 | PR01001 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72045 | 08 | 32 | 2" | BDL | 72045 | B32S1 | N | 0 | PR72044 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72047 | 08 | 32 | 2" | BDL | 72047 | B32S1 | N | 0 | PR72041 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.53 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL24097 | 08 | 32 | 1" | BDL | 24097 | B32S1 | N | 0 | HCM24095 | BDL60034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31038 | 08 | 32 | 3/4" | BDL | 31038 | B32S1 | N | 0 | BDL31039 | BDL31034 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL34017 | 08 | 32 | 3/4" | BDL | 34017 | B4S1 | N | 0 | PR34027 | BDL34016 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL35008 | 08 | 32 | 1" | BDL | 35008 | B4S1 | N | 0 | PR36012 | BDL60031 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.27 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL35009 | 08 | 32 | 4" | BDL | 35009 | B4S1 | N | 0 | PR35015 | BDL60031 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL36017 | 08 | 32 | 3" | BDL | 36017 | B32S1 | N | 0 | 32-PSV-3684, PR36019 | BDL36018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36017 | 08 | 32 | 6" | BDL | 36017 | B32S1 | N | 0 | 32-PSV-3684, PR36019 | BDL36018 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36018 | 08 | 32 | 6" | BDL | 36018 | B32S1 | N | 0 | BDL36017 | BDL36010 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL37008 | 08 | 32 | 3/4" | BDL | 37008 | B32S1 | N | 0 | 32-Z-7300 | BDL73044 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL43017 | 08 | 32 | 1/2" | BDL | 43017 | B32S1 | N | 0 | PR43051 | BDL43016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL43019 | 08 | 32 | 1/2" | BDL | 43019 | B32S1 | N | 0 | BDL24095 | BDL60036 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
VZ12013 | 08 | 32 | 3/4" | VZ | 12013 | 1CS2 | ET | 30 | 32-S-1200B | DRAIN | 5.0 | 150.0 | 0.1 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 273 | 23,25
VZ24005 |  | 32 | 1" | VZ | 24005 | D20S1 | HB | 30 | 32-S-2400 | BDL24001 | 52.0/52.0 | 150.0/-45.0 | 39.2 | 73.0 |  | 78.01 | 153.15 | H | VESSEL TRIM | L | - | - | >1.5 | 73 | sh.19 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-045-01 |  | F | N | 141 | N | 513 | 15
WW64009 | 08 | 32 | 1-1/2" | WW | 64009 | B4S2 | N | 0 | FROM LC-23051 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
IA02011 | 08 | 32 | 1/2" | IA | 02011 | B-13 | N | 0 | IA02002 | 100 LITERS AIR TANK | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.68M | 2 | Art 4.3 | NA | N | 4 | N | 32-P-070-09 |  | - | N | 000 | - | 200
JCW86019 | 08 | 32 | 2" | JCW | 86019 | B-1 | HB | 30 | CWS86017 | CWR86001 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
IA89013 | 08 | 32 | 1/2" | IA | 89013 | B-13 | N | 0 | IA62006 | TP-N50609 (S-8909A/B/C/D, PCV-8962) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IW89039 | 08 | 32 | 3/4" | IW | 89039 | B-1 | N | 0 | IW01001 | 32-US-1211-03 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
JCW86013 |  | 32 | 1/2" | JCW | 86013 | B-1 | HB | 30 | JCW86016 | JCW86012 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86014 |  | 32 | 1-1/2" | JCW | 86014 | B-1 | HB | 30 | JCW86017 | CWR86013 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86015 |  | 32 | 1-1/2" | JCW | 86015 | B-1 | HB | 30 | CWS86017 | CWR86012 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JWR23003 | 08 | 32 | 2" | JWR | 23003 | B-1 | N | 0 | TP-4 (JWR230102) | JWR67003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR32005 | 08 | 32 | 1-1/2" | JWR | 32005 | C3S1 | N | 0 | JWR32001 | VA32002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR36002 | 08 | 32 | 2" | JWR | 36002 | B-1 | N | 0 | TP-146 (JWS360136) | JWR36001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40005 | 08 | 32 | 2" | JWR | 40005 | B-1 | N | 0 | TP-4 (JWR400102) | JWR40003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWS63003 | 08 | 32 | 1-1/2" | JWS | 63003 | B-1 | N | 0 | JWS63004 | 32-P-6300A/N5 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | N | 000 | N | 10
LC63039 |  | 32 | 6" | LC | 63039 | B-5 | P | 50 | 32-E-6300 | TO SAFE LOCATION | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63078 |  | 32 | 2" | LC | 63078 | B-5 | HB | 40 | LC6300G | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LN89005 | 08 | 32 | 1/2" | LN | 89005 | B-1 | N | 0 | LN89001 | LN81002 | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 26.46 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 172
LPN02005 | 08 | 32 | 1" | LPN | 02005 | 1C13 | N | 0 | LPN01001 | LPN10008 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN11005 | 08 | 32 | 1/2" | LPN | 11005 | 3DS3 | N | 0 | TEA11013 | LPN11004 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LS16184 |  | 32 | 1" | LS | 16184 | B-5 | HB | 70 | LS63183 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23019 |  | 32 | 3/4" | LS | 23019 | B-5 | HB | 60 | LS63067 | LS23018 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.18 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23030 |  | 32 | 1/2" | LS | 23030 | B-5 | HB | 60 | JLS23019 | LC63147 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.15 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N02002 | 08 | 32 | 3/4" | N | 02002 | B-1 | N | 0 | N67013 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N15004 | 08 | 32 | 1/2" | N | 15004 | B-1 | N | 0 | 32-S-1501 | N15001 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.9 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N32006 | 08 | 32 | 1" | N | 32006 | B4S1 | N | 0 | TP-28A, (CYLINDER) | 32-D-3204 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N36017 | 08 | 32 | 1/2" | N | 36017 | B4S1 | N | 0 | TP-188 (32-D-3608) | N36018 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36021 | 08 | 32 | 1" | N | 36021 | B4S1 | N | 0 | TP-171 (CYLINDER 2, STAGE 2, PACKING 2, C79) | N36012 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N40006 | 08 | 32 | 1" | N | 40006 | B-1 | N | 0 | NITROGEN CONNECTION | ET71039 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 140
N89058 | 08 | 32 | 3/4" | N | 89058 | B-1 | N | 0 | N89067 | N89052 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N91015 | 08 | 32 | 2" | N | 91015 | 1CS2 | N | 0 | N91013 | 32-V-9001B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.70 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-01 |  | M | N | 000 | N | 166
O13010 | 7A | 32 | 1" | O | 13010 | 1CS2 | P | 50 | O13020 | O13004 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O15003 |  | 32 | 1/2" | O | 15003 | 1FS4 | ET | 30 | O15004 | O14010 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O31015 |  | 32 | 1/2" | O | 31015 | B4S2 | ET | 30 | O31007 | O31016 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
O67010 | 08 | 32 | 1" | O | 67010 | 1CS2 | N | 0 | O66015 | PX86022 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
P23015 | 7A | 32 | 1" | P | 23015 | 1FS4 | HB | 30 | P23019 | P23017 | 42.0/42.0 | -40.0/200.0 | 18.0 | 90.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.17 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 141 | N | 344 | ,10
PP89009 | 08 | 32 | 8" | PP | 89009 | 5CS7 | N | 0 | TP-N51102 (D-8901) | 32-PK-8300 | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.63 | 1 | NA | NA | NA | NR | N | 32-P-082-07 |  | M | N | 110 | N | 443 | 6,25,23
PR21012 |  | 32 | 1/2" | PR | 21012 | 1FS4 | CF | 25 | HN21006 | PR21014 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | Art 4.3 | NA | N | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR31016 | 08 | 32 | 1-1/2" | PR | 31016 | 1FS4 | N | 0 | PR31022 | JLS31010 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR34024 |  | 32 | 1" | PR | 34024 | B4S1 | P | 50 | 32-S-3401B | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-01,32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR36036 | 08 | 32 | 2" | PR | 36036 | B32S1 | P | 50 | TP-111 (32-D-3604) | PR36021 | 10.0/10.0 | -45.0/180.0 | 5.5 | 107.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 107 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 357 | 10
PR40020 |  | 32 | 1-1/2" | PR | 40020 | C42S1 | ST | 30 | PR40029 | PR40026 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | G | N | 141 | N | 338 | 10
PR72010 | 08 | 32 | 6" | PR | 72010 | C42S1 | N | 0 | PR72009 | PR72015 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72019 | 08 | 32 | 1" | PR | 72019 | C42S1 | HA | 30 | TP-012 (PR720116) | PR72015 | 43.7/43.7 | -45.0/120.0 | 30.0 | 65.0 |  | 65.55 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 65 | sh.52D | 1 | Art 4.3 | NA | N | 20 | N | 32-P-007-04 |  | G | N | 141 | N | 356 | 10
PR72071 | 08 | 32 | 1" | PR | 72071 | C42S1 | N | 0 | PR72064 | BDL72069 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | Art 4.3 | NA | N | 7 | N | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PW50022 |  | 32 | 1-1/2" | PW | 50022 | B4S2 | P | 50 | PW50025 | PW50017 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
CWS89050 | 08 | 32 | 4" | CWS | 89050 | B-1 | N | 0 | CWS89038 | TP-N20105 (32-E-8901) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.68C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
DO12035 |  | 32 | 1" | DO | 12035 | 1CS2 | ET | 30 | 32-S-1200C | DO12022 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
LS89057 | 08 | 32 | 1/2" | LS | 89057 | B-5 | HB | 60 | LS89035 | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
HN72009 | 08 | 32 | 1" | HN | 72009 | C6S1 | N | 0 | SP-04-172B1-06 | PR720105 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
CD31004 | 08 | 32 | 1" | CD | 31004 | 1CS2 | N | 0 | 32-SP-04-13100-07 | P31016 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | F | N | 100 | N | 288
IW64038 | 08 | 32 | 3/4" | IW | 64038 | B-1 | N | 0 | IW64025 | 32-US-1121-16 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64044 | 08 | 32 | 3/4" | IW | 64044 | B-1 | N | 0 | IW01001 | 32-US-1111-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64050 | 08 | 32 | 3/4" | IW | 64050 | B-1 | N | 0 | IW01001 | 32-US-1111-002 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89035 | 08 | 32 | 3/4" | IW | 89035 | B-1 | N | 0 | IW89020 | US-3211-05 EL.10000 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89037 | 08 | 32 | 3/4" | IW | 89037 | B-1 | N | 0 | IW89020 | US-3221-01 AT GRADE | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
JWS64011 | 08 | 32 | 1" | JWS | 64011 | B-1 | N | 0 | JWS64008 | 32-Z-6400 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64026 | 08 | 32 | 3" | JWS | 64026 | B-1 | N | 0 | JWS64025 | TP-3 (JWS400100) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64061 | 08 | 32 | 8" | JWS | 64061 | B-1 | N | 0 | JWS64053 | JWS61001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
LC02004 |  | 32 | 3/4" | LC | 02004 | B-5 | HB | 30 | LS02004 | LC02001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23040 |  | 32 | 1/2" | LC | 23040 | B-5 | HB | 30 | LS23021 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31031 |  | 32 | 1/2" | LC | 31031 | B-5 | HB | 30 | LS31030 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31039 | 08 | 32 | 1/2" | LC | 31039 | B-5 | HB | 30 | LS31036 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34001 |  | 32 | 1/2" | LC | 34001 | B-5 | HB | 30 | LS34006 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34003 |  | 32 | 1/2" | LC | 34003 | B-5 | HB | 30 | LS34005 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC6300H |  | 32 | 1-1/2" | LC | 6300H | B-5 | HB | 40 | 32-1121-R-006 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63035 |  | 32 | 3" | LC | 63035 | B-5 | P | 50 | LC63034 | 32-D-6300 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LS31044 | 08 | 32 | 1-1/2" | LS | 31044 | B-5 | HB | 70 | PR31023 | LC31044 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS34004 |  | 32 | 1/2" | LS | 34004 | B-5 | HB | 60 | LS63030 | LC34004 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60028 |  | 32 | 1" | LS | 60028 | B-5 | HB | 70 | Hose connection | BDL60058 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-01 |  | E | N | 000 | N | 90
LS60032 |  | 32 | 1" | LS | 60032 | B-5 | HB | 70 | PURGE CONNECTION | BDL60063 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78A | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS6300L |  | 32 | 1" | LS | 6300L | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300Q |  | 32 | 1" | LS | 6300Q | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63033 | 08 | 32 | 3/4" | LS | 63033 | B-5 | HB | 60 | LS63193 | JLS31010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AC |  | 32 | 1-1/2" | LS | 630AC | B-5 | HB | 70 | LS63183 | 32-1111-S-011 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630BA |  | 32 | 3/4" | LS | 630BA | B-5 | HB | 60 | LS63178 | LC6300U | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63129 |  | 32 | 6" | LS | 63129 | B-5 | HB | 90 | LS63177 | LS72129 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63178 |  | 32 | 3" | LS | 63178 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63195 |  | 32 | 1" | LS | 63195 | B-5 | HB | 70 | LS63206 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63198 |  | 32 | 1" | LS | 63198 | B-5 | HB | 70 | LS63197 | CAP | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N6700B | 08 | 32 | 3/4" | N | 6700B | B-1 | N | 0 | N67017 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700C | 08 | 32 | 1" | N | 6700C | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700G | 08 | 32 | 3/4" | N | 6700G | B-1 | N | 0 | N01009 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67050 | 08 | 32 | 2" | N | 67050 | B-1 | N | 0 | HEADER | N01001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67059 | 08 | 32 | 1" | N | 67059 | B-1 | N | 0 | N67050 | TP-151 (N360141) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67069 | 08 | 32 | 3/4" | N | 67069 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67075 | 08 | 32 | 1-1/2" | N | 67075 | B-1 | N | 0 | N67079 | N80023 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N71020 | 08 | 32 | 1" | N | 71020 | B-1 | N | 0 | NITROGEN CONNECTION | ET71038 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.50B | 2 | Art 4.3 | NA | N | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 140
N80025 | 08 | 32 | 2" | N | 80025 | B-1 | N | 0 | 32-D-8001 | 32-AE-8001 | 4.5/-0.5 | 110.0/110.0 | 2.75 | 60.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 60 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-060-01 |  | E | N | 000 | N | 149
N81019 | 08 | 32 | 1/2" | N | 81019 | 1CS2 | N | 0 | N89006 | 32-PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60A | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
P40027 |  | 32 | 1/2" | P | 40027 | QXC25S2 | ST | 30 | P40030 | 32-Z-4004B | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
PA02010 | 08 | 32 | 3/4" | PA | 02010 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62051 | 08 | 32 | 3/4" | PA | 62051 | B-1 | N | 0 | PA62045 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62081 | 08 | 32 | 3/4" | PA | 62081 | B-1 | N | 0 | PA62080 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62083 | 08 | 32 | 3/4" | PA | 62083 | B-1 | N | 0 | PA62080 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62092 | 08 | 32 | 3/4" | PA | 62092 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89056 | 08 | 32 | 3/4" | PA | 89056 | B-1 | N | 0 | PA62055 | FX-6269 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PCW89017 | 08 | 32 | 12" | PCW | 89017 | 1CS2 | P | 100 | TP-N50705 (P-8900A/B) | TP-N50801 (S-8910A/B) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
SWW92018 | 08 | 32 | 8" | SWW | 92018 | 1CS2 | N | 0 | DETAIL A | SWW92004 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92030 | 08 | 32 | 2" | SWW | 92030 | 1CS2 | N | 0 | SWW92005 | 32-S-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
VA00024 | 08 | 32 | 4" | VA | 00024 | B-1 | N | 0 | 2121-ACW-VP-015 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00030 | 08 | 32 | 4" | VA | 00030 | B-1 | N | 0 | 2121-ACW-SM-107 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00048 | 08 | 32 | 4" | VA | 00048 | B-1 | N | 0 | 2211-ACW-SM-091 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00062 | 08 | 32 | 4" | VA | 00062 | B-1 | N | 0 | 4111-ACW-SM-017 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00071 | 08 | 32 | 4" | VA | 00071 | B-1 | N | 0 | 4121-ACW-SM-021 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00077 | 08 | 32 | 4" | VA | 00077 | B-1 | N | 0 | 4131-ACW-SM-025 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00106 | 08 | 32 | 4" | VA | 00106 | B-1 | N | 0 | 2121-ACW-SM-084 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA35002 | 08 | 32 | 1" | VA | 35002 | B4S2 | N | 0 | JWR35001 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.27 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA52016 | 08 | 32 | 6" | VA | 52016 | B4S2 | N | 0 | PN52030 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA52018 | 08 | 32 | 1" | VA | 52018 | B4S2 | N | 0 | JWR52003 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA60001 | 08 | 32 | 3" | VA | 60001 | B4S2 | N | 0 | LS63047 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.41 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA72001 | 08 | 32 | 1" | VA | 72001 | B4S2 | N | 0 | JWS72005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.51 | 2 | NA | NA | NA | 6 | N | 32-U-022-01 |  | E | N | 000 | N | 183
VA81024 | 08 | 32 | 8" | VA | 81024 | B4S2 | N | 0 | 32-C-8124 | OUTDOOR TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.61 | 2 | NA | NA | NA | 6 | N | 32-P-061-02 |  | E | N | 000 | N | 183
VA81026 | 08 | 32 | 1" | VA | 81026 | B4S2 | N | 0 | 32-PSV-8111 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.59 | 2 | NA | NA | NA | 6 | N | 32-P-070-01 |  | E | N | 000 | N | 183
VA89022 | 08 | 32 | 1" | VA | 89022 | B4S2 | N | 0 | CWR89049 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.68C | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
FW68I11 | 08 | 32 | 2" | FW | 68I11 | B-13 | N | 0 | FW68I08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I11 | 08 | 32 | 3" | FW | 68I11 | B-13 | N | 0 | FW68I08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I17 | 08 | 32 | 1-1/2" | FW | 68I17 | B-13 | N | 0 | FW68I19 | FW68I15 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I42 | 08 | 32 | 1" | FW | 68I42 | B-13 | N | 0 | FW68I21 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68K01 | 08 | 32 | 1/2" | FW | 68K01 | B-7 | N | 0 | XV6803A | XV6803A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K01 | 08 | 32 | 6" | FW | 68K01 | B-7 | N | 0 | XV6803A | XV6803A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K11 | 08 | 32 | 3/4" | FW | 68K11 | B-7 | N | 0 | FW68A19 | FW68K09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68L05 | 08 | 32 | 1" | FW | 68L05 | B-13 | N | 0 | FW68K12 | FW68L20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L05 | 08 | 32 | 4" | FW | 68L05 | B-13 | N | 0 | FW68K12 | FW68L20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L07 | 08 | 32 | 1" | FW | 68L07 | B-13 | N | 0 | MSN-002 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L10 | 08 | 32 | 1" | FW | 68L10 | B-13 | N | 0 | FW68L02 | FW68L02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L10 | 08 | 32 | 2" | FW | 68L10 | B-13 | N | 0 | FW68L02 | FW68L02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L20 | 08 | 32 | 1" | FW | 68L20 | B-13 | N | 0 | FW68L05 | MSN-006 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L20 | 08 | 32 | 2" | FW | 68L20 | B-13 | N | 0 | FW68L05 | MSN-006 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L23 | 08 | 32 | 1-1/2" | FW | 68L23 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68L25 | 08 | 32 | 1" | FW | 68L25 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L25 | 08 | 32 | 2" | FW | 68L25 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68M01 | 08 | 32 | 1" | FW | 68M01 | B-13 | N | 0 | FW68M46 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M12 | 08 | 32 | 1" | FW | 68M12 | B-13 | N | 0 | FW68M11 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
PCW89012 | 08 | 32 | 24" | PCW | 89012 | 1CS2 | P | 100 | TPN50402 (A-8900) | TP-N50601 (S-8909A/B/C/D) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68N | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PCW89016 | 08 | 32 | 12" | PCW | 89016 | 1CS2 | N | 0 | TP-N50902 (E-8900A) | TP-N51507 (32-E-8900A) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68O | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
HCM23045 |  | 32 | 1" | HCM | 23045 | 1FS4 | ST | 30 | HCM23044 | HCM23048 | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-047-04 |  | G | N | 141 | N | 332 | 10
HCM23049 |  | 32 | 1-1/2" | HCM | 23049 | 1FS4 | HB | 30 | JLS23008 | HCM23050 | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23066 | 08 | 32 | 1/2" | HCM | 23066 | 1FS4 | N | 0 | 32-R-2300 | 32-PDT-2301 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23066 |  | 32 | 3/4" | HCM | 23066 | 1FS4 | JP | 0 | 32-R-2300 | 32-PDT-2301 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23070 |  | 32 | 1/2" | HCM | 23070 | 1FS4 | JP | 0 | LS63147 | 32-R-2300 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23070 |  | 32 | 3/4" | HCM | 23070 | 1FS4 | JP | 0 | LS63147 | 32-R-2300 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
SWW92027 | 08 | 32 | 1-1/2" | SWW | 92027 | 1CS2 | N | 0 | 32-H-9001C | SWW92013 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
TEA11009 | 08 | 32 | 1/2" | TEA | 11009 | 3FS3 | N | 0 | TEA11012 | 32-P-1100A | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
TEA11011 | 08 | 32 | 1/2" | TEA | 11011 | 3FS3 | N | 0 | 32-P-1100B | TEA11006 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
TEA11013 | 08 | 32 | 1" | TEA | 11013 | 3DS3 | N | 0 | FO11012 | TEA11001 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11210 | 08 | 32 | 1" | TEA | 11210 | 3FS3 | N | 0 | TEA11026 | 32-P-1100B | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
HN24002 | 08 | 32 | 1-1/2" | HN | 24002 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24063 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.19 | 2 | I | MOD.A | Y | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 170
HN67014 | 08 | 32 | 3/4" | HN | 67014 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67017 | 08 | 32 | 3/4" | HN | 67017 | C6S1 | N | 0 | HN67002 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67020 | 08 | 32 | 3/4" | HN | 67020 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67020 | 08 | 32 | 1-1/2" | HN | 67020 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67021 | 08 | 32 | 1-1/2" | HN | 67021 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
IW64074 | 08 | 32 | 3/4" | IW | 64074 | B-1 | N | 0 | IW64003 | 32-US-1124-003 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89023 | 08 | 32 | 1" | IW | 89023 | B-1 | N | 0 | IW01001 | 32-US-1211-10 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW6200I | 08 | 32 | 3/4" | IW | 6200I | B-1 | N | 0 | IW64027 | AT GRADE | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64010 | 08 | 32 | 3/4" | IW | 64010 | B-1 | N | 0 | IW01001 | IW64011 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64021 | 08 | 32 | 3/4" | IW | 64021 | B-1 | N | 0 | IW64016 | 32-US-1121-05 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64037 | 08 | 32 | 3/4" | IW | 64037 | B-1 | N | 0 | IW64025 | 32-US-1121-15 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64039 | 08 | 32 | 3/4" | IW | 64039 | B-1 | N | 0 | IW64025 | 32-US-1121-17 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89026 | 08 | 32 | 3/4" | IW | 89026 | B-1 | N | 0 | IW89023 | 32-US-1211-09 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89028 | 08 | 32 | 3/4" | IW | 89028 | B-1 | N | 0 | IW01001 | IW89029 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89032 | 08 | 32 | 3/4" | IW | 89032 | B-1 | N | 0 | IW89020 | US-3221-01 AT GRADE | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
CHWR20004 | 08 | 32 | 1" | CHWR | 20004 | B-5 | N | 0 | JLS20001 | JLS20001 | 9.0 | 280.0 | 6.0/6.0 | 10.0/170.0 |  | 14.51 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | >1.5 | 10 | sh.11 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-023-01 |  | A | N | 010 | N | 54
CHWR61008 | 08 | 32 | 6" | CHWR | 61008 | B-1 | N | 0 | 32-D-6101 | CHWR61007 | 3.5 | 100.0 | 0.0/0.0 | 7.0/2.0 |  | 5.25 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-02 |  | E | N | 010 | N | 53
CHWR61013 |  | 32 | 10" | CHWR | 61013 | B-1 | CF | 40 | CHWR61002 | CHWR61012 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWS14005 |  | 32 | 3/4" | CHWS | 14005 | B-1 | CF | 25 | CHWR15007 | 32-P-1401 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14005 |  | 32 | 1" | CHWS | 14005 | B-1 | CF | 25 | CHWR15007 | 32-P-1401 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS14005 |  | 32 | 2" | CHWS | 14005 | B-1 | CF | 25 | CHWR15007 | 32-P-1401 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20004 |  | 32 | 1" | CHWS | 20004 | B-1 | CF | 25 | 32-R-2000 | 32-Z-2005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS20005 |  | 32 | 2" | CHWS | 20005 | B-1 | CF | 25 | 32-Z-2005 | 32-P-2000 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
BDL23051 | 08 | 32 | 1/2" | BDL | 23051 | B32S1 | N | 0 | HCM22003 | BDL22019 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.16 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23079 | 08 | 32 | 1" | BDL | 23079 | B32S1 | N | 0 | PR23005 | BDL23016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
BDL2400A | 08 | 32 | 3/4" | BDL | 2400A | B32S1 | N | 0 | TP-5 (HCM240108) | BDL24057 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.21A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
IW64008 | 08 | 32 | 3/4" | IW | 64008 | B-1 | N | 0 | IW64009 | 32-US-1113-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64015 | 08 | 32 | 3/4" | IW | 64015 | B-1 | N | 0 | IW01001 | IW64014 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64030 | 08 | 32 | 3/4" | IW | 64030 | B-1 | N | 0 | IW64025 | 32-US-1121-10 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64047 | 08 | 32 | 3/4" | IW | 64047 | B-1 | N | 0 | IW64046 | 32-US-1127-005 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64071 | 08 | 32 | 3/4" | IW | 64071 | B-1 | N | 0 | IW64072 | 32-US-1124-002 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89020 | 08 | 32 | 2" | IW | 89020 | B-1 | N | 0 | IW01001 | HEADER | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89027 | 08 | 32 | 3/4" | IW | 89027 | B-1 | N | 0 | IW01001 | LS89051 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89041 | 08 | 32 | 3/4" | IW | 89041 | B-1 | N | 0 | IW89028 | IW89040 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
JCW86012 |  | 32 | 1-1/2" | JCW | 86012 | B-1 | HB | 30 | JCW86013 | JCW86011 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86020 |  | 32 | 2" | JCW | 86020 | B-1 | HB | 30 | CWS86019 | JCW86021 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JW73001 |  | 32 | 3" | JW | 73001 | B-1 | JR | 0 | BU73040 | BU73040 | 9.0 | 175.0 | 7.0 | 80.0 |  | 13.53 | 29.4 | H | JACKET WATER | L | - | - | >1.5 | 80 | sh.55 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-001-02 |  | E | N | 000 | N | 88
JWR14002 | 08 | 32 | 3/4" | JWR | 14002 | B-1 | N | 0 | 32-E-1450A | JWR14003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.7 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
FW68A0M | 08 | 45 | 10" | FW | 68A0M | UGB-1PE | N | 0 | FW68A85 | FW68A86 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A33 | 08 | 45 | 8" | FW | 68A33 | PEB-69 | N | 0 | FW68A20 | FW68A97 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A43 | 08 | 45 | 1-1/2" | FW | 68A43 | B-7 | N | 0 | FW68A38 | 45-HR-6804 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A46 | 08 | 45 | 18" | FW | 68A46 | PEB-69 | N | 0 | FW68A17 | FW68A83 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A54 | 08 | 45 | 3/4" | FW | 68A54 | B-7 | N | 0 | FW68B93 | FW68D09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A72 | 08 | 45 | 1-1/2" | FW | 68A72 | B-13 | N | 0 | FW68A34 | 45-HR-6852 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-01 |  | - | Y | 000 | - | 74
FW68A96 | 08 | 45 | 12" | FW | 68A96 | UGB-1PE | N | 0 | FW68A18 | FW68A19 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0S | 08 | 45 | 6" | FW | 68B0S | UGB-1PE | N | 0 | FW68B72 | 45-HY-6821 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B47 | 08 | 45 | 10" | FW | 68B47 | PEB-69 | N | 0 | FW68A03 | FW68B0H | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B82 | 08 | 45 | 1-1/2" | FW | 68B82 | B-7 | N | 0 | FW68B40 | 45-HR-6820 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-02 |  | E | N | 000 | N | 75
FW68B99 | 08 | 45 | 6" | FW | 68B99 | UGB-1PE | N | 0 | FW68B27 | FW68B16 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68C02 | 08 | 32 | 4" | FW | 68C02 | B-7 | N | 0 | FW68C01 | 32-XV-6801A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C07 | 08 | 32 | 4" | FW | 68C07 | B-13 | N | 0 | 32-XV-6801A | FW68H30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68D07 | 08 | 45 | 1" | FW | 68D07 | B-13 | N | 0 | 45-XV-6816A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68E08 | 08 | 32 | 3/4" | FW | 68E08 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E25 | 08 | 32 | 3/4" | FW | 68E25 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E25 | 08 | 32 | 3" | FW | 68E25 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
VA31002 | 08 | 32 | 1" | VA | 31002 | B4S2 | N | 0 | CWR93006 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.73 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
VA40001 | 08 | 32 | 1-1/2" | VA | 40001 | B4S2 | N | 0 | TP-8 (PN400109) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.30A | 2 | NA | NA | NA | 6 | N | 32-P-049-02 |  | E | N | 000 | N | 183
VA52017 | 08 | 32 | 1" | VA | 52017 | B4S2 | N | 0 | JWR52002 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA64004 | 08 | 32 | 1" | VA | 64004 | B4S2 | N | 0 | JWS64001 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.44 | 2 | NA | NA | NA | 6 | N | 32-U-022-01 |  | E | N | 000 | N | 183
VA81025 | 08 | 32 | 1" | VA | 81025 | B4S2 | N | 0 | 32-PSV-8110 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.59 | 2 | NA | NA | NA | 6 | N | 32-P-070-01 |  | E | N | 000 | N | 183
IW64051 | 08 | 32 | 3/4" | IW | 64051 | B-1 | N | 0 | IW01001 | IW64052 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64073 | 08 | 32 | 3/4" | IW | 64073 | B-1 | N | 0 | IW64003 | 32-US-1124-004 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89029 | 08 | 32 | 3/4" | IW | 89029 | B-1 | N | 0 | IW89028 | PA89037 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89036 | 08 | 32 | 3/4" | IW | 89036 | B-1 | N | 0 | IW89020 | US-3211-03 AT GRADE | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
JLS23011 |  | 32 | 1-1/2" | JLS | 23011 | B-5 | HB | 50 | HCM23057 | HCM23063 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS31010 | 08 | 32 | 3" | JLS | 31010 | B-5 | N | 0 | PR31022 | PR31016 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 6 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JWR37002 | 08 | 32 | 3/4" | JWR | 37002 | B-1 | N | 0 | 32-Z-2400B | JWR37001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.29 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR43001 | 08 | 32 | 3/4" | JWR | 43001 | C3S1 | N | 0 | 32-E-4301 | JWR43002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.33 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR43001 | 08 | 32 | 3" | JWR | 43001 | C3S1 | N | 0 | 32-E-4301 | JWR43002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.33 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
DW69024 | 08 | 32 | 3/4" | DW | 69024 | B-13 | IS | 50 | DW69022 | TO SUB-STATION | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
ET71060 | 08 | 32 | 1-1/2" | ET | 71060 | C3S1 | N | 0 | 32-T-7110B | CATALYST DISCHARGE | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 7 | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
LS31019 |  | 32 | 1-1/2" | LS | 31019 | B-5 | HB | 70 | LS63039 | PR31023 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS32002 |  | 32 | 1/2" | LS | 32002 | B-5 | HB | 60 | 32-E-3200 | LC32002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.24 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50046 |  | 32 | 3/4" | LS | 50046 | B-5 | HB | 30 | P50017 | LC50003 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 92
LS50049 |  | 32 | 8" | LS | 50049 | 3CS6 | HB | 100 | 32-S-5001 | LS50002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 11.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.34 | 2 | I | MOD.A | Y | NR | N | 32-U-052-01 |  | M | N | 000 | N | 103
LS60007 |  | 32 | 1-1/2" | LS | 60007 | B-5 | HB | 70 | 32-D-6011 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.41 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-02 |  | E | N | 000 | N | 90
LS60017 |  | 32 | 1" | LS | 60017 | B-5 | HB | 70 | PURGE CONNECTION | BDL60047 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60027 |  | 32 | 1" | LS | 60027 | B-5 | HB | 70 | HOSE CONNECTION | BDL60057 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-01 |  | E | N | 000 | N | 90
LS61001 |  | 32 | 1" | LS | 61001 | B-5 | HB | 70 | JLS61001 | LC61001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.42 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63007 |  | 32 | 3/4" | LS | 63007 | B-5 | HB | 60 | LS63178 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
PA62031 | 08 | 32 | 3/4" | PA | 62031 | B-1 | N | 0 | PA62032 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62042 | 08 | 32 | 3/4" | PA | 62042 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62049 | 08 | 32 | 3/4" | PA | 62049 | B-1 | N | 0 | PA62045 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62080 | 08 | 32 | 1" | PA | 62080 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89046 | 08 | 32 | 3/4" | PA | 89046 | B-1 | N | 0 | PA89021 | US-3211-02 AT GRADE | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
BDL21014 | 08 | 32 | 1/2" | BDL | 21014 | B32S1 | N | 0 | HD22006 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-010-01 |  | G | N | 141 | N | 460 | 10
PX86027 |  | 32 | 1/2" | PX | 86027 | QXC25S1 | JP | 0 | 32-P-8600B | 32-Z-8600B | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86027 |  | 32 | 3/4" | PX | 86027 | QXC25S1 | JP | 0 | 32-P-8600B | 32-Z-8600B | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86038 | 08 | 32 | 1/2" | PX | 86038 | QXC25S1 | N | 0 | DRAIN BOX | PX86033 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
SA81010 | 08 | 32 | 6" | SA | 81010 | 1CS2 | N | 0 | 32-PK-8102 | 32-ZF-8108 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.59 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-03 |  | G | N | 200 | N | 406 | 6,10,23,25
PN52022 | 7A | 32 | 20" | PN | 52022 | 1CS2 | HB | 40 | PN52020 | 32-Z-5201B | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PP80003 | 08 | 32 | 14" | PP | 80003 | 5CS7 | N | 0 | 32-D-8002B | 32-ZF-8100B | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.58 | 1 | II | MOD.A2 | Y | NR | N | 32-P-060-01 |  | M | N | 110 | N | 439 | 6,23,25
PP83006 | 08 | 32 | 8" | PP | 83006 | 5CS7 | N | 0 | 32-PK-8300 | COLLECTING BOX (GROUND LEVEL) (BY CLIENT) TO BE GROUNDED | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.63 | 1 | NA | NA | NA | NR | N | 32-P-082-07 |  | M | N | 110 | N | 443 | 6,25,23
PR21017 |  | 32 | 1/2" | PR | 21017 | 1FS4 | CF | 25 | PR21009 | TP-10 (P-2100, CLEAR HC (PROPYLENE)) | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | Art 4.3 | NA | N | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21017 |  | 32 | 3/4" | PR | 21017 | 1FS4 | CF | 25 | PR21009 | TP-10 (P-2100, CLEAR HC (PROPYLENE)) | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | Art 4.3 | NA | N | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
DMW01001 | 08 | 32 | 3" | DMW | 01001 | SXB-48 | N | 0 | DMW220003 OSBL LINE | DMW64001 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.2 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-042-01 |  | M | N | 000 | N | 26
DO12036 |  | 32 | 1/2" | DO | 12036 | 1CS2 | ET | 30 | 32-D-1200C | 32-S-1200C | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12036 |  | 32 | 1-1/2" | DO | 12036 | 1CS2 | ET | 30 | 32-D-1200C | 32-S-1200C | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DW01001 | 08 | 32 | 2" | DW | 01001 | B-13 | IS | 50 | DW220003 OSBL LINE | DW69B05 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.2 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
FL60002 | 08 | 32 | 8" | FL | 60002 | B32S1 | N | 0 | 32-D-6001 | FL01001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
FL60003 |  | 32 | 2" | FL | 60003 | B32S1 | ST | 30 | 32-D-6002 | FL60002 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | I | MOD.A | Y | 20 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
FL60004 | 08 | 32 | 8" | FL | 60004 | B32S1 | N | 0 | BDH60004 | FL60001 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.41 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 490 | 10
FO11004 |  | 32 | 1" | FO | 11004 | 1CS2 | ET | 30 | FO11003 | FO11005 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | NR | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11007 | 08 | 32 | 1" | FO | 11007 | B4S2 | N | 0 | 32-P-1101 | FO11023 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11010 | 08 | 32 | 1/2" | FO | 11010 | 1CS2 | N | 0 | FO11003 | TEA11026 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11020 | 08 | 32 | 1/2" | FO | 11020 | 3DS3 | N | 0 | 32-S-1100 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FW68M31 | 08 | 32 | 1" | FW | 68M31 | B-13 | N | 0 | FW68M35 | FW68M35 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M35 | 08 | 32 | 2" | FW | 68M35 | B-13 | N | 0 | FW68K06 | FW68M31 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M42 | 08 | 32 | 1" | FW | 68M42 | B-13 | N | 0 | FW68M39 | FW68M43 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M42 | 08 | 32 | 3" | FW | 68M42 | B-13 | N | 0 | FW68M39 | FW68M43 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M49 | 08 | 32 | 1-1/2" | FW | 68M49 | B-13 | N | 0 | FW68M25 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68N04 | 08 | 32 | 1-1/2" | FW | 68N04 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N21 | 08 | 32 | 1-1/2" | FW | 68N21 | B-13 | N | 0 | FW68K05 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N21 | 08 | 32 | 3" | FW | 68N21 | B-13 | N | 0 | FW68K05 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N46 | 08 | 32 | 3" | FW | 68N46 | B-13 | N | 0 | FW68N51 | FW68K05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N47 | 08 | 32 | 1" | FW | 68N47 | B-13 | N | 0 | SWIVEL JOINT | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N49 | 08 | 32 | 1" | FW | 68N49 | B-13 | N | 0 | FW68N52 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N58 | 08 | 32 | 1" | FW | 68N58 | B-13 | N | 0 | FW68N34 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68O04 | 08 | 32 | 3" | FW | 68O04 | B-13 | N | 0 | FW68O05 | FW68O01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O14 | 08 | 32 | 4" | FW | 68O14 | B-13 | N | 0 | FW68C10 | HEADER | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68P01 | 08 | 32 | 2" | FW | 68P01 | B-13 | N | 0 | FW68P18 | FW68P18 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P04 | 08 | 32 | 4" | FW | 68P04 | B-13 | N | 0 | FW68K07 | FW68P05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P15 | 08 | 32 | 1" | FW | 68P15 | B-13 | N | 0 | FW68P14 | FW68P14 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68Q04 | 08 | 32 | 1-1/2" | FW | 68Q04 | B-13 | N | 0 | FW68Q06 | FW68Q02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q04 | 08 | 32 | 2" | FW | 68Q04 | B-13 | N | 0 | FW68Q06 | FW68Q02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68Q05 | 08 | 32 | 1-1/2" | FW | 68Q05 | B-13 | N | 0 | FW68Q02 | FW68Q02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
HCM23072 |  | 32 | 1" | HCM | 23072 | 3FS4 | HB | 30 | HCM24061 | HCM23075 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23080 | 08 | 32 | 1-1/2" | HCM | 23080 | C42S1 | N | 0 | PR24045 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM24025 |  | 32 | 3/4" | HCM | 24025 | D20S1 | P | 50 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24025 |  | 32 | 1-1/2" | HCM | 24025 | D20S1 | P | 50 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24025 |  | 32 | 2" | HCM | 24025 | D20S1 | P | 50 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24025 | 08 | 32 | 3" | HCM | 24025 | D20S1 | N | 0 | HCM24094 | BDL24088 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM24057 |  | 32 | 8" | HCM | 24057 | D20S1 | P | 75 | HCM24069 | P23027 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24077 |  | 32 | 8" | HCM | 24077 | D20S1 | P | 75 | 32-T-2400 | 32-E-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24095 | 08 | 32 | 3/4" | HCM | 24095 | D20S1 | P | 50 | HCM23065 | 32-R-2300 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.15A | 1 | III | MOD.G | Y | 1 | N | 32-P-044-01 |  | F | N | 141 | N | 530 | 15
HCM24095 | 08 | 32 | 1" | HCM | 24095 | D20S1 | P | 50 | HCM23065 | 32-R-2300 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.15A | 1 | III | MOD.G | Y | 1 | N | 32-P-044-01 |  | F | N | 141 | N | 530 | 15
HCM24097 |  | 32 | 3/4" | HCM | 24097 | D20S1 | P | 50 | 32-T-2400 | HCM24089 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24097 |  | 32 | 4" | HCM | 24097 | D20S1 | P | 50 | 32-T-2400 | HCM24089 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24097 |  | 32 | 8" | HCM | 24097 | D20S1 | P | 75 | 32-T-2400 | HCM24089 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM31018 |  | 32 | 4" | HCM | 31018 | C42S1 | HB | 30 | HCM31012 | 32-S-3101B | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31020 | 08 | 32 | 1/2" | HCM | 31020 | C42S1 | N | 0 | CD31005 | BDL31040 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31020 | 08 | 32 | 1" | HCM | 31020 | C42S1 | N | 0 | CD31005 | BDL31040 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM31022 |  | 32 | 4" | HCM | 31022 | C42S1 | HB | 30 | 32-S-3101A | BDL31038 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HN67024 | 08 | 32 | 1-1/2" | HN | 67024 | C6S1 | N | 0 | HN67013 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN71001 | 08 | 32 | 1-1/2" | HN | 71001 | C6S1 | N | 0 | NITROGEN CONNECTION | ET71039 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.49 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN72004 | 08 | 32 | 1-1/2" | HN | 72004 | C6S1 | N | 0 | 172C0-03 | PR72020 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.53 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN72005 | 08 | 32 | 1-1/2" | HN | 72005 | C6S1 | N | 0 | NITROGEN CONNECTION | PR01001 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.51 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 170
HN72011 | 08 | 32 | 1-1/2" | HN | 72011 | C6S1 | N | 0 | PR720105 | SP-04-172B1-03 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
HOS89002 | 08 | 32 | 3" | HOS | 89002 | C-2 | HA | 90 | TP-N60201 (32-E-8908AA) | TP-N42901 (32-S-8900A/B) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL SUPPLY | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 208
HOS89004 | 08 | 32 | 3" | HOS | 89004 | C-2 | HA | 90 | TP-N60203 (32-E-8908BA) | TP-N42501 (32-CPN-A408) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL SUPPLY | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 208
HOS89004 | 08 | 32 | 4" | HOS | 89004 | C-2 | HA | 90 | TP-N60203 (32-E-8908BA) | TP-N42501 (32-CPN-A408) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL SUPPLY | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 208
IW89034 | 08 | 32 | 3/4" | IW | 89034 | B-1 | N | 0 | IW89020 | US-3211-02 AT GRADE | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
JLS23018 |  | 32 | 1/2" | JLS | 23018 | B-5 | HB | 40 | LS63042 | LS23029 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS31008 | 08 | 32 | 3" | JLS | 31008 | B-5 | HB | 50 | LS31019 | JLS31006 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JWR14001 | 08 | 32 | 1" | JWR | 14001 | B-1 | N | 0 | 32-E-1451 | JWR14003 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.7 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR36003 | 08 | 32 | 2" | JWR | 36003 | B-1 | N | 0 | TP-148 (JWR360138) | JWR36001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR52002 | 08 | 32 | 1-1/2" | JWR | 52002 | B-1 | N | 0 | Seal Pot | VA52017 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JCW86011 |  | 32 | 1/2" | JCW | 86011 | B-1 | HB | 30 | JCW86012 | PX86018 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JCW86017 |  | 32 | 1/2" | JCW | 86017 | B-1 | HB | 30 | PX86025 | PX86002 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JLS13002 |  | 32 | 2" | JLS | 13002 | B-5 | HB | 50 | O13002 | O13026 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-025-01 |  | E | N | 000 | N | 105
JLS23013 |  | 32 | 3/4" | JLS | 23013 | B-5 | HB | 40 | LS63045 | LS23032 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23014 |  | 32 | 1/2" | JLS | 23014 | B-5 | HB | 40 | LS63045 | LS23023 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23014 |  | 32 | 1-1/2" | JLS | 23014 | B-5 | HB | 50 | LS63045 | LS23023 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23017 |  | 32 | 1/2" | JLS | 23017 | B-5 | HB | 40 | LS63044 | LS23031 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23017 |  | 32 | 1-1/2" | JLS | 23017 | B-5 | HB | 50 | LS63044 | LS23031 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS31009 |  | 32 | 1" | JLS | 31009 | B-5 | HB | 50 | PR31017 | PR31017 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JW43001 | 08 | 32 | 3" | JW | 43001 | B-1 | N | 0 | PR43033 | PR43035 | 9.0 | 175.0 | 7.0 | 80.0 |  | 13.53 | 29.4 | H | JACKET WATER | L | - | - | >1.5 | 80 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 88
JWR23002 | 08 | 32 | 3" | JWR | 23002 | B-1 | N | 0 | PJW23004 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11 | DELETED
JWR24003 | 08 | 32 | 3/4" | JWR | 24003 | B-1 | N | 0 | 32-E-2401 | JWR24001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.19 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
BDL24073 | 08 | 32 | 1" | BDL | 24073 | B32S1 | N | 0 | BDL21008 | BDL60035 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24083 | 08 | 32 | 3/4" | BDL | 24083 | B32S1 | N | 0 | PR22014 | BDL23055 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24084 | 08 | 32 | 3/4" | BDL | 24084 | B32S1 | N | 0 | BDL24061 | BDL24072 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31024 | 08 | 32 | 3/4" | BDL | 31024 | B32S1 | N | 0 | PR31015 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36027 | 08 | 32 | 2" | BDL | 36027 | B32S1 | N | 0 | TP-116,HCM360118 | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL40040 | 08 | 32 | 3/4" | BDL | 40040 | B32S1 | N | 0 | P40036 | BDL40043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.31 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
JWR64041 | 08 | 32 | 10" | JWR | 64041 | B-1 | N | 0 | JWR61002 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71002 | 08 | 32 | 3/4" | JWR | 71002 | C3S1 | N | 0 | 32-E-7102 | JWR71003 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
HCM32044 | 08 | 32 | 2" | HCM | 32044 | C42S1 | HB | 40 | HCM32030 | BDL32029, PSV-3280 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24G | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HD40006 | 08 | 32 | 3/4" | HD | 40006 | 3FS4 | N | 0 | N40007 | HCM40001 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.30 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
HN21005 | 08 | 32 | 1-1/2" | HN | 21005 | C6S1 | N | 0 | NITROGEN CONNECTION | BDH21005 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.12 | 2 | I | MOD.A | Y | 1 | N | 32-U-031-02 |  | E | N | 000 | N | 170
HN67008 | 08 | 32 | 3/4" | HN | 67008 | C6S1 | N | 0 | HN67007 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67016 | 08 | 32 | 3/4" | HN | 67016 | C6S1 | N | 0 | HN67002 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67026 | 08 | 32 | 3/4" | HN | 67026 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67026 | 08 | 32 | 1-1/2" | HN | 67026 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN72003 | 08 | 32 | 1-1/2" | HN | 72003 | C6S1 | N | 0 | 172C0-09 | PR72024 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.53 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN72009 | 08 | 32 | 1-1/2" | HN | 72009 | C6S1 | N | 0 | SP-04-172B1-06 | PR720105 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
FW68E28 | 08 | 32 | 6" | FW | 68E28 | B-7 | N | 0 | FW68E27 | FW68E26 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68G21 | 08 | 45 | 1" | FW | 68G21 | B-13 | N | 0 | FW68D07 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68G21 | 08 | 45 | 3" | FW | 68G21 | B-13 | N | 0 | FW68D07 | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-04 |  | - | Y | 000 | - | 74
FW68H18 | 08 | 32 | 1" | FW | 68H18 | B-13 | N | 0 | FW68H17 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H30 | 08 | 32 | 3" | FW | 68H30 | B-13 | N | 0 | FW68C07 | FW68H27 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H59 | 08 | 32 | 1" | FW | 68H59 | B-13 | N | 0 | FW68H58 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I02 | 08 | 32 | 1" | FW | 68I02 | B-13 | N | 0 | MSN-003 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I02 | 08 | 32 | 1-1/2" | FW | 68I02 | B-13 | N | 0 | MSN-003 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I02 | 08 | 32 | 3" | FW | 68I02 | B-13 | N | 0 | MSN-003 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68K05 | 08 | 32 | 3" | FW | 68K05 | B-13 | N | 0 | XV6806A | FW68N09 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68R13 | 08 | 45 | 3/4" | FW | 68R13 | B-13 | N | 0 | 45-XV-6822A | FW68R10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68I03 | 08 | 32 | 3" | FW | 68I03 | B-13 | N | 0 | MSN-003 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I19 | 08 | 32 | 1-1/2" | FW | 68I19 | B-13 | N | 0 | FW68I06 | FW68I01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I19 | 08 | 32 | 2" | FW | 68I19 | B-13 | N | 0 | FW68I06 | FW68I01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I39 | 08 | 32 | 1-1/2" | FW | 68I39 | B-13 | N | 0 | FW68I40 | FW68I40 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68L21 | 08 | 32 | 1-1/2" | FW | 68L21 | B-13 | N | 0 | FW68L02 | MSN-004 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68L21 | 08 | 32 | 3" | FW | 68L21 | B-13 | N | 0 | FW68L02 | MSN-004 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
WW61001 | 08 | 32 | 6" | WW | 61001 | B4S2 | N | 0 | CHWR61007 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.42 | 2 | I | MOD.A | Y | 1 | N | 32-U-023-02 |  | E | N | 000 | N | 87
WW91002 | 08 | 32 | 1/2" | WW | 91002 | B4S2 | N | 0 | 19-S-9014 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.105 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-082-06 |  | E | N | 000 | N | 87
WW92004 | 08 | 32 | 8" | WW | 92004 | B4S2 | N | 0 | 32-S-9005 | SCRAP CONTAINER | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.72 | 2 | I | MOD.A | Y | 1 | N | 32-P-082-08 |  | E | N | 000 | N | 87
JWS64002 | 08 | 32 | 3/4" | JWS | 64002 | B-1 | N | 0 | 32-E-6400B | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64002 | 08 | 32 | 1-1/2" | JWS | 64002 | B-1 | N | 0 | 32-E-6400B | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64002 | 08 | 32 | 20" | JWS | 64002 | B-1 | N | 0 | 32-E-6400B | JWS64004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64010 | 08 | 32 | 3/4" | JWS | 64010 | B-1 | N | 0 | 32-P-6400C | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64010 | 08 | 32 | 20" | JWS | 64010 | B-1 | N | 0 | 32-P-6400C | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWR43003 | 08 | 32 | 3/4" | JWR | 43003 | C3S1 | N | 0 | JWR43001 | VA43011 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWS24011 | 08 | 32 | 6" | JWS | 24011 | D20S1 | N | 0 | JWS64052 | 32-E-2403 | 49.0/49.0 | -45.0/150.0 | 5.0 | 30.0 |  | 73.51 | 128.56 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.20 | 2 | II | MOD.A2 | Y | 1 | Y | 32-U-022-01 |  | M | N | 000 | N | 1020
JWS52003 | 08 | 32 | 3/4" | JWS | 52003 | B-1 | N | 0 | JWS64059 | 32-E-5252A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS63004 | 08 | 32 | 1-1/2" | JWS | 63004 | B-1 | N | 0 | JWS64056 | JWS63003 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64030 | 08 | 32 | 3/4" | JWS | 64030 | B-1 | N | 0 | JWS64058 | E-5103 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JLS13001 |  | 32 | 3" | JLS | 13001 | B-5 | HB | 50 | O13003 | O13021 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-025-01 |  | E | N | 000 | N | 105
JLS31012 |  | 32 | 1-1/2" | JLS | 31012 | B-5 | HB | 50 | PR31024 | PR31018 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | E | N | 000 | N | 111 | 1
FW68A06 | 08 | 45 | 6" | FW | 68A06 | PEB-69 | N | 0 | FW68A03 | FW68A91 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A0B | 08 | 45 | 6" | FW | 68A0B | B-7 | N | 0 | FW68A0A | FW68A0X | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A0T | 08 | 45 | 6" | FW | 68A0T | UGB-1PE | N | 0 | FW68A11 | 45-HY-6805 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A37 | 08 | 45 | 6" | FW | 68A37 | PEB-69 | N | 0 | FW68A17 | FW68A0Q | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A65 | 08 | 45 | 16" | FW | 68A65 | PEB-69 | N | 0 | FW68A10 | FW68A0H | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A78 | 08 | 45 | 1-1/2" | FW | 68A78 | B-13 | N | 0 | FW68A26 | 45-HR-6858 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A89 | 08 | 45 | 1-1/2" | FW | 68A89 | B-7 | N | 0 | FW68A38 | 45-HR-6825 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A92 | 08 | 45 | 6" | FW | 68A92 | UGB-1PE | N | 0 | FW68A08 | 45-HY-6803 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0E | 08 | 45 | 6" | FW | 68B0E | UGB-1PE | N | 0 | FW68B08 | 45-HY-6814 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0O | 08 | 45 | 6" | FW | 68B0O | UGB-1PE | N | 0 | FW68B41 | 45-HY-6822 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0Z | 08 | 45 | 6" | FW | 68B0Z | UGB-1PE | N | 0 | 45-HY-6817 | FW68B59 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B69 | 08 | 45 | 18" | FW | 68B69 | PEB-69 | N | 0 | FW68A17 | FW68B70 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B87 | 08 | 45 | 6" | FW | 68B87 | PEB-69 | N | 0 | FW68A03 | FW68B0F | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B95 | 08 | 45 | 6" | FW | 68B95 | UGB-1PE | N | 0 | FW68B14 | FW68B15 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
LS6300G |  | 32 | 1" | LS | 6300G | B-5 | HB | 70 | LS01001 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300M |  | 32 | 1" | LS | 6300M | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300W |  | 32 | 2" | LS | 6300W | B-5 | HB | 80 | LS63201 | 32-1121-S-005 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AB |  | 32 | 2" | LS | 630AB | B-5 | HB | 80 | LS63206 | 32-1127-S-010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AD |  | 32 | 1-1/2" | LS | 630AD | B-5 | HB | 70 | LS63177 | 32-1115-S-012 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS630AL |  | 32 | 1-1/2" | LS | 630AL | B-5 | HB | 70 | LS63193 | JLS23010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63176 |  | 32 | 1" | LS | 63176 | B-5 | HB | 70 | LS63177 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63177 |  | 32 | 2" | LS | 63177 | B-5 | HB | 80 | LS01001 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63177 |  | 32 | 6" | LS | 63177 | B-5 | HB | 90 | LS01001 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63197 |  | 32 | 1-1/2" | LS | 63197 | B-5 | HB | 70 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
BDL23044 | 08 | 32 | 3/4" | BDL | 23044 | B32S1 | N | 0 | PR23032 | BDL31031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.17 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23066 | 08 | 32 | 1/2" | BDL | 23066 | B32S1 | N | 0 | 32-Z-2303A | BDL23065 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.15 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL24070 | 08 | 32 | 3/4" | BDL | 24070 | B32S1 | N | 0 | HCM24070 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.19 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL31025 | 08 | 32 | 2" | BDL | 31025 | B32S1 | N | 0 | PR24032 | BDL31031 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
PR23029 |  | 32 | 1-1/2" | PR | 23029 | D20S1 | ST | 30 | PR23032 | 32-D-2300 | 55.0/55.0 | -45.0/190.0 | 40.0/40.0 | 80.0/121.0 |  | 82.81 | 141.72 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | N | 141 | N | 334 | 10
PR24043 |  | 32 | 1/2" | PR | 24043 | D20S1 | HB | 30 | PR24042 | HCM23079 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24043 |  | 32 | 1-1/2" | PR | 24043 | D20S1 | HB | 30 | PR24042 | HCM23079 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24045 |  | 32 | 1" | PR | 24045 | D20S1 | HB | 30 | PR24044 | HCM23080 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR31015 |  | 32 | 3/4" | PR | 31015 | 1FS4 | JR | 0 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31015 | 7A | 32 | 1-1/2" | PR | 31015 | 1FS4 | HB | 30 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31015 | 08 | 32 | 1-1/2" | PR | 31015 | 1FS4 | N | 0 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31015 |  | 32 | 2" | PR | 31015 | 1FS4 | JR | 0 | PR22011 | PR40021 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR34019 |  | 32 | 3/4" | PR | 34019 | QXB26S1 | ET | 30 | N34007 | PR34028 | 8.0/8.0 | 200.0/-45.0 | 5.0 | 80.0 |  | 12.83 | 28.5 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-048-01 |  | G | N | 141 | N | 392 | 10
PR36023 | 08 | 32 | 1" | PR | 36023 | C42S1 | P | 50 | PR36038 | PR36022 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28A | 1 | Art 4.3 | NA | N | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR40025 |  | 32 | 1/2" | PR | 40025 | C42S1 | ST | 30 | PR40027 | VZ40006 | 30.0/30.0 | 150.0/-45.0 | 20.0 | 60.0 |  | 45 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 60 | sh.30 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 364 | 10
PR40033 |  | 32 | 4" | PR | 40033 | C42S1 | HB | 30 | PR40026 | BDL40036 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G | N | 141 | N | 359 | 10
PR43041 |  | 32 | 1/2" | PR | 43041 | C42S1 | HB | 30 | PR43038 | BDL43024 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR53004 | 08 | 32 | 3/4" | PR | 53004 | B4S1 | P | 50 | TP-002 (PR530113) | PR53005 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
PR53004 | 08 | 32 | 3" | PR | 53004 | B4S1 | P | 50 | TP-002 (PR530113) | PR53005 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
DW01001 | 08 | 32 | 3" | DW | 01001 | B-13 | N | 0 | DW220003 OSBL LINE | DW69B05 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.2 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69A03 | 08 | 32 | 2" | DW | 69A03 | B-13 | IS | 50 | DW01001 | 32-ES-6907 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B03 | 08 | 32 | 1-1/2" | DW | 69B03 | B-13 | N | 0 | DW69B02 | 32-ES-6911 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B15 | 08 | 32 | 1-1/2" | DW | 69B15 | B-13 | IS | 50 | DW69B12 | 32-ES-6909 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
FW68A03 | 08 | 45 | 20" | FW | 68A03 | PEB-69 | N | 0 | FW68A10 | FW68A10 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A0O | 08 | 45 | 6" | FW | 68A0O | UGB-1PE | N | 0 | FW68A44 | 45-HM-6807 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0U | 08 | 45 | 6" | FW | 68A0U | UGB-1PE | N | 0 | FW68A13 | 45-HY-6806 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A18 | 08 | 45 | 16" | FW | 68A18 | PEB-69 | N | 0 | FW68A20 | FW68A96 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A25 | 08 | 45 | 8" | FW | 68A25 | PEB-69 | N | 0 | FW68A20 | FW68A98 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A47 | 08 | 45 | 6" | FW | 68A47 | PEB-69 | N | 0 | FW68A46 | FW68A0K | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
PW51012 | 08 | 32 | 1" | PW | 51012 | B4S1 | N | 0 | 32-D-5101 | COLLECTIVE SPILL DRUM | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51012 | 08 | 32 | 1-1/2" | PW | 51012 | B4S1 | N | 0 | 32-D-5101 | COLLECTIVE SPILL DRUM | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51019 | 08 | 32 | 1" | PW | 51019 | B4S1 | N | 0 | TP-N9 (PW510119) | PW51018 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-03 |  | E | N | 110 | N | 82
PX86019 | 08 | 32 | 1/2" | PX | 86019 | QXC25S1 | N | 0 | PX86024 | PX86037 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86020 | 08 | 32 | 1/2" | PX | 86020 | QXC25S1 | N | 0 | PX86021 | PX86002 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86024 | 08 | 32 | 1/2" | PX | 86024 | QXC25S1 | N | 0 | PX86025 | PX86020 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
FW68Q11 | 08 | 32 | 1" | FW | 68Q11 | B-13 | N | 0 | FW68Q10 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68R15 | 08 | 45 | 1/2" | FW | 68R15 | B-7 | N | 0 | FW68R07 | 45-XV-6824A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R18 | 08 | 45 | 3/4" | FW | 68R18 | B-13 | N | 0 | 45-XV-6819A | FW68R10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
HCM32024 |  | 32 | 3/4" | HCM | 32024 | C42S1 | HB | 30 | 32-D-3200 | TP-01A (32-D-3201A) | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32024 |  | 32 | 4" | HCM | 32024 | C42S1 | HB | 30 | 32-D-3200 | TP-01A (32-D-3201A) | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32043 | 08 | 32 | 2" | HCM | 32043 | C42S1 | HB | 30 | TP-05B (32-D-3202B) | HCM32032 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24G | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HD22005 | 08 | 32 | 3/4" | HD | 22005 | 3FS4 | N | 0 | HD01002 | HD40006 | 45.0 | 80.0 | 40.0 | 32.0 |  | 67.5 | 148.95 | H | HYDROGEN | G | - | - | >1.5 | 32 | sh.13 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-002-01 |  | F | Y | 040 | N | 291 | 5,23,10,25,36
PR72006 | 08 | 32 | 3/4" | PR | 72006 | C42S1 | N | 0 | 32-D-7201 | PW72007 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR34020 |  | 32 | 1-1/2" | PR | 34020 | B4S1 | ET | 50 | PR34021 | 32-D-3400 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34022 |  | 32 | 3/4" | PR | 34022 | B4S1 | P | 50 | 32-S-3401A | 32-E-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34022 |  | 32 | 10" | PR | 34022 | B4S1 | P | 100 | 32-S-3401A | 32-E-3500 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34025 |  | 32 | 1-1/2" | PR | 34025 | B4S1 | P | 50 | 32-S-3401B | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01,32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35015 | 08 | 32 | 1" | PR | 35015 | B4S1 | N | 0 | 32-D-3500 | BDL35009 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35015 | 08 | 32 | 6" | PR | 35015 | B4S1 | N | 0 | 32-D-3500 | BDL35009 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.27 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR35016 | 08 | 32 | 1/2" | PR | 35016 | B4S2 | N | 0 | 32-P-3501 | PR35017 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35016 | 08 | 32 | 1" | PR | 35016 | B4S2 | N | 0 | 32-P-3501 | PR35017 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35018 | 08 | 32 | 1-1/2" | PR | 35018 | B4S2 | N | 0 | PR35017 | PR35020 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35020 | 08 | 32 | 1/2" | PR | 35020 | B4S2 | N | 0 | PR35021 | 32-P-3501 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR35020 | 08 | 32 | 1-1/2" | PR | 35020 | B4S2 | N | 0 | PR35021 | 32-P-3501 | 6.0 | 120.0 | 2.0 | 60.0 |  | 9 | 29.4 | H | PROPYLENE | L | - | - | >1.5 | 60 | sh.27 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-02 |  | D | N | 141 | N | 372 | 15
PR36009 |  | 32 | 1-1/2" | PR | 36009 | C42S1 | HB | 30 | PR36013 | PR34021 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36026 | 08 | 32 | 10" | PR | 36026 | B4S1 | N | 0 | TP-100, 32-D-3601, 32-FO-3651 | 32-PDT-3651 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28A | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-048-03 |  | C | Y | 141 | N | 397 | ,10
PR40021 |  | 32 | 3/4" | PR | 40021 | D20S1 | ST | 30 | PR31015 | PR40029 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-048-01 |  | F | N | 141 | N | 330 | 15
PR40021 |  | 32 | 1-1/2" | PR | 40021 | D20S1 | ST | 30 | PR31015 | PR40029 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-048-01 |  | F | N | 141 | N | 330 | 15
PR40023 |  | 32 | 2" | PR | 40023 | C42S1 | ST | 30 | PR40027 | 32-R-4001 | 30.0/30.0 | 150.0/-45.0 | 20.0 | 60.0 |  | 45 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 60 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 364 | 10
VG89002 | 08 | 32 | 24" | VG | 89002 | B-1 | N | 0 | VG89001 | VENT TO ATMOSPHERE | 0.25 | 110.0 | 0.015 | 40.0 |  | .28 | 26.46 | P | PROCESS VENT/EQUALIZ.LINE | G | - | - | >1.5 | 40 | sh.68M | 1 | NA | NA | NA | 1 | N | 32-P-082-09 |  | E | N | 010 | N | 3282
JWR24003 | 08 | 32 | 1" | JWR | 24003 | B-1 | N | 0 | 32-E-2401 | JWR24001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.19 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR24003 | 08 | 32 | 20" | JWR | 24003 | B-1 | N | 0 | 32-E-2401 | JWR24001 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.19 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
VA50008 | 08 | 32 | 8" | VA | 50008 | B4S2 | N | 0 | LS50002 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.34 | 2 | NA | NA | NA | 6 | N | 32-P-050-01 |  | E | N | 000 | N | 183
VA64002 | 08 | 32 | 1" | VA | 64002 | B4S2 | N | 0 | CWR64013 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.44 | 2 | NA | NA | NA | 6 | N | 32-U-021-01 |  | E | N | 000 | N | 183
VA64005 | 08 | 32 | 1" | VA | 64005 | B4S2 | N | 0 | JWS64002 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.44 | 2 | NA | NA | NA | 6 | N | 32-U-022-01 |  | E | N | 000 | N | 183
VA65001 | 08 | 32 | 1" | VA | 65001 | B4S2 | N | 0 | CHWR65003 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.45 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA71007 | 08 | 32 | 2" | VA | 71007 | B4S2 | N | 0 | BDL71033 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.48 | 2 | NA | NA | NA | 6 | N | 32-U-031-03 |  | E | N | 000 | N | 183
VA71007 | 08 | 32 | 3" | VA | 71007 | B4S2 | N | 0 | BDL71033 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.48 | 2 | NA | NA | NA | 6 | N | 32-U-031-03 |  | E | N | 000 | N | 183
VA88002 | 08 | 32 | 8" | VA | 88002 | B-1 | N | 0 | 32-D-8007 | VG89001 | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.67 | 2 | NA | NA | NA | 1 | N | 32-P-082-09 |  | E | N | 000 | N | 181
BDL71036 | 08 | 32 | 2" | BDL | 71036 | B4S1 | N | 0 | ET71064 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL72066 | 08 | 32 | 1/2" | BDL | 72066 | B32S1 | N | 0 | TP-025 (PR720167) | BDL72060 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
CHWS14014 |  | 32 | 1-1/2" | CHWS | 14014 | B-1 | HA | 30 | 32-E-1400B | 32-D-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS14014 |  | 32 | 4" | CHWS | 14014 | B-1 | HA | 30 | 32-E-1400B | 32-D-1400B | 9.0 | 190.0 | 5.0/5.0 | 5.0/60.0 |  | 13.55 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | >1.5 | 5 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 52
CHWS61028 |  | 32 | 2" | CHWS | 61028 | B-1 | CF | 25 | CHWS61002 | CHWS61003 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CO26025 | 08 | 32 | 1" | CO | 26025 | 1IS5 | N | 0 | CO26033 | CO26026 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO31001 | 08 | 32 | 3/4" | CO | 31001 | 1IS5 | N | 0 | CO31002 | CO2819 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO31002 | 08 | 32 | 3/4" | CO | 31002 | 1IS5 | N | 0 | EMERGENCY KILLER SYSTEM CO 10% IN NITROGEN | CO31001 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CT14010 |  | 32 | 1" | CT | 14010 | 3FS3 | CF | 25 | VZ14012 | CT14002 | 70.0 | 80.0 | 50.0 | 6.0 |  | 105 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.7 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | M | N | 232 | N | 286 | 23,29,25
IA01001 | 08 | 32 | 3/4" | IA | 01001 | B-13 | N | 0 | IA300003 OSBL LINE | IA62092 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.2 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA40001 | 08 | 32 | 1" | IA | 40001 | B-13 | N | 0 | CWR89010 | TO C-4001 COMPRESSOR AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62016 | 08 | 32 | 1" | IA | 62016 | B-13 | N | 0 | IA62001 | TO REFRIGERATION UNIT C-6100 AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA02011 | 08 | 32 | 1" | IA | 02011 | B-13 | N | 0 | IA02002 | 100 LITERS AIR TANK | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.68M | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62080 | 08 | 32 | 1-1/2" | IA | 62080 | B-13 | N | 0 | IA62089 | 32-IAM-011 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
FW68L28 | 08 | 32 | 1-1/2" | FW | 68L28 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68M23 | 08 | 32 | 2" | FW | 68M23 | B-13 | N | 0 | FW68M25 | FW68M24 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M37 | 08 | 32 | 1" | FW | 68M37 | B-13 | N | 0 | FW68M08 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M45 | 08 | 32 | 1" | FW | 68M45 | B-13 | N | 0 | FW68M05 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68N38 | 08 | 32 | 1" | FW | 68N38 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N57 | 08 | 32 | 1" | FW | 68N57 | B-13 | N | 0 | FW68N34 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68P09 | 08 | 32 | 4" | FW | 68P09 | B-13 | N | 0 | FW68K07 | FW68P10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68Q06 | 08 | 32 | 3" | FW | 68Q06 | B-13 | N | 0 | FW68Q02 | FW68C09 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68R03 | 08 | 45 | 1/2" | FW | 68R03 | B-7 | N | 0 | FW68R07 | 45-XV-6820A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R03 | 08 | 45 | 4" | FW | 68R03 | B-7 | N | 0 | FW68R07 | 45-XV-6820A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
JWS64027 | 08 | 32 | 4" | JWS | 64027 | B-1 | N | 0 | JWS64054 | JWS43001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64060 | 08 | 32 | 3/4" | JWS | 64060 | B-1 | N | 0 | 32-P-6400A | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64060 | 08 | 32 | 20" | JWS | 64060 | B-1 | N | 0 | 32-P-6400A | JWS64008 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64069 | 08 | 32 | 3/4" | JWS | 64069 | B-1 | N | 0 | JWS64056 | 32-Z-7300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS71001 | 08 | 32 | 2" | JWS | 71001 | C3S1 | N | 0 | JWS64033 | 32-E-7102 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS71001 | 08 | 32 | 3" | JWS | 71001 | C3S1 | N | 0 | JWS64033 | 32-E-7102 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS72003 | 08 | 32 | 3/4" | JWS | 72003 | D20S1 | N | 0 | JWS64018 | 32-E-7203 | 33.7/33.7 | 245.0/-45.0 | 5.0 | 30.0 |  | 52.54 | 150.8 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-022-01 |  | M | N | 141 | N | 1030
JWS72004 | 08 | 32 | 3/4" | JWS | 72004 | C42S1 | N | 0 | JWS64017 | 32-E-7200 | 33.7/33.7 | 150.0/-45.0 | 3.0 | 30.0 |  | 50.56 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-U-022-01 |  | M | N | 141 | N | 1032
JWS72004 | 08 | 32 | 6" | JWS | 72004 | C42S1 | N | 0 | JWS64017 | 32-E-7200 | 33.7/33.7 | 150.0/-45.0 | 3.0 | 30.0 |  | 50.56 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-U-022-01 |  | M | N | 141 | N | 1032
LA16002 |  | 32 | 1-1/2" | LA | 16002 | 4CS2 | HH | 30 | 32-D-1600 | LA16022 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16004 |  | 32 | 3/4" | LA | 16004 | 4CS2 | EH | 30 | 32-S-1601 | LA16021 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16004 |  | 32 | 1" | LA | 16004 | 4CS2 | EH | 30 | 32-S-1601 | LA16021 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16014 |  | 32 | 1" | LA | 16014 | 4CS2 | EH | 30 | 32-D-1601 | 32-D-1600 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16014 |  | 32 | 1-1/2" | LA | 16014 | 4CS2 | EH | 30 | 32-D-1601 | 32-D-1600 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
JWR61002 | 08 | 32 | 8" | JWR | 61002 | B-1 | N | 0 | JWR61001 | JWR64041 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64006 | 08 | 32 | 20" | JWR | 64006 | UGB-1PE | N | 0 | JWR64042 | JWR64005 | 9.0 | 80.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-022-02 |  | E | N | 000 | N | 19
JWR73001 | 08 | 32 | 1" | JWR | 73001 | B-1 | N | 0 | JW73001 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.55 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWS64054 | 08 | 32 | 12" | JWS | 64054 | B-1 | N | 0 | JWS64008 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64054 | 08 | 32 | 20" | JWS | 64054 | B-1 | N | 0 | JWS64008 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64076 | 08 | 32 | 3/4" | JWS | 64076 | B-1 | N | 0 | JWS64054 | 32-E-1450A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-023-01 |  | E | N | 000 | N | 10
LA16013 |  | 32 | 1/2" | LA | 16013 | 4CS2 | ET | 30 | LA16012 | 32-D-1601 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA84036 |  | 32 | 1" | LA | 84036 | 4CS2 | ET | 30 | LA84035 | LA84011 | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
FW68C11 | 08 | 32 | 3/4" | FW | 68C11 | B-13 | N | 0 | FW68C12 | WATER ALARM GONG | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68E04 | 08 | 32 | 2" | FW | 68E04 | B-7 | N | 0 | FW68E41 | FW68E03 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
LS52005 |  | 32 | 1" | LS | 52005 | B-5 | HB | 30 | LS50036 | 32-H-5201 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-052-03 |  | E | N | 000 | N | 92
LS52006 |  | 32 | 1/2" | LS | 52006 | B-5 | HB | 30 | 32-D-5200 | LC52003 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS52008 |  | 32 | 3/4" | LS | 52008 | B-5 | HB | 60 | 32-E-5200 | LC52002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.37 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS52008 |  | 32 | 1-1/2" | LS | 52008 | B-5 | HB | 70 | 32-E-5200 | LC52002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.37 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS60020 |  | 32 | 1" | LS | 60020 | B-5 | HB | 70 | PURGE CONNECTION | BDL60050 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60029 |  | 32 | 1" | LS | 60029 | B-5 | HB | 70 | HOSE CONNECTION | BDL60059 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS6300C |  | 32 | 1" | LS | 6300C | B-5 | HB | 70 | LS6300A | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63019 |  | 32 | 1" | LS | 63019 | B-5 | HB | 70 | LS63013 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63075 |  | 32 | 1" | LS | 63075 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63090 |  | 32 | 1" | LS | 63090 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N01009 | 08 | 32 | 2" | N | 01009 | B-1 | N | 0 | N01001 | N6700G | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N13004 | 08 | 32 | 1/2" | N | 13004 | B-1 | N | 0 | N67032 | N13001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.6 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N14021 | 08 | 32 | 1" | N | 14021 | 1CS2 | N | 0 | N67034 | N14022 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.8 | 2 | NA | NA | NA | 5 | N | 32-P-026-02 |  | M | N | 000 | N | 154
N16001 | 08 | 32 | 1/2" | N | 16001 | 1CS2 | N | 0 | N67036 | N16011 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.10 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N31004 | 08 | 32 | 1" | N | 31004 | B-1 | N | 0 | NITROGEN CONNECTION | PR31022 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N32005 | 08 | 32 | 1-1/2" | N | 32005 | B4S1 | N | 0 | TP-26A, (CYLINDER) | N32004 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32019 | 08 | 32 | 1" | N | 32019 | B4S1 | N | 0 | N32020 | TP-27B, CYLINDER 1 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
BDL32036 | 08 | 32 | 2" | BDL | 32036 | B32S1 | N | 0 | TP-02B (32-D-3201B) | BDL32029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24G | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL33013 | 08 | 32 | 1" | BDL | 33013 | B32S1 | N | 0 | BDL33009 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL34016 | 08 | 32 | 3" | BDL | 34016 | B4S1 | N | 0 | BDL34017 | BDL60037 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL37004 | 08 | 32 | 1/2" | BDL | 37004 | B32S1 | N | 0 | 32-Z-3300B | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.29 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL43026 | 08 | 32 | 3/4" | BDL | 43026 | B32S1 | N | 0 | PR43050 | BDL34016 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.33 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL50003 | 08 | 32 | 3/4" | BDL | 50003 | B4S1 | N | 0 | PR50012 | BDL50002 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.35 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
PR72023 | 08 | 32 | 6" | PR | 72023 | C42S1 | N | 0 | PR72020 | PR72002 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72048 | 08 | 32 | 1" | PR | 72048 | C42S1 | N | 0 | 32-S-7201B | BDL72048 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72062 | 08 | 32 | 1/2" | PR | 72062 | C42S1 | N | 0 | PR72020 | BDL72037 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PW50019 |  | 32 | 1/2" | PW | 50019 | B4S2 | HB | 30 | 32-D-5002 | PW50020 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50019 |  | 32 | 2" | PW | 50019 | B4S2 | HB | 30 | 32-D-5002 | PW50020 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW52019 | 08 | 32 | 6" | PW | 52019 | B4S2 | N | 0 | 32-T-5200 | ACW | 0.7 | 100.0 | 0.1 | 55.0 |  | 1.05 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 55 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 83
PW72007 | 08 | 32 | 2" | PW | 72007 | B4S2 | N | 0 | PR72006 | ACW | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.51 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 30
PX86021 | 08 | 32 | 1/2" | PX | 86021 | QXC25S1 | N | 0 | 32-P-8600A | 32-Z-8600A | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86021 |  | 32 | 3/4" | PX | 86021 | QXC25S1 | JP | 0 | 32-P-8600A | 32-Z-8600A | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86031 | 08 | 32 | 1/2" | PX | 86031 | QXC25S1 | N | 0 | PX86030 | 32-P-8600B | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
TEA11001 | 08 | 32 | 1" | TEA | 11001 | 3DS3 | N | 0 | 32-D-1100 | 32-S-1100 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
ET71035 | 08 | 32 | 1-1/2" | ET | 71035 | D1S1 | N | 0 | ET710135 | ET71036 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 153.15 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 325 | ,10
ET71081 | 08 | 32 | 1/2" | ET | 71081 | C3S1 | N | 0 | ET71051 | BDL71031 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-006-02 |  | C | N | 041 | N | 323 | ,10
VA86002 | 08 | 32 | 2" | VA | 86002 | B4S2 | N | 0 | CWR86021 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.65 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
PX86026 |  | 32 | 1" | PX | 86026 | QXC25S1 | JP | 0 | PX86027 | PX86025 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86032 | 08 | 32 | 3/4" | PX | 86032 | QXC25S1 | N | 0 | 32-D-8600 | PX86030 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86037 |  | 32 | 1/2" | PX | 86037 | QXC25S1 | JP | 0 | PX86019 | PX86002 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
SA81013 | 08 | 32 | 6" | SA | 81013 | 1CS2 | N | 0 | 32-PK-8102 | 32-ZF-8108 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.61 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-03 |  | G | N | 200 | N | 406 | 6,10,23,25
SL21002 | 08 | 32 | 1" | SL | 21002 | 2FS4 | N | 0 | 32-R-2100 | BDH21004 | 50.0/50.0 | -40.0/200.0 | 37.0 | 20.0 |  | 80.16 | 148.95 | H | SLURRY | S | - | - | <1.5 | 20 | sh.12 | 2 | I | MOD.A | Y | NR | N | 32-P-042-01 |  | H-1 | N | 110 | N | 411 | 12,15,6,17
SWW92002 | 08 | 32 | 1/2" | SWW | 92002 | 1CS2 | N | 0 | DRAIN | BLIND FLANGE | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92002 | 08 | 32 | 1" | SWW | 92002 | 1CS2 | N | 0 | DRAIN | BLIND FLANGE | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92002 | 08 | 32 | 3" | SWW | 92002 | 1CS2 | N | 0 | DRAIN | BLIND FLANGE | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92005 | 08 | 32 | 1" | SWW | 92005 | 1CS2 | N | 0 | 32-P-9005 | HEADER | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92005 | 08 | 32 | 1-1/2" | SWW | 92005 | 1CS2 | N | 0 | 32-P-9005 | HEADER | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92005 | 08 | 32 | 3" | SWW | 92005 | 1CS2 | N | 0 | 32-P-9005 | HEADER | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
O13021 |  | 32 | 1/2" | O | 13021 | 1CS2 | ST | 30 | JLS13001 | 32-P-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13021 |  | 32 | 1" | O | 13021 | 1CS2 | ST | 30 | JLS13001 | 32-P-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13021 |  | 32 | 1-1/2" | O | 13021 | 1CS2 | ST | 30 | JLS13001 | 32-P-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13026 |  | 32 | 1-1/2" | O | 13026 | 1CS2 | ST | 30 | O13002 | 32-D-1300 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13037 |  | 32 | 3/4" | O | 13037 | B4S2 | ET | 30 | OIL DRUM | 32-P-1301 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O13037 |  | 32 | 1-1/2" | O | 13037 | B4S2 | ET | 30 | OIL DRUM | 32-P-1301 | 6.0 | 180.0 | 2.0 | 40.0 |  | 9.03 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 227 | 23,25
O15006 |  | 32 | 3/4" | O | 15006 | 1FS4 | ET | 30 | O15020 | 32-P-1501B | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15020 |  | 32 | 1" | O | 15020 | 1FS4 | ET | 30 | O15019 | O15006 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15025 |  | 32 | 1/2" | O | 15025 | 1FS4 | ET | 30 | 32-P-1501B | O15019 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O20002 |  | 32 | 3/4" | O | 20002 | 1FS4 | ET | 30 | O15008 | 32-Z-2005 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-042-01 |  | M | N | 110 | N | 245 | 23,25
O20008 | 08 | 32 | 1/2" | O | 20008 | 1FS4 | N | 0 | 32-Z-2001A | BDL20002 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O21007 |  | 32 | 3/4" | O | 21007 | 1FS4 | ET | 30 | O15009 | TP-8 (Z-2012, FO-2106) | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O65002 |  | 32 | 1-1/2" | O | 65002 | B4S2 | ET | 30 | O65010 | WASTE OIL DRUM | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 221
O66001 |  | 32 | 3/4" | O | 66001 | B4S2 | ET | 30 | 32-D-6600 | O66022 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66001 |  | 32 | 2" | O | 66001 | B4S2 | ET | 30 | 32-D-6600 | O66022 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66011 |  | 32 | 2" | O | 66011 | B4S2 | HH | 30 | 32-P-6601 | O66024 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66019 |  | 32 | 3/4" | O | 66019 | 1CS2 | ET | 30 | 32-P-6600 | 32-S-6601 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
O66019 |  | 32 | 1-1/2" | O | 66019 | 1CS2 | ET | 30 | 32-P-6600 | 32-S-6601 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.46 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-03 |  | M | N | 110 | N | 235 | 23,25
PR72006 | 08 | 32 | 2" | PR | 72006 | C42S1 | N | 0 | 32-D-7201 | PW72007 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72009 | 08 | 32 | 1" | PR | 72009 | C42S1 | N | 0 | 32-D-7200 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72009 | 08 | 32 | 6" | PR | 72009 | C42S1 | N | 0 | 32-D-7200 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72015 | 08 | 32 | 1/2" | PR | 72015 | C42S1 | N | 0 | 32-E-7203 | 32-T-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72015 | 08 | 32 | 3/4" | PR | 72015 | C42S1 | N | 0 | 32-E-7203 | 32-T-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72015 | 08 | 32 | 3" | PR | 72015 | C42S1 | N | 0 | 32-E-7203 | 32-T-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72018 | 08 | 32 | 3/4" | PR | 72018 | C42S1 | N | 0 | PR72028 | BDL72024 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72018 | 08 | 32 | 1-1/2" | PR | 72018 | C42S1 | N | 0 | PR72028 | BDL72024 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72018 | 08 | 32 | 3" | PR | 72018 | C42S1 | N | 0 | PR72028 | BDL72024 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72020 | 08 | 32 | 1" | PR | 72020 | C42S1 | N | 0 | TP-014 (PR720106) | 32-S-7201A | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52D | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72020 | 08 | 32 | 6" | PR | 72020 | C42S1 | N | 0 | TP-014 (PR720106) | 32-S-7201A | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52D | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72022 | 08 | 32 | 3/4" | PR | 72022 | C42S1 | N | 0 | 32-T-7203 | TP-014 (PR720101) | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72022 | 08 | 32 | 3" | PR | 72022 | C42S1 | N | 0 | 32-T-7203 | TP-014 (PR720101) | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72022 | 08 | 32 | 6" | PR | 72022 | C42S1 | N | 0 | 32-T-7203 | TP-014 (PR720101) | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72024 | 08 | 32 | 6" | PR | 72024 | C42S1 | N | 0 | PR72020 | 32-S-7201B | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 347 | ,15
PR72037 | 08 | 32 | 2" | PR | 72037 | C42S1 | N | 0 | PR72017 | BDL72032 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR43024 | 08 | 32 | 3/4" | PR | 43024 | C42S1 | N | 0 | PR43035 | HCM43001 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43024 | 08 | 32 | 1" | PR | 43024 | C42S1 | N | 0 | PR43035 | HCM43001 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43028 |  | 32 | 3/4" | PR | 43028 | C42S1 | ST | 30 | PR43045 | OG43001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43028 |  | 32 | 2" | PR | 43028 | C42S1 | ST | 30 | PR43045 | OG43001 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43030 | 08 | 32 | 3" | PR | 43030 | C42S1 | N | 0 | 32-E-4301 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43032 | 08 | 32 | 2" | PR | 43032 | C42S1 | N | 0 | PR43031 | 32-T-4300 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43033 | 08 | 32 | 1-1/2" | PR | 43033 | C42S1 | N | 0 | PR43031 | PR43035 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | A | N | 141 | N | 354 | 15
PR43035 | 08 | 32 | 3/4" | PR | 43035 | C42S1 | N | 0 | PR43033 | PR43024 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43035 | 08 | 32 | 1-1/2" | PR | 43035 | C42S1 | N | 0 | PR43033 | PR43024 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43050 |  | 32 | 3/4" | PR | 43050 | C42S1 | HB | 30 | PR43045 | BDL43026 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43050 |  | 32 | 2" | PR | 43050 | C42S1 | HB | 30 | PR43045 | BDL43026 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43051 |  | 32 | 1/2" | PR | 43051 | C42S1 | HB | 30 | PR43027 | BDL43017 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR50010 |  | 32 | 12" | PR | 50010 | B4S1 | P | 100 | P50013 | 32-T-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
PR50010 |  | 32 | 1" | PR | 50010 | B4S1 | P | 50 | P50013 | 32-T-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 7.53 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 375 | ,10
PR50011 | 08 | 32 | 1" | PR | 50011 | B4S1 | N | 0 | 32-T-5001 | TP-N1 (PR510101) | 5.0/-1.0 | 180.0/180.0 | 0.2 | 40.0 |  | 7.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.35 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 373 | ,10
PR50011 | 08 | 32 | 6" | PR | 50011 | B4S1 | N | 0 | 32-T-5001 | TP-N1 (PR510101) | 5.0/-1.0 | 180.0/180.0 | 0.2 | 40.0 |  | 7.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.35 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 373 | ,10
PR51015 | 08 | 32 | 1-1/2" | PR | 51015 | B4S1 | ST | 30 | TP-N2 (PR510110) | TP-001, PR530101 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | I | MOD.A | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR51015 | 08 | 32 | 4" | PR | 51015 | B4S1 | ST | 30 | TP-N2 (PR510110) | TP-001, PR530101 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | I | MOD.A | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
HCM23062 |  | 32 | 1/2" | HCM | 23062 | 1FS4 | JP | 0 | HCM23061 | HCM23070 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23063 |  | 32 | 1/2" | HCM | 23063 | 1FS4 | JP | 0 | JLS23011 | HCM23082 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23063 | 08 | 32 | 1/2" | HCM | 23063 | 1FS4 | N | 0 | JLS23011 | HCM23082 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM32037 | 08 | 32 | 1" | HCM | 32037 | C42S1 | HB | 30 | TP-03A (32-D-3201A) | HCM32031 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HN67015 | 08 | 32 | 3/4" | HN | 67015 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67018 | 08 | 32 | 3/4" | HN | 67018 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67018 | 08 | 32 | 1-1/2" | HN | 67018 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
IA62083 | 08 | 32 | 1/2" | IA | 62083 | B-13 | N | 0 | IA62089 | 32-IAM-026 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620AA | 08 | 32 | 3/4" | IA | 620AA | B-13 | N | 0 | IA62077 | 32-IAT-140 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AX | 08 | 32 | 3/4" | IA | 620AX | B-13 | N | 0 | IA62085 | 32-IAT-137 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA68D01 | 08 | 45 | 1" | IA | 68D01 | B-13 | N | 0 | IA68D05 | IA68D06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68F02 | 08 | 32 | 1/2" | IA | 68F02 | B-13 | N | 0 | IA68R10 | IA68F03 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | N | 000 | - | 200
IA68F07 | 08 | 32 | 1/2" | IA | 68F07 | B-13 | N | 0 | IA68R03 | SFP-001 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-14 |  | - | N | 000 | - | 200
DMW50002 | 08 | 32 | 1/2" | DMW | 50002 | SXB-48 | N | 0 | DMW50001 | LS50003 | 9.0 | 50.0 | 6.5 | 35.0 |  | 13.5 | 28.5 | H | DEMINERALIZED WATER | L | - | - | <1.5 | 35 | sh.34 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-050-01 |  | M | N | 000 | N | 26
DO12012 | 08 | 32 | 1/2" | DO | 12012 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12012 | 08 | 32 | 1" | DO | 12012 | 1CS2 | N | 0 | N12020 | DO12010 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DO12014 |  | 32 | 1" | DO | 12014 | 1CS2 | ET | 30 | 32-S-1200B | DO12022 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12037 | 08 | 32 | 1/2" | DO | 12037 | 1CS2 | N | 0 | DO12035 | DO12034 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DW69B02 | 08 | 32 | 2" | DW | 69B02 | B-13 | N | 0 | DW01001 | DW69B01 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
FW68Z01 | 08 | 45 | 1" | FW | 68Z01 | B-13 | N | 0 | DELUGE VALVE | WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | Y | 000 | - | 74
HCM22003 |  | 32 | 1/2" | HCM | 22003 | D20S1 | P | 50 | PR33019 | P23027 | 55.0/55.0 | -45.0/150.0 | 42.0/42.0 | 50.0/73.0 |  | 82.51 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 50 | sh.13 | 1 | III | MOD.G | Y | 1 | N | 32-P-044-01 |  | F | N | 141 | N | 328 | 15
HCM23061 | 08 | 32 | 1/2" | HCM | 23061 | 1FS4 | N | 0 | HCM23057 | HCM23066 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23064 |  | 32 | 1/2" | HCM | 23064 | 1FS4 | JP | 0 | HCM23063 | VZ23003 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23067 |  | 32 | 1/2" | HCM | 23067 | 1FS4 | JP | 0 | JLS23016 | LS23024 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23067 |  | 32 | 3/4" | HCM | 23067 | 1FS4 | JP | 0 | JLS23016 | LS23024 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.14 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23084 |  | 32 | 1/2" | HCM | 23084 | 1FS4 | JP | 0 | HCM23082 | HCM23087 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
LA16019 |  | 32 | 3/4" | LA | 16019 | 1FS4 | ET | 30 | 32-P-1600B | 32-S-1600 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA23005 |  | 32 | 1/2" | LA | 23005 | 1FS4 | ET | 30 | LA23006 | P23022 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.16 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA84032 |  | 32 | 1-1/2" | LA | 84032 | 4CS2 | ET | 30 | LA84011 | 32-P-8402B | 0.01 | 50.0 | 0.0 | 25.0 |  | .02 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | NA | NA | NA | NR | N | 32-P-062-02 |  | M | N | 210 | N | 601
LA84034 |  | 32 | 1" | LA | 84034 | 4CS2 | ET | 30 | LA84033 | LA84012 | 6.0 | 190.0 | 3.87/0.0 | 25.0/25.0 |  | 9.49 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | NR | N | 32-P-062-02 |  | M | N | 210 | N | 602
LA84041 |  | 32 | 1" | LA | 84041 | 4CS2 | ET | 30 | 32-S-8402B | LA84008 | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LC21001 |  | 32 | 3/4" | LC | 21001 | B-5 | HB | 30 | LS21001 | WW21001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23020 |  | 32 | 1/2" | LC | 23020 | B-5 | HB | 30 | LS23021 | LC23019 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23059 |  | 32 | 1" | LC | 23059 | B-5 | P | 50 | LS23040 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC24011 |  | 32 | 1" | LC | 24011 | B-5 | HB | 40 | LS24014 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC14001 |  | 32 | 1/2" | LC | 14001 | B-5 | HB | 30 | LS63007 | LC14002 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.8 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23017 |  | 32 | 1" | LC | 23017 | B-5 | HB | 40 | LS23018 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.18 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23027 |  | 32 | 1/2" | LC | 23027 | B-5 | HB | 30 | LS23029 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23062 |  | 32 | 1/2" | LC | 23062 | B-5 | HB | 30 | LS23049 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31006 |  | 32 | 3/4" | LC | 31006 | B-5 | HB | 30 | LS31022 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC51006 |  | 32 | 3/4" | LC | 51006 | B-5 | HB | 30 | LS51004 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC51009 |  | 32 | 3/4" | LC | 51009 | B-5 | HB | 30 | LS51001 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC61004 |  | 32 | 3/4" | LC | 61004 | B-5 | HB | 30 | LS61001 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC6300S |  | 32 | 3/4" | LC | 6300S | B-5 | HB | 30 | 32-1111-S-011 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63028 |  | 32 | 1" | LC | 63028 | B-5 | P | 50 | LC63034 | JWR64006 | 12.0 | 180.0 | 8.0/5.0 | 95.0/95.0 |  | 18.05 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 95 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-01 |  | E | N | 000 | N | 136
LS630AM |  | 32 | 1" | LS | 630AM | B-5 | HB | 70 | JLS23010 | LC23061 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63140 |  | 32 | 1/2" | LS | 63140 | B-5 | HB | 60 | LS63193 | JLS23021 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63191 |  | 32 | 2" | LS | 63191 | B-5 | HB | 80 | LS63189 | 32-1121-S-002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89039 |  | 32 | 1" | LS | 89039 | B-5 | HB | 70 | LS01001 | 32-US-1211-10 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89039 |  | 32 | 2" | LS | 89039 | B-5 | HB | 80 | LS01001 | 32-US-1211-10 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89042 |  | 32 | 3/4" | LS | 89042 | B-5 | HB | 60 | LS89039 | 32-US-1211-09 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.85 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N36019 | 08 | 32 | 2" | N | 36019 | B4S1 | N | 0 | TP-184 (32-D-3609) | TO TEMPORARY TANK | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
LS24010 |  | 32 | 1" | LS | 24010 | B-5 | HB | 70 | JLS24001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.20 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
N32013 | 08 | 32 | 1" | N | 32013 | B4S1 | N | 0 | TP-30A, (CYLINDER) | HEADER | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24E | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | 148
N32015 | 08 | 32 | 1/2" | N | 32015 | B4S1 | N | 0 | TP-40B, (32-D-3204B) | N32016 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N33003 | 08 | 32 | 1/2" | N | 33003 | B-1 | N | 0 | N67000 | N33001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N36009 | 08 | 32 | 1" | N | 36009 | B4S1 | N | 0 | TP-177 (CYLINDER 3, STAGE 1, PACKING 3, C46) | N36005 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N52030 | 08 | 32 | 1/2" | N | 52030 | 1CS2 | N | 0 | N52035 | 32-A-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.37 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-01 |  | M | N | 000 | N | 166
N6700F | 08 | 32 | 3/4" | N | 6700F | B-1 | N | 0 | N6700C | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700T | 08 | 32 | 3/4" | N | 6700T | B-1 | N | 0 | N67003 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-03 |  | E | N | 000 | N | 140
N67017 | 08 | 32 | 3" | N | 67017 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
BDL60001 |  | 32 | 1-1/2" | BDL | 60001 | B32S1 | ST | 30 | 32-D-6002 | CANTAINER | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.41 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60001 |  | 32 | 10" | BDL | 60001 | B32S1 | ST | 30 | 32-D-6002 | CANTAINER | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.41 | 1 | II | MOD.A2 | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60035 | 08 | 32 | 16" | BDL | 60035 | B32S1 | N | 0 | BDL34018 | BDL60002 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | III | MOD.G | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60049 | 08 | 32 | 1" | BDL | 60049 | B32S1 | N | 0 | N67100 | BDL60061 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL65005 | 08 | 32 | 1" | BDL | 65005 | B4S1 | N | 0 | BDL65002 | BDL65001 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.45 | 1 | I | MOD.A | Y | 1 | N | 32-P-031-01 |  | G | N | 141 | N | 470 | ,10
BDL71027 | 08 | 32 | 3/4" | BDL | 71027 | B4S1 | N | 0 | ET71077 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
PCW89010 | 08 | 32 | 2" | PCW | 89010 | 1CS2 | N | 0 | TP-N51703 (XV-8940) | 32-Z-8906 (TP-N41001) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68O | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PCW89010 | 08 | 32 | 12" | PCW | 89010 | 1CS2 | N | 0 | TP-N51703 (XV-8940) | 32-Z-8906 (TP-N41001) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68O | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PJW23007 |  | 32 | 6" | PJW | 23007 | B-1 | HB | 30 | PJW23006 | JWS64047 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | I | MOD.A | Y | 20 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW23008 |  | 32 | 3/4" | PJW | 23008 | B-1 | HB | 30 | PJW23006 | JWS32001 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
PN52016 | 7A | 32 | 1-1/2" | PN | 52016 | 1CS2 | HA | 30 | 32-E-5200 | 32-A-5200 | 6.9 | 200.0 | 0.5/0.5 | 110.0/30.0 |  | 9.18 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.37 | 2 | I | MOD.A | Y | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 151
PN52016 | 7A | 32 | 10" | PN | 52016 | 1CS2 | HA | 40 | 32-E-5200 | 32-A-5200 | 6.9 | 200.0 | 0.5/0.5 | 110.0/30.0 |  | 9.18 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.37 | 2 | I | MOD.A | Y | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 151
PN52018 | 7A | 32 | 1/2" | PN | 52018 | 1CS2 | HB | 30 | PN52027 | 32-E-5200 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52018 | 7A | 32 | 2" | PN | 52018 | 1CS2 | HB | 40 | PN52027 | 32-E-5200 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
TEA11012 | 08 | 32 | 1" | TEA | 11012 | 3DS3 | N | 0 | TEA11026 | TEA11009 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11026 | 08 | 32 | 1" | TEA | 11026 | 3DS3 | N | 0 | 32-S-1100 | TEA11012 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
VA00004 | 08 | 32 | 4" | VA | 00004 | B-1 | N | 0 | 1114-ACW-SM-062 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00013 | 08 | 32 | 4" | VA | 00013 | B-1 | N | 0 | 1211-ACW-SM-001 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00014 | 08 | 32 | 4" | VA | 00014 | B-1 | N | 0 | 3221-ACW-SM-101 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00050 | 08 | 32 | 4" | VA | 00050 | B-1 | N | 0 | 2211-ACW-SM-110 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00059 | 08 | 32 | 4" | VA | 00059 | B-1 | N | 0 | 3221-ACW-SM-111 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00064 | 08 | 32 | 4" | VA | 00064 | B-1 | N | 0 | 1123-ACW-SM-036 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00067 | 08 | 32 | 4" | VA | 00067 | B-1 | N | 0 | 4121-ACW-SM-011 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00102 | 08 | 32 | 4" | VA | 00102 | B-1 | N | 0 | 6111-ACW-SM-080 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA15004 | 08 | 32 | 1-1/2" | VA | 15004 | B4S2 | N | 0 | 32-D-1501 | N15001 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.9 | 2 | NA | NA | NA | 6 | N | 32-P-024-01 |  | E | N | 000 | N | 183
VA24010 | 08 | 32 | 1" | VA | 24010 | B4S2 | N | 0 | JWR24006 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.20 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA32004 | 08 | 32 | 2" | VA | 32004 | B4S2 | N | 0 | TP-36B, (32-D-3204B) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.24K | 2 | NA | NA | NA | 6 | N | 32-P-047-05 |  | E | N | 000 | N | 183
VA34002 | 08 | 32 | 2" | VA | 34002 | B4S2 | N | 0 | CD34009 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.26 | 2 | NA | NA | NA | 6 | N | 32-P-043-03 |  | E | N | 000 | N | 183
VA36001 | 08 | 32 | 2" | VA | 36001 | B4S2 | N | 0 | TP-183 (32-D-3609) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.28G | 2 | NA | NA | NA | 6 | N | 32-P-048-03 |  | E | N | 000 | N | 183
VZ15006 |  | 32 | 3/4" | VZ | 15006 | 1CS2 | EH | 30 | 32-S-1501 | 32-S-1501 | 1.0 | 150.0 | 0.1 | 30.0 |  | 1.5 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 241 | 23,25
VZ23008 | 08 | 32 | 2" | VZ | 23008 | D20S1 | HB | 40 | 32-D-2300 | DRAIN | 45.0/45.0 | 250.0/-45.0 | 38.0 | 120.0 |  | 0 | 0 | V | VESSEL TRIM | G | - | - | >1.5 | 120 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | N | 141 | N | 361 | 10
VZ34003 |  | 32 | 1" | VZ | 34003 | B32S1 | P | 50 | 32-S-3400 | PR34019 | 5.0/5.0 | 120.0/-45.0 | 0.6 | 80.0 |  | 7.5 | 29.4 | H | VESSEL TRIM | GS | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | G | N | 141 | N | 425 | ,10
VZ72014 | 08 | 32 | 2" | VZ | 72014 | C42S1 | N | 0 | 32-E-7200 | DRAIN | 43.7/43.7 | 150.0/-45.0 | 25.0 | 61.1 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | >1.5 | 61.1 | sh.51 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 414 | ,15
VZ81004 | 08 | 32 | 4" | VZ | 81004 | 1CS2 | N | 0 | 32-D-8106 | 32-D-8106 | 0.1/-0.01 | 100.0/100.0 | 0.02 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 40 | sh.62 | 2 | NA | NA | NA | NR | N | 32-P-061-04 |  | G | N | 200 | N | 410 | 6,25,23,25,10
SWW92024 | 08 | 32 | 4" | SWW | 92024 | 1CS2 | N | 0 | 32-D-9005 | ACW | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92026 | 08 | 32 | 3" | SWW | 92026 | 1CS2 | N | 0 | 32-H-9001B | SWW92012 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92029 | 08 | 32 | 1-1/2" | SWW | 92029 | 1CS2 | N | 0 | SWW92015 | 32-H-9001E | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
TEA10002 | 08 | 32 | 1/2" | TEA | 10002 | 3DS3 | N | 0 | TEAL CYLINDER | FO10001 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
VA00001 | 08 | 32 | 4" | VA | 00001 | B-1 | N | 0 | 1111-ACW-SM-044 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00012 | 08 | 32 | 4" | VA | 00012 | B-1 | N | 0 | 1123-ACW-SM-040 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00023 | 08 | 32 | 4" | VA | 00023 | B-1 | N | 0 | 2121-ACW-MH-003 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00034 | 08 | 32 | 4" | VA | 00034 | B-1 | N | 0 | 2121-ACW-SM-118 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00043 | 08 | 32 | 4" | VA | 00043 | B-1 | N | 0 | 2131-ACW-SM-067 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00045 | 08 | 32 | 4" | VA | 00045 | B-1 | N | 0 | 2131-ACW-SM-070 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00054 | 08 | 32 | 4" | VA | 00054 | B-1 | N | 0 | 3221-ACW-SM-092 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00098 | 08 | 32 | 4" | VA | 00098 | B-1 | N | 0 | 7111-ACW-SM-075 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
FO11013 | 08 | 32 | 1/2" | FO | 11013 | 3DS3 | N | 0 | TEA11014 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11022 |  | 32 | 3/4" | FO | 11022 | B4S2 | ET | 30 | FO11023 | FO11006 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11022 |  | 32 | 2" | FO | 11022 | B4S2 | ET | 30 | FO11023 | FO11006 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
O66024 |  | 32 | 1" | O | 66024 | B4S2 | ET | 30 | O66011 | O66025 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
P23023 |  | 32 | 3/4" | P | 23023 | 1FS4 | ST | 30 | P23022 | HCM23056 | 42.0/42.0 | -40.0/200.0 | 30.0 | 100.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | G | N | 141 | N | 521 | 10
P23025 |  | 32 | 1/2" | P | 23025 | C42S5 | HB | 30 | P23024 | 32-D-2301 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23025 |  | 32 | 14" | P | 23025 | C42S5 | HB | 40 | P23024 | 32-D-2301 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P23030 | 08 | 32 | 3" | P | 23030 | C42S2 | HB | 30 | 32-R-2300 | BDL23068 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P31010 |  | 32 | 3/4" | P | 31010 | QXC25S2 | P | 50 | 32-Z-3100A | BDL31026 | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P31011 |  | 32 | 1" | P | 31011 | QXC25S2 | P | 50 | 32-S-3100 | 32-Z-3100A | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | II | MOD.A2 | Y | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P31011 |  | 32 | 2" | P | 31011 | QXC25S2 | P | 50 | 32-S-3100 | 32-Z-3100A | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | II | MOD.A2 | Y | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P40025 |  | 32 | 1" | P | 40025 | C42S1 | HB | 30 | P40030 | P40032 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
P40025 |  | 32 | 3" | P | 40025 | C42S1 | HB | 30 | P40030 | P40032 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
P40030 | 08 | 32 | 1/2" | P | 40030 | C42S3 | WS | 50 | TP-2 (P400101) | 32-E-4001 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40030 | 08 | 32 | 3/4" | P | 40030 | C42S3 | WS | 50 | TP-2 (P400101) | 32-E-4001 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | III | MOD.G | Y | 20 | N | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40030 | 08 | 32 | 32" | P | 40030 | C42S3 | WS | 50 | TP-2 (P400101) | 32-E-4001 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 31.23 | 35.04 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.30 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-3 | N | 141 | N | 423 | 13,10,20
P40032 |  | 32 | 8" | P | 40032 | C42S2 | ET | 40 | P40041 | VZ40006 | 25.0/25.0 | -45.0/130.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 85 | sh.31 | 1 | III | MOD.G | Y | 20 | Y | 32-P-049-01 |  | G-2 | N | 141 | N | 429 | ,10,6,11,13,38,39
FW68O08 | 08 | 32 | 1-1/2" | FW | 68O08 | B-13 | N | 0 | FW68O06 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
PR72043 | 08 | 32 | 1" | PR | 72043 | C42S1 | N | 0 | PR72015 | BDL72039 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72043 | 08 | 32 | 3" | PR | 72043 | C42S1 | N | 0 | PR72015 | BDL72039 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PR72064 | 08 | 32 | 1-1/2" | PR | 72064 | C42S1 | N | 0 | TP-017 (PR720132) | BDL72069 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | II | MOD.A2 | Y | 7 | N | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72064 | 08 | 32 | 2" | PR | 72064 | C42S1 | N | 0 | TP-017 (PR720132) | BDL72069 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | II | MOD.A2 | Y | 7 | Y | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72066 | 08 | 32 | 1-1/2" | PR | 72066 | C42S1 | N | 0 | TP-018 (PR720115) | BDL72070 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | II | MOD.A2 | Y | 7 | N | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72066 | 08 | 32 | 3" | PR | 72066 | C42S1 | N | 0 | TP-018 (PR720115) | BDL72070 | 43.7/43.7/4.5 | 150.0/-45.0/300.0 | 23.8/3.2 | 40.0/280.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.52C | 1 | II | MOD.A2 | Y | 7 | Y | 32-P-007-04 |  | F | N | 141 | N | 352 | ,15
PR72074 | 08 | 32 | 1/2" | PR | 72074 | C42S1 | N | 0 | TP-022 (PR720109) | BDL72063 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PW50016 | 08 | 32 | 3/4" | PW | 50016 | B4S2 | N | 0 | 32-T-5001 | PW50017 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50016 | 08 | 32 | 1" | PW | 50016 | B4S2 | N | 0 | 32-T-5001 | PW50017 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50016 | 08 | 32 | 3" | PW | 50016 | B4S2 | N | 0 | 32-T-5001 | PW50017 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW50023 |  | 32 | 1" | PW | 50023 | B4S2 | HB | 30 | 32-P-5001 | 32-T-5001 | 9.0 | 180.0 | 4.0 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | I | MOD.A | Y | 20 | N | 32-P-050-02 |  | E | N | 140 | N | 31
PW50023 |  | 32 | 6" | PW | 50023 | B4S2 | HB | 30 | 32-P-5001 | 32-T-5001 | 9.0 | 180.0 | 4.0 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | I | MOD.A | Y | 20 | N | 32-P-050-02 |  | E | N | 140 | N | 31
PW50026 | 08 | 32 | 1" | PW | 50026 | B4S2 | N | 0 | 32-D-5002 | PR50011 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW51010 | 08 | 32 | 3/4" | PW | 51010 | B4S1 | N | 0 | 32-D-5102 | (TRENCH) | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51010 | 08 | 32 | 1-1/2" | PW | 51010 | B4S1 | N | 0 | 32-D-5102 | (TRENCH) | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51011 |  | 32 | 1" | PW | 51011 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51011 |  | 32 | 2" | PW | 51011 | B4S1 | ST | 30 | 32-D-5100 | 32-D-5102 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51014 | 08 | 32 | 2" | PW | 51014 | B4S1 | N | 0 | 32-D-5101 | BDL51018 | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PR51017 | 08 | 32 | 3/4" | PR | 51017 | B4S1 | ST | 30 | D-5110 (TP-N15) | PR51016 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR51017 | 08 | 32 | 3" | PR | 51017 | B4S1 | ST | 30 | D-5110 (TP-N15) | PR51016 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR53006 | 08 | 32 | 1/2" | PR | 53006 | B4S1 | N | 0 | PR53004 | BDL53003 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | Art 4.3 | NA | N | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
IA62010 | 08 | 32 | 1/2" | IA | 62010 | B-13 | N | 0 | IA62003 | 32-IAM-127 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-02 |  | - | N | 000 | - | 200
IA62010 | 08 | 32 | 1-1/2" | IA | 62010 | B-13 | N | 0 | IA62003 | 32-IAM-127 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-02 |  | - | N | 000 | - | 200
IA620AC | 08 | 32 | 3/4" | IA | 620AC | B-13 | N | 0 | IA62077 | 32-IAT-141 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AE | 08 | 32 | 3/4" | IA | 620AE | B-13 | N | 0 | IA62081 | 32-IAT-132 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AE | 08 | 32 | 1" | IA | 620AE | B-13 | N | 0 | IA62081 | 32-IAT-132 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AP | 08 | 32 | 1-1/2" | IA | 620AP | B-13 | N | 0 | IA62081 | 32-IAT-132 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AV | 08 | 32 | 1-1/2" | IA | 620AV | B-13 | N | 0 | IA620AQ | 32-IAT-083 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA62904 | 08 | 32 | 1-1/2" | IA | 62904 | B-13 | N | 0 | IA62004 | 20 LTR TANK | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
VZ01003 | 08 | 32 | 1/2" | VZ | 01003 | 3FS4 | N | 0 | 32-S-0101 | BDL01037 | 45.0 | 100.0 | 40.0 | 40.0 |  | 0 | 0 | V | VESSEL TRIM | G | - | - | >1.5 | 40 | sh.1 | 1 | Art 4.3 | NA | N | NR | N | 32-P-002-01 |  | F | Y | 040 | N | 290 | 5,23,10,25,36
VZ12009 |  | 32 | 3/4" | VZ | 12009 | 1CS2 | ET | 30 | 32-D-1200A | 32-D-1200A | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12009 |  | 32 | 2" | VZ | 12009 | 1CS2 | ET | 30 | 32-D-1200A | 32-D-1200A | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
VZ12010 |  | 32 | 1" | VZ | 12010 | 1CS2 | ET | 30 | 32-D-1200B | 32-D-1200B | 0.5 | 150.0 | 0.05 | 30.0 |  | .75 | 28.5 | IO | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.5 | 2 | NA | NA | NA | NR | N | 32-P-022-01 |  | M | N | 220 | N | 272 | 23,25
IA68N03 | 08 | 32 | 1" | IA | 68N03 | B-13 | N | 0 | IA68N04 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N35 | 08 | 32 | 1" | IA | 68N35 | B-13 | N | 0 | SWIVEL JOINT | IA68M11 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68O03 | 08 | 32 | 1" | IA | 68O03 | B-13 | N | 0 | IA68O04 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68O19 | 08 | 32 | 1" | IA | 68O19 | B-13 | N | 0 | IA68O09 | IA68O10 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68P08 | 08 | 32 | 1" | IA | 68P08 | B-13 | N | 0 | IA68P06 | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Q05 | 08 | 32 | 1" | IA | 68Q05 | B-13 | N | 0 | IA68Q04 | IA68Q01 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
LA84038 |  | 32 | 1" | LA | 84038 | 4CS2 | ET | 30 | LA84037 | LA84032 | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LC13004 |  | 32 | 1/2" | LC | 13004 | B-5 | HB | 30 | LC13001 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23039 |  | 32 | 1/2" | LC | 23039 | B-5 | HB | 30 | LS23029 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23049 |  | 32 | 1/2" | LC | 23049 | B-5 | HB | 30 | LS23034 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.17 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC24015 |  | 32 | 1-1/2" | LC | 24015 | B-5 | HB | 40 | LS63073 | LC34004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.20 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31013 |  | 32 | 1/2" | LC | 31013 | B-5 | HB | 30 | LS31025 | LC31015 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31018 | 08 | 32 | 1" | LC | 31018 | B-5 | P | 50 | LS31023 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
HOR89003 | 08 | 32 | 3" | HOR | 89003 | C-2 | HA | 90 | TP-N42502 (32-CPN-A408) | TP-N60204 (32-P-8908C/D) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL RETURN | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 209
HTF89005 | 08 | 32 | 1" | HTF | 89005 | C-2 | HA | 80 | HOR89001 | COLLECTION DRUM | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | DIATHERMIC OIL/HOT THERMAL FLUID | L | - | - | <1.5 | 280 | sh.68R | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 207
IA23001 | 08 | 32 | 1" | IA | 23001 | B-13 | N | 0 | IA62079 | TO C-2500 COMPRESSOR AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62006 | 08 | 32 | 2" | IA | 62006 | B-13 | N | 0 | IA01001 | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62008 | 08 | 32 | 2" | IA | 62008 | C3S1 | N | 0 | 32-D-6200 | VA62001 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA620AO | 08 | 32 | 1-1/2" | IA | 620AO | B-13 | N | 0 | 32-IAT-079 | 32-IAM-013 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA68C01 | 08 | 32 | 1" | IA | 68C01 | B-13 | N | 0 | IA68C05 | AIR MAINTENANCE DEVICE | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-18 |  | - | N | 000 | - | 200
IA68H29 | 08 | 32 | 1" | IA | 68H29 | B-13 | N | 0 | IA68C09 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I26 | 08 | 32 | 1" | IA | 68I26 | B-13 | N | 0 | IA68I20 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
ET22007 | 08 | 32 | 1" | ET | 22007 | 3FS4 | N | 0 | ET22010 | P23022 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | N | 32-P-044-01 |  | G | N | 041 | N | 322 | 36,10,5
ET22007 | 08 | 32 | 2" | ET | 22007 | 3FS4 | N | 0 | ET22010 | P23022 | 48.0 | 120.0 | 40.0 | 40.0 |  | 72 | 148.95 | H | ETHYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-044-01 |  | G | N | 041 | N | 322 | 36,10,5
ET71037 | 08 | 32 | 1" | ET | 71037 | C3S1 | N | 0 | ET71036 | ET71064 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71038 | 08 | 32 | 1" | ET | 71038 | C3S1 | N | 0 | ET71037 | ET710138 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.49 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
ET71048 |  | 32 | 4" | ET | 71048 | C3S1 | HB | 30 | ET71049 | 32-E-7100 | 38.3 | 250.0 | 32.6/32.6 | 50.0/100.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 50 | sh.48 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-006-02 |  | C | N | 041 | N | 316 | ,10
ET71076 | 7A | 32 | 1" | ET | 71076 | C3S1 | HA | 60 | ET71042 | BDL71026 | 38.3/4.5 | 250.0/250.0 | 30.0/3.2 | 100.0/210.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | NR | N | 32-P-006-02 |  | C | N | 041 | N | 317 | 10,37
LS13002 |  | 32 | 1" | LS | 13002 | B-5 | HB | 70 | LS13001 | 32-D-1300 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23024 |  | 32 | 1/2" | LS | 23024 | B-5 | HB | 60 | HCM23067 | LC23034 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23034 |  | 32 | 1/2" | LS | 23034 | B-5 | HB | 60 | 32-S-2300 | LC23049 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.17 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23048 |  | 32 | 1/2" | LS | 23048 | B-5 | HB | 60 | HCM23063 | LC23050 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31031 |  | 32 | 1/2" | LS | 31031 | B-5 | HB | 60 | 32-S-3100 | LC31030 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS43011 |  | 32 | 3/4" | LS | 43011 | C6S1 | HB | 50 | 32-E-4303 | LC43001 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.33 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | E | N | 141 | N | 1092
LS43011 |  | 32 | 1" | LS | 43011 | C6S1 | HB | 50 | 32-E-4303 | LC43001 | 29.0/-1.0 | 250.0/250.0 | 3.5/3.5 | 200.0/148.0 |  | 45.4 | 76.65 | H | STEAM - LP | G | - | - | >1.5 | 148 | sh.33 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | E | N | 141 | N | 1092
LS60016 |  | 32 | 1" | LS | 60016 | B-5 | HB | 70 | PURGE CONNECTION | BDL60046 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60026 |  | 32 | 1" | LS | 60026 | B-5 | HB | 70 | HOSE CONNECTION | BDL60056 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78 | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-01 |  | E | N | 000 | N | 90
IA6200F | 08 | 32 | 1" | IA | 6200F | B-13 | N | 0 | IA62001 | 32-AH-0001 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200O | 08 | 32 | 1" | IA | 6200O | B-13 | N | 0 | IA62077 | 32-IAM-044 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200R | 08 | 32 | 1" | IA | 6200R | B-13 | N | 0 | IA62078 | 32-IAM-007 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62060 | 08 | 32 | 1" | IA | 62060 | B-13 | N | 0 | IA62001 | TO C-2500 COMPRESSOR AREA | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62075 | 08 | 32 | 2" | IA | 62075 | B-13 | N | 0 | IA62001 | IA62052 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62079 | 08 | 32 | 1-1/2" | IA | 62079 | B-13 | N | 0 | IA62089 | 32-IAM-004 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62091 | 08 | 32 | 1-1/2" | IA | 62091 | B-13 | N | 0 | IA62010 | VA62002 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-02 |  | - | N | 000 | - | 200
IA620AJ | 08 | 32 | 3/4" | IA | 620AJ | B-13 | N | 0 | IA62081 | 32-IAT-134 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AN | 08 | 32 | 3/4" | IA | 620AN | B-13 | N | 0 | IA62081 | 32-IAT-085 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
LC63029 |  | 32 | 3/4" | LC | 63029 | B-5 | P | 50 | LC63059 | LC63040 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63031 |  | 32 | 4" | LC | 63031 | B-5 | P | 50 | 32-D-6300 | LC63041 | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63040 |  | 32 | 2" | LC | 63040 | B-5 | P | 50 | 32-D-6300 | ACW | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-060-02 |  | E | Y | 000 | N | 133 | 77
LC63086 |  | 32 | 3/4" | LC | 63086 | B-5 | HB | 30 | LS63194 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63104 |  | 32 | 2" | LC | 63104 | B-5 | P | 50 | LC63001 | HEADER | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
N67019 | 08 | 32 | 3/4" | N | 67019 | B-1 | N | 0 | N67020 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67051 | 08 | 32 | 2" | N | 67051 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67088 | 08 | 32 | 3/4" | N | 67088 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67099 | 08 | 32 | 3/4" | N | 67099 | B-1 | N | 0 | N67029 | BDL60045 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67102 | 08 | 32 | 1" | N | 67102 | B-1 | N | 0 | N67061 | BDL60053 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N73003 | 08 | 32 | 1" | N | 73003 | B-1 | N | 0 | NITROGEN CONNECTION | BU73055 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.54 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | E | N | 000 | N | 140
N80011 | 08 | 32 | 3" | N | 80011 | 1CS2 | N | 0 | N89071 | 32-PV-8011A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.57 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N01008 | 08 | 32 | 2" | N | 01008 | B-1 | N | 0 | N01001 | LPN01001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N12021 | 08 | 32 | 1-1/2" | N | 12021 | 1CS2 | N | 0 | 32-D-1200B | N12009 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N12023 | 08 | 32 | 1/2" | N | 12023 | 1CS2 | N | 0 | N67057 | N12020 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
N13002 | 08 | 32 | 1-1/2" | N | 13002 | B-1 | N | 0 | N13003 | 32-D-1602 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.6 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N16010 | 08 | 32 | 2" | N | 16010 | 1CS2 | N | 0 | 32-D-1600 | N16011 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.10 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N32022 | 08 | 32 | 2" | N | 32022 | B4S1 | N | 0 | TP-33B, (32-D-3203B) | TO TEMPORARY TANK | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N33002 | 08 | 32 | 3/4" | N | 33002 | B-1 | N | 0 | N33001 | 32-P-3300B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N36012 | 08 | 32 | 1" | N | 36012 | B4S1 | N | 0 | TP-168 (CYLINDER 1, STAGE 1, PACKING 1, C79) | TP-178 (32-D-3608) | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N36018 | 08 | 32 | 2" | N | 36018 | B4S1 | N | 0 | TP-180 (32-D-3608) | TO TEMPORARY TANK | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
LO32005 | 08 | 32 | 1/2" | LO | 32005 | QXB-55 | N | 0 | TP-12A, PK-3600, C40, NEA STANDARD COARSE STRAINER | TP-13A, 32-P-3202A | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 110 | N | 800
LO36006 | 08 | 32 | 3" | LO | 36006 | QXB-55 | N | 0 | TP-136 (PK-3600) | TP-137 (32-P-3602) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.28D | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 110 | N | 800
N67042 | 08 | 32 | 1/2" | N | 67042 | B-1 | N | 0 | N67043 | 32-H-5201 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67081 | 08 | 32 | 3/4" | N | 67081 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67095 | 08 | 32 | 3/4" | N | 67095 | B-1 | N | 0 | N67017 | BDL60044 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N670AA | 08 | 32 | 1" | N | 670AA | B-1 | N | 0 | N67005 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N670AD | 08 | 32 | 3/4" | N | 670AD | B-1 | N | 0 | N6700H | FX-6748 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N72008 | 08 | 32 | 1-1/2" | N | 72008 | B4S2 | HA | 60 | TP-013 (N720129) | N72006 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.48 | 2 | Art 4.3 | NA | N | NR | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N72008 | 08 | 32 | 3" | N | 72008 | B4S2 | HA | 70 | TP-013 (N720129) | N72006 | 4.5 | 250.0 | 3.2 | 225.0 |  | 5.99 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 225 | sh.48 | 2 | Art 4.3 | NA | N | NR | N | 32-P-007-05 |  | E | N | 000 | N | 147 | 26,9,37
N73005 | 08 | 32 | 1" | N | 73005 | B-1 | N | 0 | NITROGEN CONNECTION TO NEAREST UTILITY STATION SHALL BE UTILIZE | BU73049 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.55 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | E | N | 000 | N | 140
N73006 | 08 | 32 | 1" | N | 73006 | B-1 | N | 0 | NITROGEN CONNECTION TO NEAREST UTILITY STATION SHALL BE UTILIZE | VZ73007 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.55 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | E | N | 000 | N | 140
N81020 | 08 | 32 | 1/2" | N | 81020 | 1CS2 | N | 0 | N89004 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N89034 | 08 | 32 | 2" | N | 89034 | B-1 | N | 0 | N01001 | N89010 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
PR01002 | 08 | 32 | 3/4" | PR | 01002 | C42S1 | N | 0 | PR80001 | PR01001 | 43.7/43.7 | 80.0/-46.0 | 31.1/31.1 | 42.0/0.0 |  | 65.55 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-01 |  | F | N | 141 | N | 360 | ,15
PR01002 | 08 | 32 | 4" | PR | 01002 | C42S1 | N | 0 | PR80001 | PR01001 | 43.7/43.7 | 80.0/-46.0 | 31.1/31.1 | 42.0/0.0 |  | 65.55 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-01 |  | F | N | 141 | N | 360 | ,15
PR01002 | 08 | 32 | 6" | PR | 01002 | C42S1 | N | 0 | PR80001 | PR01001 | 43.7/43.7 | 80.0/-46.0 | 31.1/31.1 | 42.0/0.0 |  | 65.55 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.1 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-01 |  | F | N | 141 | N | 360 | ,15
PR22015 | 08 | 32 | 3/4" | PR | 22015 | D20S1 | N | 0 | PR22016 | PR23012 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR22015 | 08 | 32 | 4" | PR | 22015 | D20S1 | N | 0 | PR22016 | PR23012 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.13 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 330 | 15
PR24038 | 08 | 32 | 3" | PR | 24038 | D20S1 | N | 0 | PR24037 | HCM23065 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR24041 |  | 32 | 1" | PR | 24041 | D20S1 | HB | 30 | PR24040 | HCM23078 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR33003 | 08 | 32 | 1-1/2" | PR | 33003 | C42S1 | N | 0 | PR33002 | PR33004 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33005 | 08 | 32 | 1" | PR | 33005 | C42S1 | N | 0 | PR33002 | SL21002 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33009 | 08 | 32 | 1-1/2" | PR | 33009 | C42S1 | N | 0 | 32-E-3300 | PR33008 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33009 | 08 | 32 | 6" | PR | 33009 | C42S1 | N | 0 | 32-E-3300 | PR33008 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33012 | 08 | 32 | 2" | PR | 33012 | C42S1 | N | 0 | PR33013 | 32-E-3301 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33013 | 08 | 32 | 3" | PR | 33013 | C42S1 | N | 0 | PR33014 | PR33012 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33021 | 08 | 32 | 1/2" | PR | 33021 | C42S1 | N | 0 | PR33022 | 32-E-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33021 | 08 | 32 | 6" | PR | 33021 | C42S1 | N | 0 | PR33022 | 32-E-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR34017 | 08 | 32 | 3/4" | PR | 34017 | B4S1 | N | 0 | 32-D-3400 | PR34029 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 6 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34017 |  | 32 | 2" | PR | 34017 | B4S1 | ET | 50 | 32-D-3400 | PR34029 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
VA62001 | 08 | 32 | 2" | VA | 62001 | B4S2 | N | 0 | IA62008 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.43 | 2 | NA | NA | NA | 6 | N | 32-U-094-02 |  | E | N | 000 | N | 183
VA81101 | 08 | 32 | 8" | VA | 81101 | B4S2 | N | 0 | 32-C-8120 | OUTDOOR TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.60A | 2 | NA | NA | NA | 6 | N | 32-P-061-02 |  | E | N | 000 | N | 183
VA94002 | 08 | 32 | 1" | VA | 94002 | B4S2 | N | 0 | CWR94004 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.74 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
WW21001 |  | 32 | 1-1/2" | WW | 21001 | B4S2 | HB | 30 | LC21001 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.12 | 2 | Art 4.3 | NA | N | 20 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW24002 | 08 | 32 | 1/2" | WW | 24002 | B4S2 | N | 0 | TP-16 (HCM240108) | DRAIN HEADER | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.21A | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW52009 | 08 | 32 | 2" | WW | 52009 | B4S2 | N | 0 | 32-D-5202 | ACW | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 87
WW64004 | 08 | 32 | 1-1/2" | WW | 64004 | B4S2 | N | 0 | FROM LC-23043 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW66003 | 08 | 32 | 8" | WW | 66003 | B4S2 | N | 0 | CONCRETE CURB | 4131-ACW-200-CS-243 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.46 | 2 | I | MOD.A | Y | 1 | N | 32-P-021-03 |  | E | N | 000 | N | 87
VA81021 | 08 | 32 | 8" | VA | 81021 | B4S2 | N | 0 | 32-C-8121 | OUTDOOR TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.60 | 2 | NA | NA | NA | 6 | N | 32-P-061-02 |  | E | N | 000 | N | 183
VA91031 | 08 | 32 | 1" | VA | 91031 | B4S2 | N | 0 | CWR91001 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.105 | 2 | NA | NA | NA | 6 | N | 32-U-021-03 |  | E | N | 000 | N | 183
FW68A01 | 08 | 45 | 18" | FW | 68A01 | PEB-69 | N | 0 | FW68A17 | IP-TCM/OFF-PIP-005 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | TP-FW-01 |  | - | N | 000 | - | 73 | 76
FW68A0G | 08 | 45 | 6" | FW | 68A0G | UGB-1PE | N | 0 | FW68A63 | 45-HY-6808 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A41 | 08 | 45 | 1-1/2" | FW | 68A41 | B-7 | N | 0 | FW68A38 | 45-HR-6802 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A67 | 08 | 45 | 16" | FW | 68A67 | PEB-69 | N | 0 | FW68A10 | FW68A0I | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B01 | 08 | 45 | 10" | FW | 68B01 | PEB-69 | N | 0 | IP-TCM/OFF-PIP-003 | FW68A03 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | TP-FW-03 |  | - | N | 000 | - | 73 | 76
FW68B06 | 08 | 45 | 6" | FW | 68B06 | PEB-69 | N | 0 | FW68A03 | FW68B0D | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B0K | 08 | 45 | 6" | FW | 68B0K | UGB-1PE | N | 0 | FW68B51 | FW68B52 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0W | 08 | 45 | 6" | FW | 68B0W | UGB-1PE | N | 0 | FW68B65 | 45-HY-6818 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B10 | 08 | 45 | 6" | FW | 68B10 | PEB-69 | N | 0 | FW68B97 | FW68B03 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B15 | 08 | 45 | 2" | FW | 68B15 | B-7 | N | 0 | FW68B95 | HOSE STATION (INDOOR) | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B15 | 08 | 45 | 8" | FW | 68B15 | B-7 | N | 0 | FW68B95 | HOSE STATION (INDOOR) | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B43 | 08 | 45 | 1/2" | FW | 68B43 | B-7 | N | 0 | FW68B0G | DELUGE VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68O19 | 08 | 32 | 1-1/2" | FW | 68O19 | B-13 | N | 0 | FW68O16 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68P02 | 08 | 32 | 1" | FW | 68P02 | B-13 | N | 0 | FW68P01 | FW68P01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P12 | 08 | 32 | 1/2" | FW | 68P12 | B-13 | N | 0 | FW68P10 | FW68P10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P18 | 08 | 32 | 3" | FW | 68P18 | B-13 | N | 0 | FW68P05 | FW68P01 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68Q09 | 08 | 32 | 1-1/2" | FW | 68Q09 | B-13 | N | 0 | FW68Q01 | FW68Q12 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | Y | 000 | - | 74
FW68R05 | 08 | 45 | 1" | FW | 68R05 | B-13 | N | 0 | 45-XV-6822A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-08 |  | - | Y | 000 | - | 74
FW68R08 | 08 | 45 | 6" | FW | 68R08 | B-13 | N | 0 | 45-XV-6819A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68R09 | 08 | 45 | 1/2" | FW | 68R09 | B-7 | N | 0 | FW68R07 | 45-XV-6819A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R09 | 08 | 45 | 6" | FW | 68R09 | B-7 | N | 0 | FW68R07 | 45-XV-6819A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
PW51017 |  | 32 | 1/2" | PW | 51017 | B4S1 | ST | 30 | FLANGE HEADER | FLANGE HEADER | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
PW51017 |  | 32 | 1" | PW | 51017 | B4S1 | ST | 30 | FLANGE HEADER | FLANGE HEADER | 10.0 | 190.0 | 5.0 | 40.0 |  | 15.06 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 40 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-04 |  | E | N | 110 | N | 82
HCM24068 |  | 32 | 10" | HCM | 24068 | C42S1 | HB | 40 | HCM24067 | HCM24093 | 42.0/42.0 | -45.0/100.0 | 35.0/35.0 | 75.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 20 | Y | 32-P-045-01 |  | G | Y | 141 | N | 529 | 10
HCM24069 |  | 32 | 3/4" | HCM | 24069 | D20S1 | HB | 30 | 32-P-2400A | 32-S-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24069 |  | 32 | 8" | HCM | 24069 | D20S1 | HB | 40 | 32-P-2400A | 32-S-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24074 |  | 32 | 6" | HCM | 24074 | D20S1 | HB | 30 | 32-P-2400B | BDL24065 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 118.55 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 20 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24075 |  | 32 | 4" | HCM | 24075 | D20S1 | P | 50 | HCM24073 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24078 |  | 32 | 3/4" | HCM | 24078 | D20S1 | P | 50 | 32-E-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24078 |  | 32 | 3" | HCM | 24078 | D20S1 | P | 50 | 32-E-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24078 |  | 32 | 6" | HCM | 24078 | D20S1 | P | 50 | 32-E-2400 | 32-T-2400 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24079 |  | 32 | 3/4" | HCM | 24079 | D20S1 | HB | 30 | HCM24080 | HCM24078 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24079 |  | 32 | 1-1/2" | HCM | 24079 | D20S1 | HB | 30 | HCM24080 | HCM24078 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24079 |  | 32 | 3" | HCM | 24079 | D20S1 | HB | 30 | HCM24080 | HCM24078 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24080 |  | 32 | 3/4" | HCM | 24080 | D20S1 | ET | 30 | 32-E-2400 | HCM24059 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 20 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24081 |  | 32 | 2" | HCM | 24081 | D20S1 | ET | 30 | HCM24080 | HCM24059 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24082 | 08 | 32 | 1-1/2" | HCM | 24082 | D20S1 | N | 0 | HCM24083 | PR24007 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-02 |  | F | N | 141 | N | 530 | 15
IA68C10 | 08 | 32 | 1" | IA | 68C10 | B-13 | N | 0 | 32-XV-6802A | IA68I20 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68C11 | 08 | 32 | 1/2" | IA | 68C11 | B-13 | N | 0 | 32-XV-6810A | IA68Q06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68H12 | 08 | 32 | 1" | IA | 68H12 | B-13 | N | 0 | IA68C09 | IA68H16 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I06 | 08 | 32 | 1" | IA | 68I06 | B-13 | N | 0 | IA68I09 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68I09 | 08 | 32 | 1" | IA | 68I09 | B-13 | N | 0 | IA68I10 | IA68I04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68L20 | 08 | 32 | 1" | IA | 68L20 | B-13 | N | 0 | IA68L09 | IA68L09 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68N31 | 08 | 32 | 1" | IA | 68N31 | B-13 | N | 0 | IA68N04 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N43 | 08 | 32 | 1" | IA | 68N43 | B-13 | N | 0 | IA68N29 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68P06 | 08 | 32 | 1/2" | IA | 68P06 | B-13 | N | 0 | IA68K09 | IA68P07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68P12 | 08 | 32 | 1/2" | IA | 68P12 | B-13 | N | 0 | IA68P13 | IA68P13 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Q08 | 08 | 32 | 1" | IA | 68Q08 | B-13 | N | 0 | IA68Q06 | IA68Q10 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68R01 | 08 | 45 | 1" | IA | 68R01 | B-13 | N | 0 | IA68R02 | To Air Maintenance Device | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
IA69P03 | 08 | 32 | 1/2" | IA | 69P03 | B-13 | N | 0 | 100 LITERS AIR TANK | IA69P02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.10 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-03 |  | - | N | 000 | - | 200
IA89047 | 08 | 32 | 1/2" | IA | 89047 | B-13 | N | 0 | IA62006 | TP-N50424 (D-8901) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89054 | 08 | 32 | 2" | IA | 89054 | B-13 | N | 0 | IA89027 | 32-IAM-108 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
LC31036 | 08 | 32 | 1-1/2" | LC | 31036 | B-5 | HB | 40 | LS31045 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC32003 |  | 32 | 1/2" | LC | 32003 | B-5 | HB | 30 | LS32003 | LC63091 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.24 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC36001 |  | 32 | 1" | LC | 36001 | B-5 | HB | 40 | LC36101 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC36101 |  | 32 | 3/4" | LC | 36101 | B-5 | HB | 30 | LS63149 | LS63102 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC43003 |  | 32 | 3/4" | LC | 43003 | B-5 | P | 50 | LS43010 | LC20001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.33 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50005 |  | 32 | 1-1/2" | LC | 50005 | B-5 | P | 50 | P50016 | TO TRENCH | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-01 |  | E | Y | 000 | N | 133 | 77
LC61001 |  | 32 | 3/4" | LC | 61001 | B-5 | HB | 30 | LS61001 | LC63104 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300K |  | 32 | 1-1/2" | LC | 6300K | B-5 | HB | 40 | 32-1122-R-007 | LC63064 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63064 |  | 32 | 3" | LC | 63064 | B-5 | HB | 50 | HEADER | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65001 |  | 32 | 1/2" | LC | 65001 | B-5 | HB | 30 | LS65003 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC65001 |  | 32 | 1" | LC | 65001 | B-5 | HB | 40 | LS65003 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
IA68K07 | 08 | 32 | 1/2" | IA | 68K07 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68N05 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68K09 | 08 | 32 | 1/2" | IA | 68K09 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68L02 | 08 | 32 | 1" | IA | 68L02 | B-13 | N | 0 | IA68L15 | IA68L21 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68L09 | 08 | 32 | 1" | IA | 68L09 | B-13 | N | 0 | IA68L20 | IA68L20 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68M21 | 08 | 32 | 1" | IA | 68M21 | B-13 | N | 0 | IA68M26 | - | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68N04 | 08 | 32 | 1" | IA | 68N04 | B-13 | N | 0 | IA68N05 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N36 | 08 | 32 | 1" | IA | 68N36 | B-13 | N | 0 | IA68M11 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
FW68N45 | 08 | 32 | 1" | FW | 68N45 | B-13 | N | 0 | FW68N42 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N48 | 08 | 32 | 1" | FW | 68N48 | B-13 | N | 0 | FW68N47 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N59 | 08 | 32 | 1" | FW | 68N59 | B-13 | N | 0 | FW68N34 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N61 | 08 | 32 | 1" | FW | 68N61 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68O05 | 08 | 32 | 3" | FW | 68O05 | B-13 | N | 0 | FW68C10 | FW68O06 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O16 | 08 | 32 | 2" | FW | 68O16 | B-13 | N | 0 | FW68O14 | FW68O19 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O22 | 08 | 32 | 1-1/2" | FW | 68O22 | B-13 | N | 0 | FW68O12 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68P10 | 08 | 32 | 3" | FW | 68P10 | B-13 | N | 0 | FW68P09 | FW68P11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68P13 | 08 | 32 | 1-1/2" | FW | 68P13 | B-13 | N | 0 | FW68P10 | FW68P10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68R01 | 08 | 45 | 1/2" | FW | 68R01 | B-7 | N | 0 | FW68R07 | 45-XV-6820A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R01 | 08 | 45 | 2" | FW | 68R01 | B-7 | N | 0 | FW68R07 | 45-XV-6820A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
LS63009 |  | 32 | 3" | LS | 63009 | B-5 | HB | 80 | LS01001 | CAP | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300A |  | 32 | 1" | LS | 6300A | B-5 | HB | 70 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63010 |  | 32 | 3/4" | LS | 63010 | B-5 | HB | 60 | LS63178 | JLS16001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63041 | 08 | 32 | 1-1/2" | LS | 63041 | B-5 | HB | 70 | LS63193 | LS31027 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63048 |  | 32 | 3/4" | LS | 63048 | B-5 | HB | 60 | LS63177 | LS33001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63101 |  | 32 | 3/4" | LS | 63101 | B-5 | HB | 60 | LS63149 | 32-US-1112-001 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63180 |  | 32 | 1" | LS | 63180 | B-5 | HB | 70 | LS63178 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS72005 |  | 32 | 3/4" | LS | 72005 | B-5 | HB | 60 | LS63129 | LC72006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.51 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89046 | 08 | 32 | 2" | LS | 89046 | 3CS6 | HB | 40 | 32-S-8905 | TP-N50607 (32-D-8909, XV-8937) | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.68N | 2 | Art 4.3 | NA | N | 27 | N | 32-P-070-11 |  | M | N | 000 | N | 91
IA68C03 | 08 | 32 | 1" | IA | 68C03 | B-13 | N | 0 | IA68C05 | AIR MAINTENANCE DEVICE | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-18 |  | - | N | 000 | - | 200
IA68I10 | 08 | 32 | 1" | IA | 68I10 | B-13 | N | 0 | IA68C10 | IA68I09 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68L15 | 08 | 32 | 1" | IA | 68L15 | B-13 | N | 0 | FUSIBLE GLASS BULB | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68M22 | 08 | 32 | 1" | IA | 68M22 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M28 | 08 | 32 | 1" | IA | 68M28 | B-13 | N | 0 | IA68M19 | IA68M29 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M65 | 08 | 32 | 1" | IA | 68M65 | B-13 | N | 0 | IA68M63 | SPRINKLER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68N49 | 08 | 32 | 1" | IA | 68N49 | B-13 | N | 0 | IA68M11 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68P02 | 08 | 32 | 1" | IA | 68P02 | B-13 | N | 0 | IA68K09 | IA68P03 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Z01 | 08 | 45 | 1-1/2" | IA | 68Z01 | B-13 | N | 0 | AIR MAINTENANCE DEVICE (TP-02) | AIR MAINTENANCE DEVICE (TP-03) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.7 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-02 |  | - | N | 000 | - | 200
N81055 | 08 | 32 | 1/2" | N | 81055 | 1CS2 | N | 0 | N89061 | 32-PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60A | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N91013 | 08 | 32 | 2" | N | 91013 | 1CS2 | N | 0 | N89001 | N91014 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.70 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-01 |  | M | N | 000 | N | 166
LPN02004 | 08 | 32 | 3/4" | LPN | 02004 | 1C13 | N | 0 | LPN01001 | LPN11011 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN11003 | 08 | 32 | 1" | LPN | 11003 | 3DS3 | N | 0 | LPN11010 | 32-D-1100 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN11010 | 08 | 32 | 1/2" | LPN | 11010 | 1CS2 | N | 0 | LPN02002 | LPN11003 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 167 | 8,29,23,25
LPN11010 | 08 | 32 | 3/4" | LPN | 11010 | 1CS2 | N | 0 | LPN02002 | LPN11003 | 12.0 | 80.0 | 3.0 | 25.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 167 | 8,29,23,25
PA62036 | 08 | 32 | 3/4" | PA | 62036 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62050 | 08 | 32 | 3/4" | PA | 62050 | B-1 | N | 0 | PA62045 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62090 | 08 | 32 | 3/4" | PA | 62090 | B-1 | N | 0 | PA62039 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62094 | 08 | 32 | 3/4" | PA | 62094 | B-1 | N | 0 | PA62035 | FX-6268 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89029 | 08 | 32 | 3/4" | PA | 89029 | B-1 | N | 0 | PA89032 | 32-US-1211-08 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PCW89018 | 08 | 32 | 1/2" | PCW | 89018 | 1CS2 | P | 50 | PCW89011 | TP-N60105 (32-D-8906) | 6.0 | 100.0 | 3.0 | 60.0 |  | 9 | 28.5 | H | PELLET CUTTING WATER | L | - | - | <1.5 | 60 | sh.68Q | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-07 |  | M | N | 000 | N | 450 | 3
PR34018 |  | 32 | 1-1/2" | PR | 34018 | B4S1 | ET | 50 | PR34017 | BDL34014 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
PR34023 |  | 32 | 1" | PR | 34023 | B4S1 | P | 50 | 32-S-3401A | PR34022 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01,32-P-048-02 |  | C | Y | 141 | N | 376 | ,10
PR34027 |  | 32 | 3/4" | PR | 34027 | B4S1 | P | 50 | 32-S-3401B | BDL34017 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR34027 |  | 32 | 1-1/2" | PR | 34027 | B4S1 | P | 50 | 32-S-3401B | BDL34017 | 5.0 | 120.0 | 0.6/0.8 | 80.0/45.0 |  | 7.5 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.26 | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | Y | 141 | N | 376 | ,10
PR36013 | 08 | 32 | 1-1/2" | PR | 36013 | C42S1 | P | 50 | TP-125 (32-D-3607, FO-3667) | PR36032 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36013 | 08 | 32 | 4" | PR | 36013 | C42S1 | P | 50 | TP-125 (32-D-3607, FO-3667) | PR36032 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36016 | 08 | 32 | 12" | PR | 36016 | B4S1 | N | 0 | PR35011 | PR36026 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-048-02 |  | C | Y | 141 | N | 397 | ,10
PR36032 | 08 | 32 | 1-1/2" | PR | 36032 | C42S1 | P | 50 | PR36013 | BDL36022 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
PR36038 | 08 | 32 | 2" | PR | 36038 | B32S1 | P | 50 | TP-102 (32-D-3601) | PR36023 | 10.0/10.0 | -45.0/180.0 | 5.5 | 107.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 107 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 357 | 10
PR43034 | 08 | 32 | 4" | PR | 43034 | C42S1 | N | 0 | PR43024 | BU73047 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-001-02 |  | F | N | 141 | N | 350 | ,15
PR43037 | 08 | 32 | 2" | PR | 43037 | C42S1 | N | 0 | PR43039 | 32-P-4300 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 350 | ,15
PR43038 |  | 32 | 1" | PR | 43038 | C42S1 | HB | 30 | PR43039 | 32AT 2401-4 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43038 | 7A | 32 | 2" | PR | 43038 | C42S1 | ET | 30 | PR43039 | 32AT 2401-4 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
O20003 | 08 | 32 | 1/2" | O | 20003 | 1FS4 | N | 0 | 32-Z-2005 | 32-R-2000 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O31011 | 08 | 32 | 1" | O | 31011 | B4S2 | N | 0 | O31012 | O31010 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
CWR64001 | 08 | 32 | 8" | CWR | 64001 | B-1 | N | 0 | HEADER | CWR64015 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR80002 | 08 | 32 | 3/4" | CWR | 80002 | B-1 | N | 0 | 32-E-8001 | CWR80005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR80002 | 08 | 32 | 4" | CWR | 80002 | B-1 | N | 0 | 32-E-8001 | CWR80005 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.57 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
VZ13005 |  | 32 | 1" | VZ | 13005 | B4S2 | HH | 30 | 32-D-1301 | 32-D-1301 | 0.5 | 180.0 | 0.05/0.05 | 70.0/100.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-021-01 |  | E | N | 110 | N | 222 | 23,25
VZ13007 | 08 | 32 | 1" | VZ | 13007 | 1CS2 | EH | 30 | 32-S-1301 | VENT | 6.0 | 180.0 | 5.0/5.0 | 100.0/70.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 224 | 23,25
VZ33002 | 08 | 32 | 1" | VZ | 33002 | C42S1 | N | 0 | 32-D-3300 | 32-D-3300 | 25.0/25.0 | 120.0/-45.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 45 | sh.25 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 384 | 15
VZ92003 | 08 | 32 | 3/4" | VZ | 92003 | 1CS2 | N | 0 | 32-S-9015 | 32-S-9015 | 10.0 | 100.0 | 7.5 | 30.0 |  | 0 | 0 | V | VESSEL TRIM | L | - | - | <1.5 | 30 | sh.72 | 2 | Art 4.3 | NA | N | NR | N | 32-P-082-08 |  | M | N | 000 | N | 32 | 28
FW68B43 | 08 | 45 | 4" | FW | 68B43 | B-7 | N | 0 | FW68B0G | DELUGE VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B48 | 08 | 45 | 3/4" | FW | 68B48 | B-7 | N | 0 | FW68B0H | FW68R07 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B49 | 08 | 45 | 10" | FW | 68B49 | PEB-69 | N | 0 | FW68A03 | FW68B0J | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B92 | 08 | 45 | 8" | FW | 68B92 | UGB-1PE | N | 0 | FW68A55 | FW68A56 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68C05 | 08 | 32 | 1/2" | FW | 68C05 | B-7 | N | 0 | FW68C01 | 32-XV-6808A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C05 | 08 | 32 | 4" | FW | 68C05 | B-7 | N | 0 | FW68C01 | 32-XV-6808A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68C14 | 08 | 32 | 3/4" | FW | 68C14 | B-13 | N | 0 | 32-XV-6810A | FW68C11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68E02 | 08 | 32 | 1" | FW | 68E02 | B-7 | N | 0 | FW68E01 | INSPECTOR TEST VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E02 | 08 | 32 | 6" | FW | 68E02 | B-7 | N | 0 | FW68E01 | INSPECTOR TEST VALVE | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E12 | 08 | 32 | 2" | FW | 68E12 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E18 | 08 | 32 | 3" | FW | 68E18 | B-7 | N | 0 | FW68E27 | FW68E26 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E24 | 08 | 32 | 3" | FW | 68E24 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68F16 | 08 | 32 | 1" | FW | 68F16 | B-13 | N | 0 | FW68F30 | ARV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F16 | 08 | 32 | 3" | FW | 68F16 | B-13 | N | 0 | FW68F30 | ARV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F17 | 08 | 32 | 3/4" | FW | 68F17 | B-13 | N | 0 | FW68F16 | FW68F16 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F20 | 08 | 32 | 3/4" | FW | 68F20 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F21 | 08 | 32 | 3/4" | FW | 68F21 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F24 | 08 | 32 | 3/4" | FW | 68F24 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F26 | 08 | 32 | 3/4" | FW | 68F26 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F30 | 08 | 32 | 3/4" | FW | 68F30 | B-13 | N | 0 | FW68R08 | DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
HCM24082 | 08 | 32 | 4" | HCM | 24082 | D20S1 | N | 0 | HCM24083 | PR24007 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 141.72 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-02 |  | F | N | 141 | N | 530 | 15
HCM24085 |  | 32 | 4" | HCM | 24085 | D20S1 | P | 50 | HCM24097 | 32-E-2403 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 150.8 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24092 | 08 | 32 | 1/2" | HCM | 24092 | D20S1 | N | 0 | BDL24063 | 32-P-2400A | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24092 | 08 | 32 | 8" | HCM | 24092 | D20S1 | N | 0 | BDL24063 | 32-P-2400A | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24093 | 08 | 32 | 1/2" | HCM | 24093 | D20S1 | N | 0 | BDL24066 | 32-P-2400B | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24093 | 08 | 32 | 1" | HCM | 24093 | D20S1 | N | 0 | BDL24066 | 32-P-2400B | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24093 | 08 | 32 | 10" | HCM | 24093 | D20S1 | N | 0 | BDL24066 | 32-P-2400B | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 111.34 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 530 | 15
HCM24098 | 08 | 32 | 3/4" | HCM | 24098 | 3FS4 | HB | 30 | HCM24061 | HCM24065 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM24098 | 08 | 32 | 1-1/2" | HCM | 24098 | 3FS4 | HB | 30 | HCM24061 | HCM24065 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.19 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM31019 |  | 32 | 4" | HCM | 31019 | C42S1 | HB | 30 | 32-S-3101B | 32-E-3200 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.23 | 1 | III | MOD.G | Y | 20 | Y | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32018 |  | 32 | 3" | HCM | 32018 | C42S1 | HB | 40 | HCM32019 | HCM32033 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 351 | 10
HCM32019 | 08 | 32 | 2" | HCM | 32019 | C42S1 | HB | 40 | TP-06A (32-D-3202A) | HCM23046 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-04 |  | G | Y | 141 | N | 351 | 10
HCM32022 |  | 32 | 1" | HCM | 32022 | C42S1 | P | 50 | HCM32021 | BDL32020 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | Y | 141 | N | 351 | 10
HCM32023 |  | 32 | 1" | HCM | 32023 | C42S1 | P | 50 | HCM32021 | BDL32020 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
IA89037 | 08 | 32 | 1" | IA | 89037 | B-13 | N | 0 | IA62006 | IA620A0 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89051 | 08 | 32 | 1/2" | IA | 89051 | B-13 | N | 0 | IA62006 | 32-D-8007 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89053 | 08 | 32 | 3/4" | IA | 89053 | B-13 | N | 0 | IA89037 | N83002 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89057 | 08 | 32 | 1" | IA | 89057 | B-13 | N | 0 | IA89054 | 32-IAM-111 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89076 | 08 | 32 | 1" | IA | 89076 | B-13 | N | 0 | IA62006 | TO 32-IAM-514 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
VA00028 | 08 | 32 | 4" | VA | 00028 | B-1 | N | 0 | 2121-ACW-SM-099 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00029 | 08 | 32 | 4" | VA | 00029 | B-1 | N | 0 | 2121-ACW-SM-100 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00036 | 08 | 32 | 4" | VA | 00036 | B-1 | N | 0 | 2121-ACW-SM-094 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
LC66002 |  | 32 | 1/2" | LC | 66002 | B-5 | HB | 30 | LS02001 | LC66001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC66002 |  | 32 | 3/4" | LC | 66002 | B-5 | HB | 30 | LS02001 | LC66001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC89001 |  | 32 | 3/4" | LC | 89001 | B-5 | P | 50 | LS01001 | Funnel | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.85 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LO23002 | 08 | 32 | 1-1/2" | LO | 23002 | QXB-55 | N | 0 | TP 13 (D-2501) | TP 12 (LO230118) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.16B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-044-03 |  | M | N | 110 | N | 800
ET71064 | 08 | 32 | 2" | ET | 71064 | C3S1 | N | 0 | ET71037 | BDL71036 | 38.3 | 150.0 | 28.0 | 40.0 |  | 57.46 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 40 | sh.50B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-006-03 |  | C | N | 041 | N | 323 | ,10
FW68R02 | 08 | 45 | 2" | FW | 68R02 | B-7 | N | 0 | FW68R07 | 45-XV-6820A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68R14 | 08 | 45 | 6" | FW | 68R14 | B-13 | N | 0 | 45-XV-6824A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-09 |  | - | Y | 000 | - | 74
N12020 | 08 | 32 | 3/4" | N | 12020 | 1CS2 | N | 0 | END CAP | 32-LT-1203 | 0.5 | 80.0 | 0.45 | 30.0 |  | .55 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.5 | 2 | NA | NA | NA | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 154
N15002 | 08 | 32 | 1/2" | N | 15002 | B-1 | N | 0 | O15011 | N15001 | 0.5 | 150.0 | 0.01 | 30.0 |  | .55 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.9 | 2 | NA | NA | NA | 1 | N | 32-P-024-01 |  | E | N | 000 | N | 141
N32023 | 08 | 32 | 1" | N | 32023 | B-1 | N | 0 | NITROGEN CONNECTION | HCM32024 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.24A | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-02 |  | E | N | 000 | N | 140
N33001 | 08 | 32 | 3/4" | N | 33001 | B-1 | N | 0 | 32-P-3300A | N3538 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.25 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 140
N34007 | 08 | 32 | 1" | N | 34007 | 1CS2 | N | 0 | CD34018 | PR34019 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.26 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-01 |  | M | N | 000 | N | 166
N36015 | 08 | 32 | 1" | N | 36015 | B4S1 | N | 0 | TP-175 (CYLINDER 3, STAGE 1, PACKING 3, C94) | N36011 | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.28G | 2 | Art 4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | 148
N43001 | 08 | 32 | 1" | N | 43001 | B-1 | N | 0 | NITROGEN CONNECTION | PR43038 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.33 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-03 |  | E | N | 000 | N | 140
N6700Y | 08 | 32 | 1" | N | 6700Y | B-1 | N | 0 | N01001 | BDL60063 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
IA89027 | 08 | 32 | 2" | IA | 89027 | B-13 | N | 0 | IA62006 | IA89054 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89062 | 08 | 32 | 1" | IA | 89062 | B-13 | N | 0 | IA89027 | 32-IAM-105 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89075 | 08 | 32 | 1" | IA | 89075 | B-13 | N | 0 | IA62006 | TO 32-IAM-513 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89075 | 08 | 32 | 1-1/2" | IA | 89075 | B-13 | N | 0 | IA62006 | TO 32-IAM-513 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA68N32 | 08 | 32 | 1" | IA | 68N32 | B-13 | N | 0 | IA68K07 | IA68N33 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N42 | 08 | 32 | 1" | IA | 68N42 | B-13 | N | 0 | IA68N24 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68P10 | 08 | 32 | 1/2" | IA | 68P10 | B-13 | N | 0 | IA68P11 | IA68P11 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Q04 | 08 | 32 | 1" | IA | 68Q04 | B-13 | N | 0 | IA68C11 | IA68Q02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68Q09 | 08 | 32 | 1" | IA | 68Q09 | B-13 | N | 0 | IA68Q07 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68R02 | 08 | 45 | 3/4" | IA | 68R02 | B-13 | N | 0 | 20 LTR TANK | HEADER | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
IA68R04 | 08 | 45 | 1" | IA | 68R04 | B-13 | N | 0 | IA68R02 | 45-XV-6819A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-12 |  | - | N | 000 | - | 200
O12001 | 7A | 32 | 1" | O | 12001 | 1CS2 | P | 50 | O13011 | 32-D-1200A | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-022-01 |  | M | N | 110 | N | 235 | 23,25
O12001 | 7A | 32 | 1-1/2" | O | 12001 | 1CS2 | P | 50 | O13011 | 32-D-1200A | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-022-01 |  | M | N | 110 | N | 235 | 23,25
O15019 |  | 32 | 1/2" | O | 15019 | 1FS4 | ET | 30 | O15025 | O15020 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O31014 | 08 | 32 | 1-1/2" | O | 31014 | B4S2 | N | 0 | VZ31007 | O31016 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-01 |  | E | N | 110 | N | 225 | 23,25
O34001 |  | 32 | 1" | O | 34001 | 1CS2 | ET | 30 | O66038 | PR34025 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
O66013 |  | 32 | 3" | O | 66013 | B4S2 | HH | 30 | O66012 | 32-D-6600 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
P50011 |  | 32 | 12" | P | 50011 | 1CR9 | HB | 40 | 32-D-5001 | 32-A-5200 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-052-01 |  | F-4 | N | 141 | N | 435 | 16,10,18,13
LO32006 | 08 | 32 | 1-1/2" | LO | 32006 | QXB-55 | N | 0 | TP 20B (LO320114) | TP 19B (32-PK-3200 B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LO36003 | 08 | 32 | 1-1/2" | LO | 36003 | QXB-55 | N | 0 | TP-142 (LO360127) | TP-141 | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.28D | 2 | Art 4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 110 | N | 800
LS02001 |  | 32 | 3/4" | LS | 02001 | B-5 | HB | 60 | LS63177 | LS66002 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS02002 |  | 32 | 3/4" | LS | 02002 | B-5 | HB | 60 | LS02001 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS13012 |  | 32 | 1/2" | LS | 13012 | B-5 | HB | 60 | 32-P-1300 | LS13010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS14001 |  | 32 | 3/4" | LS | 14001 | B-5 | HB | 60 | 32-E-1400A | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
PN52015 |  | 32 | 20" | PN | 52015 | B4S2 | P | 100 | 32-D-5200 | 32-T-5200 | 0.5 | 120.0 | 0.2 | 100.0 |  | .55 | 26.46 | P | PROCESS NITROGEN | G | - | - | >1.5 | 100 | sh.37 | 2 | NA | NA | NA | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 142
PN52029 | 08 | 32 | 1-1/2" | PN | 52029 | 1CS2 | N | 0 | N52041 | N52041 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PP89011 | 08 | 32 | 8" | PP | 89011 | 5CS7 | N | 0 | TP-N51104 (D-8901) | 32-PK-8300 | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.68M | 1 | NA | NA | NA | NR | N | 32-P-082-07 |  | M | N | 110 | N | 443 | 6,25,23
PR24044 |  | 32 | 1-1/2" | PR | 24044 | D20S1 | P | 50 | PR24039 | PR24045 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR33032 | 08 | 32 | 1" | PR | 33032 | D20S1 | N | 0 | PR33019 | BDL33021 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR36028 | 08 | 32 | 1-1/2" | PR | 36028 | C42S1 | P | 50 | PR36039 | PR36022 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | G | Y | 141 | N | 353 | 10
PR36040 | 08 | 32 | 2" | PR | 36040 | B32S1 | P | 50 | PR36029 | PR36029 | 10.0/10.0 | -45.0/180.0 | 5.5 | 107.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 107 | sh.28B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-03 |  | G | Y | 141 | N | 357 | 10
PR72049 | 08 | 32 | 1" | PR | 72049 | C42S1 | N | 0 | 32-E-7201 | PR72014 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72060 | 08 | 32 | 1-1/2" | PR | 72060 | C42S1 | HA | 30 | TP-023 (PR720161) | BDL72072 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PR72060 | 08 | 32 | 2" | PR | 72060 | C42S1 | HA | 30 | TP-023 (PR720161) | BDL72072 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.52A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-007-04 |  | F | N | 141 | N | 347 | ,15
PW50025 |  | 32 | 1-1/2" | PW | 50025 | B4S2 | P | 50 | 32-T-5001 | 32-D-5202 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PW52017 | 08 | 32 | 3" | PW | 52017 | B4S2 | N | 0 | PW52013 | 32-D-5202 | 9.0 | 180.0 | 3.1 | 100.0 |  | 13.54 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 85 | 78
O66003 |  | 32 | 1-1/2" | O | 66003 | B4S2 | ET | 30 | O66023 | 32-D-6600 | 4.0 | 180.0 | 0.01/2.0 | 30.0/30.0 |  | 6.02 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.46 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-021-03 |  | E | N | 110 | N | 221
O66045 | 08 | 32 | 1/2" | O | 66045 | 1CS2 | N | 0 | O67010 | PX86032 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.65 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 235 | 23,25
P23016 | 7A | 32 | 1" | P | 23016 | 1FS4 | HB | 30 | P23018 | P23017 | 42.0/42.0 | -40.0/200.0 | 18.0 | 90.0 |  | 67.34 | 148.95 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.17 | 1 | Art 4.3 | NA | N | NR | N | 32-P-044-01 |  | G | N | 141 | N | 344 | ,10
P23032 | 08 | 32 | 3" | P | 23032 | C42S2 | HB | 30 | 32-R-2300 | BDL23069 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P31014 | 7A | 32 | 1/2" | P | 31014 | QXC25S2 | HB | 30 | P31016 | P31011 | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P31015 | 08 | 32 | 2" | P | 31015 | QXC25S2 | N | 0 | 32-Z-3100B | SP 3101 | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | II | MOD.A2 | Y | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
P31016 | 08 | 32 | 1/2" | P | 31016 | QXC25S2 | N | 0 | CD31004 | 32-Z-3100B | 25.0/25.0 | -40.0/190.0 | 18.0 | 90.0 |  | 39.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.23 | 1 | Art 4.3 | NA | N | NR | N | 32-P-047-01 |  | G-2 | N | 141 | N | 422 | ,10,6,11,13
PA62032 | 08 | 32 | 3/4" | PA | 62032 | B-1 | N | 0 | PA01001 | HEADER | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62039 | 08 | 32 | 1" | PA | 62039 | B-1 | N | 0 | PA01001 | PA02007 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62078 | 08 | 32 | 3/4" | PA | 62078 | B-1 | N | 0 | PA62077 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62079 | 08 | 32 | 3/4" | PA | 62079 | B-1 | N | 0 | PA62036 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
CWR89022 | 08 | 32 | 4" | CWR | 89022 | B-1 | N | 0 | TP-N20402 (32-E-8902) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68D | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89037 | 08 | 32 | 1-1/2" | CWR | 89037 | B-1 | N | 0 | TP-N20106 (32-E-8901) | CWR89026 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89037 | 08 | 32 | 4" | CWR | 89037 | B-1 | N | 0 | TP-N20106 (32-E-8901) | CWR89026 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68C | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR93005 | 08 | 32 | 3/4" | CWR | 93005 | B-1 | N | 0 | CWR93002 | VA93001 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.73 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWS01010 | 08 | 32 | 3" | CWS | 01010 | UGB-1PE | N | 0 | CWS01009 | CWS64001 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.2 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-01 |  | E | N | 000 | N | 15
CWS60413 | 08 | 32 | 3/4" | CWS | 60413 | B-1 | N | 0 | CWS64006 | 32-E-9004 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS64004 | 08 | 32 | 4" | CWS | 64004 | UGB-1PE | N | 0 | CWS01008 | CWS64005 | 7.5 | 80.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 3LPE | N | 32-U-021-02 |  | E | N | 000 | N | 15
CWS64005 | 08 | 32 | 2" | CWS | 64005 | B-1 | N | 0 | CWS64004 | 32-E-8000 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
WW64008 | 08 | 32 | 1-1/2" | WW | 64008 | B4S2 | N | 0 | FROM LC-23035 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
WW64013 | 08 | 32 | 1-1/2" | WW | 64013 | B4S2 | N | 0 | FROM LC-23036 | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 87
BDL00001 | 08 | 32 | 1" | BDL | 00001 | B32S1 | N | 0 | 32-AH-0001 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01003 | 08 | 32 | 1" | BDL | 01003 | B32S1 | N | 0 | PR24007 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01013 | 08 | 32 | 1/2" | BDL | 01013 | B32S1 | N | 0 | ET01001 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BU73055 | 08 | 32 | 1" | BU | 73055 | B32S1 | N | 0 | BU01001 | 32-S-7302A | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
BU73089 | 08 | 32 | 3/4" | BU | 73089 | D20S1 | N | 0 | 32-P-7300 | BU73050 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 153.15 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
CHWR15002 | 08 | 32 | 1/2" | CHWR | 15002 | B-1 | CF | 25 | JCHW14002 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR15002 | 08 | 32 | 1" | CHWR | 15002 | B-1 | CF | 25 | JCHW14002 | CHWR15006 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.9A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
FW68F30 | 08 | 32 | 1-1/2" | FW | 68F30 | B-13 | N | 0 | FW68R08 | DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F30 | 08 | 32 | 6" | FW | 68F30 | B-13 | N | 0 | FW68R08 | DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68G10 | 08 | 45 | 2" | FW | 68G10 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68G37 | 08 | 45 | 3" | FW | 68G37 | B-13 | N | 0 | FW68D05 | FW68G44 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68G41 | 08 | 45 | 1" | FW | 68G41 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68G41 | 08 | 45 | 3" | FW | 68G41 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
FW68G44 | 08 | 45 | 2" | FW | 68G44 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-06 |  | - | Y | 000 | - | 74
N67034 | 08 | 32 | 1/2" | N | 67034 | B-1 | N | 0 | N67039 | N14021 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N67037 | 08 | 32 | 1/2" | N | 67037 | B-1 | N | 0 | N67017 | LS63047 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-052-01 |  | E | N | 000 | N | 140
N67037 | 08 | 32 | 1" | N | 67037 | B-1 | N | 0 | N67017 | LS63047 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-052-01 |  | E | N | 000 | N | 140
N67055 | 08 | 32 | 1" | N | 67055 | B-1 | N | 0 | N67005 | N67002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-04 |  | E | N | 000 | N | 140
N67063 | 08 | 32 | 1/2" | N | 67063 | B-1 | N | 0 | N67017 | 32-D-5102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-04 |  | E | N | 000 | N | 140
N67066 | 08 | 32 | 1" | N | 67066 | B-1 | N | 0 | N67020 | 32-T-5200 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.38 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-052-02 |  | E | N | 000 | N | 140
N67084 | 08 | 32 | 3/4" | N | 67084 | B-1 | N | 0 | N67061 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
PR40022 | 08 | 32 | 3/4" | PR | 40022 | C42S1 | N | 0 | PR33023 | HCM40001 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR40022 | 08 | 32 | 1-1/2" | PR | 40022 | C42S1 | N | 0 | PR33023 | HCM40001 | 25.0/25.0 | -45.0/150.0 | 24.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 341 | 15
PR40032 |  | 32 | 1" | PR | 40032 | C42S1 | HB | 30 | PR40029 | BDL40025 | 25.0/25.0 | -45.0/150.0 | 20.0 | 40.0 |  | 37.5 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.30 | 1 | I | MOD.A | Y | 20 | N | 32-P-008-01 |  | G | N | 141 | N | 338 | 10
PR43027 |  | 32 | 3/4" | PR | 43027 | C42S1 | HB | 30 | PR43045 | 32AT 2401-3 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43027 |  | 32 | 1-1/2" | PR | 43027 | C42S1 | HB | 30 | PR43045 | 32AT 2401-3 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43027 |  | 32 | 2" | PR | 43027 | C42S1 | ET | 30 | PR43045 | 32AT 2401-3 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.33 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR43031 | 08 | 32 | 1" | PR | 43031 | C42S1 | N | 0 | 32-P-4300 | PR43032 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
HCM40001 | 08 | 32 | 1-1/2" | HCM | 40001 | C42S1 | N | 0 | ET71039 | 32-R-4001 | 40.0/40.0 | -45.0/150.0 | 20.0 | 40.0 |  | 60.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-049-01 |  | F | N | 141 | N | 326 | ,15
HCM40001 | 08 | 32 | 4" | HCM | 40001 | C42S1 | N | 0 | ET71039 | 32-R-4001 | 40.0/40.0 | -45.0/150.0 | 20.0 | 40.0 |  | 60.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 40 | sh.30 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-049-01 |  | F | N | 141 | N | 326 | ,15
PN52021 | 7A | 32 | 3/4" | PN | 52021 | 1CS2 | HB | 30 | PN52020 | 32-Z-5201A | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PN52021 | 7A | 32 | 20" | PN | 52021 | 1CS2 | HB | 40 | PN52020 | 32-Z-5201A | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
VA00063 | 08 | 32 | 4" | VA | 00063 | B-1 | N | 0 | 4111-ACW-SM-018 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00075 | 08 | 32 | 4" | VA | 00075 | B-1 | N | 0 | 4131-ACW-SM-015 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00078 | 08 | 32 | 4" | VA | 00078 | B-1 | N | 0 | 4131-SW-MH-004 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00083 | 08 | 32 | 4" | VA | 00083 | B-1 | N | 0 | 4221-ACW-SM-119 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA11006 | 08 | 32 | 3/4" | VA | 11006 | B4S2 | N | 0 | 32-D-1102 | VA11005 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.47 | 2 | NA | NA | NA | 6 | N | 32-P-020-01 |  | E | N | 000 | N | 183
VA11006 | 08 | 32 | 2" | VA | 11006 | B4S2 | N | 0 | 32-D-1102 | VA11005 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.47 | 2 | NA | NA | NA | 6 | N | 32-P-020-01 |  | E | N | 000 | N | 183
VA14006 | 08 | 32 | 2" | VA | 14006 | B4S2 | N | 0 | CHWS14015 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.8 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA21004 | 08 | 32 | 1-1/2" | VA | 21004 | B4S2 | N | 0 | 32-R-2100 | 32-R-2100 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.12 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA21004 | 08 | 32 | 4" | VA | 21004 | B4S2 | N | 0 | 32-R-2100 | 32-R-2100 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.12 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA23002 | 08 | 32 | 1/2" | VA | 23002 | B4S2 | N | 0 | LS63067 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.18 | 2 | NA | NA | NA | 6 | N | 32-U-052-01 |  | E | N | 000 | N | 183
VA40002 | 08 | 32 | 6" | VA | 40002 | B4S2 | N | 0 | TP-19 (32-D-4001) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.30B | 2 | NA | NA | NA | 6 | N | 32-P-049-03 |  | E | N | 000 | N | 183
VA40004 | 08 | 32 | 3" | VA | 40004 | B4S2 | P | 50 | TP-18 (LO400131) | FLAME ARRESTOR FA-4010 (LOOSE SUPPLY) | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.30B | 2 | NA | NA | NA | 6 | N | 32-P-049-03 |  | E | N | 000 | N | 183
SA81019 | 08 | 32 | 1" | SA | 81019 | 1CS2 | N | 0 | IA89015 | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
SWW92001 | 08 | 32 | 1" | SWW | 92001 | 1CS2 | N | 0 | 32-D-9005 | 32-P-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92001 | 08 | 32 | 6" | SWW | 92001 | 1CS2 | N | 0 | 32-D-9005 | 32-P-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92025 | 08 | 32 | 1-1/2" | SWW | 92025 | 1CS2 | N | 0 | SWW92011 | 32-H-9001A | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92033 | 08 | 32 | 2" | SWW | 92033 | 1CS2 | N | 0 | 32-S-9005 | WW92001 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
TEA10001 | 08 | 32 | 1" | TEA | 10001 | 3DS3 | N | 0 | 32-D-1001 | 32-D-1100 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA10007 | 08 | 32 | 1/2" | TEA | 10007 | 3DS3 | N | 0 | 32-D-1001 | FO10010 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA10007 | 08 | 32 | 1" | TEA | 10007 | 3DS3 | N | 0 | 32-D-1001 | FO10010 | 12.0 | 150.0 | 5.0 | 30.0 |  | 18.03 | 74.4 | IO | TEAL | L | - | - | <1.5 | 30 | sh.4 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 265 | 8,29
TEA11004 | 08 | 32 | 1/2" | TEA | 11004 | 3FS3 | N | 0 | 32-P-1100A | FO11015 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.47 | 1 | Art 4.3 | NA | N | NR | N | 32-P-020-01 |  | F | N | 343 | N | 266 | 8,29
FO11005 |  | 32 | 1" | FO | 11005 | B4S2 | ET | 30 | FO11004 | 32-D-1102 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-020-01 |  | E | N | 110 | N | 211 | 23,25
FO11009 | 08 | 32 | 1/2" | FO | 11009 | 1CS2 | N | 0 | FO11003 | TEA11009 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FW68A0H | 08 | 45 | 12" | FW | 68A0H | UGB-1PE | N | 0 | FW68A65 | FW68A66 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0H | 08 | 45 | 16" | FW | 68A0H | UGB-1PE | N | 0 | FW68A65 | FW68A66 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A10 | 08 | 45 | 18" | FW | 68A10 | PEB-69 | N | 0 | FW68A46 | FW68A67 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A15 | 08 | 45 | 6" | FW | 68A15 | PEB-69 | N | 0 | FW68A03 | FW68A0V | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A35 | 08 | 45 | 6" | FW | 68A35 | PEB-69 | N | 0 | FW68A20 | FW68A93 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
HCM23035 |  | 32 | 1-1/2" | HCM | 23035 | C42S1 | ST | 30 | HCM23018 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23052 |  | 32 | 1" | HCM | 23052 | 1FS4 | ST | 30 | HCM23050 | TP-5 (PR230100) | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23055 | 08 | 32 | 1/2" | HCM | 23055 | 1FS4 | N | 0 | P23022 | TP-11 (PR230112) | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23055 | 08 | 32 | 3/4" | HCM | 23055 | 1FS4 | N | 0 | P23022 | TP-11 (PR230112) | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23079 | 08 | 32 | 1" | HCM | 23079 | C42S1 | N | 0 | PR24043 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM32017 |  | 32 | 3/4" | HCM | 32017 | C42S1 | HB | 30 | VZ32002 | FO35015 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32020 |  | 32 | 2" | HCM | 32020 | C42S1 | HB | 40 | HCM32019 | PR31023 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-02 |  | G | Y | 141 | N | 351 | 10
HCM32027 |  | 32 | 3/4" | HCM | 32027 | C42S1 | HB | 30 | 32-E-3200 | HCM32029 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32027 |  | 32 | 1-1/2" | HCM | 32027 | C42S1 | HB | 30 | 32-E-3200 | HCM32029 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32027 |  | 32 | 3" | HCM | 32027 | C42S1 | HB | 30 | 32-E-3200 | HCM32029 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32036 | 08 | 32 | 2" | HCM | 32036 | C42S1 | HB | 40 | HCM32019 | BDL32030 | 43.5/43.5 | -45.0/150.0 | 40.0 | 120.0 |  | 65.26 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.24A | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-04 |  | G | Y | 141 | N | 351 | 10
CHWS61005 |  | 32 | 3/4" | CHWS | 61005 | B-1 | CF | 25 | CHWS61028 | CHWS14005 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
FO11002 | 08 | 32 | 1/2" | FO | 11002 | 3DS3 | N | 0 | 32-D-1100 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11006 |  | 32 | 3/4" | FO | 11006 | B4S2 | ET | 30 | FO11022 | 32-P-1101 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FO11008 | 08 | 32 | 1/2" | FO | 11008 | 1CS2 | N | 0 | FO11003 | TEA11210 | 10.0 | 100.0 | 6.0 | 40.0 |  | 15 | 28.5 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-02 |  | M | N | 110 | N | 215 | 23,25
FO11023 |  | 32 | 1" | FO | 11023 | B4S2 | ET | 30 | FO11007 | FO11022 | 6.0/5.0 | 150.0/180.0 | 0.5 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.47 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-02 |  | E | N | 110 | N | 211 | 23,25
FW68A0R | 08 | 45 | 6" | FW | 68A0R | UGB-1PE | N | 0 | FW68A57 | 45-HY-6809 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A22 | 08 | 45 | 12" | FW | 68A22 | B-7 | N | 0 | FW68A95 | FW68K08 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A63 | 08 | 45 | 6" | FW | 68A63 | PEB-69 | N | 0 | FW68A10 | FW68A0G | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A83 | 08 | 45 | 12" | FW | 68A83 | PEB-69 | N | 0 | FW68A46 | FW68A0N | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A90 | 08 | 45 | 6" | FW | 68A90 | UGB-1PE | N | 0 | FW68A04 | 45-HY-6801 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B08 | 08 | 45 | 6" | FW | 68B08 | PEB-69 | N | 0 | FW68A03 | FW68B0E | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B19 | 08 | 45 | 1-1/2" | FW | 68B19 | B-7 | N | 0 | FW68B27 | 45-HR-6808 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B64 | 08 | 45 | 12" | FW | 68B64 | B-7 | N | 0 | FW68B0U | FW68S13 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B93 | 08 | 45 | 8" | FW | 68B93 | UGB-1PE | N | 0 | FW68A53 | FW68A54 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B97 | 08 | 45 | 6" | FW | 68B97 | UGB-1PE | N | 0 | 45-HY-6812 | FW68B10 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68E06 | 08 | 32 | 2" | FW | 68E06 | B-7 | N | 0 | FW68E41 | FW68E13 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E09 | 08 | 32 | 2" | FW | 68E09 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E10 | 08 | 32 | 2" | FW | 68E10 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
IW64009 | 08 | 32 | 3/4" | IW | 64009 | B-1 | N | 0 | IW01001 | IW64008 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64027 | 08 | 32 | 3/4" | IW | 64027 | B-1 | N | 0 | IW64025 | 32-US-1121-07 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89021 | 08 | 32 | 3/4" | IW | 89021 | B-1 | N | 0 | IW89020 | US-..... | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW89042 | 08 | 32 | 3/4" | IW | 89042 | B-1 | N | 0 | IW89028 | PA89053 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
JCW86018 |  | 32 | 1-1/2" | JCW | 86018 | B-1 | HB | 30 | CWS86018 | CWR86014 | 7.5 | 80.0 | 5.0 | 26.0 |  | 11.25 | 29.4 | H | JACKET COOLING WATER | L | - | - | >1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-062-01 |  | E | N | 000 | N | 14
JLS23010 |  | 32 | 1" | JLS | 23010 | B-5 | HB | 50 | LS63070 | LS23022 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS23021 |  | 32 | 1/2" | JLS | 23021 | B-5 | HB | 40 | LS63140 | LS23033 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.15 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | E | N | 000 | N | 111 | 1
JLS31007 |  | 32 | 1" | JLS | 31007 | B-5 | HB | 50 | PR22011 | PR31015 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS31007 |  | 32 | 3" | JLS | 31007 | B-5 | HB | 50 | PR22011 | PR31015 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-008-01 |  | E | N | 000 | N | 111 | 1
JLS50005 |  | 32 | 18" | JLS | 50005 | B-5 | HB | 40 | LS50032 | LS50047 | 1.0/-1.0 | 280.0/280.0 | 0.5 | 110.0 |  | 1.61 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | N | 000 | N | 108
JLS50006 |  | 32 | 16" | JLS | 50006 | B-5 | HB | 40 | LS50033 | LS50035 | 1.0/-1.0 | 280.0/280.0 | 0.5 | 110.0 |  | 1.61 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 108
JLS61001 |  | 32 | 12" | JLS | 61001 | B-5 | HB | 60 | LS63049 | LS61001 | 6.9/-1.0 | 280.0/280.0 | 5.0 | 160.0 |  | 11.13 | 29.4 | H | STEAM LP JACKET | G | - | - | >1.5 | 160 | sh.42 | 2 | I | MOD.A | Y | 20 | N | 32-U-023-02 |  | E | N | 000 | N | 111 | 1
IA89063 | 08 | 32 | 1" | IA | 89063 | B-13 | N | 0 | IA89027 | 32-IAM-113 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA89067 | 08 | 32 | 1/2" | IA | 89067 | B-13 | N | 0 | IA62006 | TP-N30606 (32-E-8921A HEATING BARREL) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89068 | 08 | 32 | 3/4" | IA | 89068 | B-13 | N | 0 | IA620A0 | 32-IAT-073 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
IA89074 | 08 | 32 | 1" | IA | 89074 | B-13 | N | 0 | IA89075 | TO 32-IAM-512 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01B |  | - | N | 000 | - | 200
LPN10004 | 08 | 32 | 1/2" | LPN | 10004 | 3DS3 | N | 0 | LPN10001 | TEA10002 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN10016 | 08 | 32 | 1" | LPN | 10016 | 1C13 | N | 0 | LPN02001 | VA10001 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN10016 | 08 | 32 | 1-1/2" | LPN | 10016 | 1C13 | N | 0 | LPN02001 | VA10001 | 12.0 | 80.0 | 5.9/4.9 | 40.0/40.0 |  | 15.96 | 25.65 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 40 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-002-01 |  | E | N | 000 | N | 3203
LPN11004 | 08 | 32 | 2" | LPN | 11004 | 3DS3 | N | 0 | LPN11003 | 32-Z-1100 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LS23022 |  | 32 | 3/4" | LS | 23022 | B-5 | HB | 60 | JLS23010 | LC23021 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23027 | 08 | 32 | 1/2" | LS | 23027 | B-5 | HB | 60 | JLS23015 | LC23045 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.15A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS16001 |  | 32 | 3/4" | LS | 16001 | B-5 | HB | 60 | JLS16001 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.10 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23038 |  | 32 | 1" | LS | 23038 | B-5 | HB | 70 | JLS23010 | LC23056 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23049 |  | 32 | 1/2" | LS | 23049 | B-5 | HB | 60 | HCM23066 | LC23062 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.14 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31021 | 08 | 32 | 1" | LS | 31021 | B-5 | HB | 70 | PR31015 | LC31016 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31022 |  | 32 | 1" | LS | 31022 | B-5 | HB | 70 | JLS31009 | LC31017 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50005 |  | 32 | 3/4" | LS | 50005 | 3CS6 | HB | 30 | LS50002 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50005 |  | 32 | 8" | LS | 50005 | 3CS6 | HB | 40 | LS50002 | 32-D-5001 | 5.0/-1.0 | 200.0/160.0 | 0.5 | 110.0 |  | 8.02 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-050-01 |  | M | N | 000 | N | 94
LS50036 |  | 32 | 3/4" | LS | 50036 | B-5 | HB | 30 | LS50033 | 32-D-5200 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
LS51002 |  | 32 | 3/4" | LS | 51002 | B-5 | HB | 60 | 32-D-5100 | LC51008 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.36 | 2 | Art 4.3 | NA | N | NR | N | 32-P-050-04 |  | E | N | 000 | N | 90
LS52007 |  | 32 | 3/4" | LS | 52007 | B-5 | HB | 30 | 32-PK-8001 | LC52001 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-052-03 |  | E | N | 000 | N | 92
LS60011 |  | 32 | 1" | LS | 60011 | B-5 | HB | 70 | PURGE CONNECTION | BDL60040 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78A | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
LS60023 |  | 32 | 1" | LS | 60023 | B-5 | HB | 70 | PURGE CONNECTION | BDL60053 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.78B | 2 | Art 4.3 | NA | N | NR | N | 32-U-031-03 |  | E | N | 000 | N | 90
SA81017 | 08 | 32 | 8" | SA | 81017 | 1CS2 | N | 0 | 32-D-8106 | 32-PK-8102 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
O12005 | 7A | 32 | 1-1/2" | O | 12005 | 1CS2 | P | 50 | O13011 | 32-D-1200C | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-022-01 |  | M | N | 110 | N | 235 | 23,25
O13004 |  | 32 | 3/4" | O | 13004 | 1CS2 | ST | 30 | O13026 | 32-D-1400B | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13004 |  | 32 | 1" | O | 13004 | 1CS2 | ST | 30 | O13026 | 32-D-1400B | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O13016 |  | 32 | 1" | O | 13016 | 1CS2 | ET | 30 | 32-P-1301 | 32-S-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13019 |  | 32 | 1-1/2" | O | 13019 | 1CS2 | ET | 30 | O66040 | 32-D-1301 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13024 |  | 32 | 2" | O | 13024 | 1CS2 | ST | 30 | O13023 | O13021 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
O15001 |  | 32 | 1/2" | O | 15001 | 1FS4 | ET | 30 | O15002 | 32-D-1401A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O15001 |  | 32 | 3/4" | O | 15001 | 1FS4 | ET | 30 | O15002 | 32-D-1401A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
PA89027 | 08 | 32 | 3/4" | PA | 89027 | B-1 | N | 0 | PA89032 | 32-US-1211-07 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89038 | 08 | 32 | 3/4" | PA | 89038 | B-1 | N | 0 | PA01001 | IW89028 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89045 | 08 | 32 | 3/4" | PA | 89045 | B-1 | N | 0 | PA89021 | US-3211-04 EL.10000 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
CWS64006 | 08 | 32 | 8" | CWS | 64006 | B-1 | N | 0 | CWS01008 | HEADER | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.83 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
SWW92011 | 08 | 32 | 3" | SWW | 92011 | 1CS2 | N | 0 | SWW92005 | 32-H-9001A | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92013 | 08 | 32 | 1-1/2" | SWW | 92013 | 1CS2 | N | 0 | SWW92027 | 32-H-9001C | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92014 | 08 | 32 | 1-1/2" | SWW | 92014 | 1CS2 | N | 0 | SWW92005 | 32-H-9001D | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92015 | 08 | 32 | 1-1/2" | SWW | 92015 | 1CS2 | N | 0 | SWW92005 | 32-H-9001E | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92028 | 08 | 32 | 1-1/2" | SWW | 92028 | 1CS2 | N | 0 | SWW92014 | 32-H-9001D | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
TEA20001 |  | 32 | 1/2" | TEA | 20001 | 3FS3 | CF | 25 | DO12017 | 32-Z-2004 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.11 | 1 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | F | N | 343 | N | 266 | 8,29
VA00015 | 08 | 32 | 4" | VA | 00015 | B-1 | N | 0 | 3221-ACW-SM-102 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00021 | 08 | 32 | 4" | VA | 00021 | B-1 | N | 0 | 1231-ACW-SM-063 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
CHWR15007 |  | 32 | 1" | CHWR | 15007 | B-1 | CF | 25 | CAP | CHWS14005 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.7 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR51005 | 08 | 32 | 3" | CHWR | 51005 | B-1 | CF | 25 | TP-N11 (CHWR510108) | CHWR61015 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61016 |  | 32 | 2" | CHWR | 61016 | B-1 | CF | 25 | CHWR14002 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CT14004 |  | 32 | 1" | CT | 14004 | 3FS3 | JP | 0 | JCHW14002 | CT15003 | 20.0 | 190.0 | 10.0 | 6.0 |  | 31.64 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | A | N | 232 | N | 285 | 23,25
CT14004 | 08 | 32 | 1" | CT | 14004 | 3FS3 | N | 0 | JCHW14002 | CT15003 | 20.0 | 190.0 | 10.0 | 6.0 |  | 31.64 | 148.95 | IO | DRY CATALYST | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | NR | N | 32-P-026-03 |  | A | N | 232 | N | 285 | 23,25
N67094 | 08 | 32 | 3/4" | N | 67094 | B-1 | N | 0 | N67020 | BDL60043 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67106 | 08 | 32 | 1" | N | 67106 | B-1 | N | 0 | N67029 | BDL60047 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78B | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N80012 | 08 | 32 | 3/4" | N | 80012 | 1CS2 | N | 0 | N89008 | TP-034 (32-S-8001B) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80012 | 08 | 32 | 1" | N | 80012 | 1CS2 | N | 0 | N89008 | TP-034 (32-S-8001B) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N80022 | 08 | 32 | 3/4" | N | 80022 | 1CS2 | N | 0 | N67079 | 32-V-8001B | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.56 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01 |  | M | N | 000 | N | 166
N81031 | 08 | 32 | 2" | N | 81031 | 1CS2 | N | 0 | TP-002 (N81030) | TP-003 (KV-8035) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | I | MOD.A | Y | 5 | N | 32-P-060-01_B |  | M | N | 000 | N | 166
N81031 | 08 | 32 | 4" | N | 81031 | 1CS2 | N | 0 | TP-002 (N81030) | TP-003 (KV-8035) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | I | MOD.A | Y | 5 | N | 32-P-060-01_B |  | M | N | 000 | N | 166
N81044 | 08 | 32 | 1/2" | N | 81044 | 1CS2 | N | 0 | N89055 | 32-PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60A | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81052 | 08 | 32 | 1/2" | N | 81052 | 1CS2 | N | 0 | N81059 | PK-8102 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.59 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-01 |  | M | N | 000 | N | 166
N81056 | 08 | 32 | 1/2" | N | 81056 | 1CS2 | N | 0 | N89063 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N83002 | 08 | 32 | 3/4" | N | 83002 | 1CS2 | N | 0 | IA89053 | TP-205 (32-S-8300) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.63 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-094-01 |  | M | N | 000 | N | 166
N89012 | 08 | 32 | 3/4" | N | 89012 | B-1 | N | 0 | N89068 | 32-ZF-8108 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N89044 | 08 | 32 | 2" | N | 89044 | B-1 | N | 0 | N01001 | IW89028 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
PR43031 | 08 | 32 | 2" | PR | 43031 | C42S1 | N | 0 | 32-P-4300 | PR43032 | 40.5/40.5 | -45.0/150.0 | 30.0 | 53.0 |  | 60.76 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 53 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 350 | ,15
PR43049 | 08 | 32 | 1" | PR | 43049 | C42S1 | N | 0 | 32-T-4300 | BDL43018 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR43049 | 08 | 32 | 4" | PR | 43049 | C42S1 | N | 0 | 32-T-4300 | BDL43018 | 28.0/28.0 | -45.0/180.0 | 21.0 | 42.0 |  | 42.12 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 42 | sh.33 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | F | N | 141 | N | 348 | 15
PR50012 | 08 | 32 | 3/4" | PR | 50012 | B4S1 | N | 0 | PR50011 | BDL50002 | 5.0/-1.0 | 180.0/180.0 | 0.2 | 40.0 |  | 7.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.35 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-02 |  | C | N | 141 | N | 373 | ,10
PR51016 | 08 | 32 | 6" | PR | 51016 | B4S1 | N | 0 | PR51017 | PR50011 | 5.0/-1.0 | 180.0/180.0 | 0.2 | 40.0 |  | 7.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 40 | sh.36A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-050-03 |  | C | N | 141 | N | 373 | ,10
PR51019 | 08 | 32 | 2" | PR | 51019 | B4S1 | N | 0 | D-5110 (TP-N8) | 32-PSV-5160 (TP-N16) | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.36A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-03 |  | C | N | 141 | N | 370 | 10
PR53001 | 08 | 32 | 2" | PR | 53001 | B4S1 | P | 30 | TP-004, PR530119 | PR50010 | 7.0 | 250.0 | 0.7 | 230.0 |  | 10.96 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 230 | sh.39A | 1 | I | MOD.A | Y | 7 | N | 32-P-050-02 |  | C | N | 141 | N | 374 | 10
PP89008 | 08 | 32 | 14" | PP | 89008 | 5CS7 | N | 0 | TP-N50433 (A-8900, XV-8935) | 32-D-8007 | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.67 | 1 | NA | NA | NA | NR | N | 32-P-070-07 |  | M | N | 110 | N | 443 | 6,25,23
PR01003 | 08 | 32 | 3/4" | PR | 01003 | D20S1 | N | 0 | PR24007 | BDL01021 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR01003 | 08 | 32 | 1" | PR | 01003 | D20S1 | N | 0 | PR24007 | BDL01021 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR21009 |  | 32 | 3/4" | PR | 21009 | 1FS4 | CF | 25 | PR21010 | 32-AE-2101 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | II | MOD.A2 | Y | NR | N | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21009 |  | 32 | 1-1/2" | PR | 21009 | 1FS4 | CF | 25 | PR21010 | 32-AE-2101 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21009 |  | 32 | 4" | PR | 21009 | 1FS4 | CF | 25 | PR21010 | 32-AE-2101 | 55.0/55.0 | -40.0/150.0 | 40.0 | 20.0 |  | 82.62 | 148.95 | H | PROPYLENE | L | - | - | >1.5 | 20 | sh.12 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-02 |  | H | N | 141 | N | 331 | 15
PR21010 |  | 32 | 1-1/2" | PR | 21010 | D20S1 | HB | 30 | 32-E-2100 | PR21011 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR21010 |  | 32 | 3" | PR | 21010 | D20S1 | HB | 30 | 32-E-2100 | PR21011 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR22013 | 08 | 32 | 1/2" | PR | 22013 | D20S1 | N | 0 | PR22012 | SL21001 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.12 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-02 |  | F | N | 141 | N | 330 | 15
PR23006 |  | 32 | 1/2" | PR | 23006 | D20S1 | HB | 30 | PR23005 | HCM23018 | 45.0/45.0 | -45.0/250.0 | 38.0 | 120.0 |  | 70.45 | 153.15 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.17 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 339 | 10
PR23013 | 7A | 32 | 2" | PR | 23013 | 1FS4 | HB | 30 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.14 | 1 | III | MOD.G | Y | NR | Y | 32-P-044-01 |  | G | N | 141 | N | 337 | 10
PR23013 | 7A | 32 | 6" | PR | 23013 | 1FS4 | HB | 30 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.14 | 1 | III | MOD.G | Y | NR | Y | 32-P-044-01 |  | G | N | 141 | N | 337 | 10
PR24007 | 08 | 32 | 3/4" | PR | 24007 | D20S1 | N | 0 | HCM24082 | PPL80001 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR24007 | 08 | 32 | 1-1/2" | PR | 24007 | D20S1 | N | 0 | HCM24082 | PPL80001 | 50.0/50.0 | 80.0/-46.0 | 20.0 | 40.0 |  | 75 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-02 |  | F | N | 141 | N | 329 | 15
PR24032 |  | 32 | 1" | PR | 24032 | 1FS4 | JR | 0 | HCM24099 | BDL31025 | 55.0/55.0 | -40.0/200.0 | 35.0 | 78.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 78 | sh.20 | 1 | II | MOD.A2 | Y | 27 | N | 32-P-046-01 |  | A | N | 141 | N | 336 | 10
VA61001 | 08 | 32 | 6" | VA | 61001 | B4S2 | N | 0 | VA61005 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA61005 | 08 | 32 | 1-1/2" | VA | 61005 | B4S2 | N | 0 | 32-D-6100 | VA61001 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA61005 | 08 | 32 | 4" | VA | 61005 | B4S2 | N | 0 | 32-D-6100 | VA61001 | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA72002 | 08 | 32 | 2" | VA | 72002 | B4S2 | N | 0 | JWR72007 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.51 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA89015 | 08 | 32 | 12" | VA | 89015 | 4CS2 | N | 0 | TP-N11202 (32-H-8901) | 32-ZF-8108 | 0.5 | 80.0 | 0.05 | 60.0 |  | .55 | 25.65 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 60 | sh.68A | 2 | NA | NA | NA | NR | N | 32-P-070-01 |  | M | N | 000 | N | 180
VA00022 | 08 | 32 | 4" | VA | 00022 | B-1 | N | 0 | 1231-SW-MH-042 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00046 | 08 | 32 | 4" | VA | 00046 | B-1 | N | 0 | 2131-ACW-SM-071 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00053 | 08 | 32 | 4" | VA | 00053 | B-1 | N | 0 | 3221-ACW-SM-088 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00073 | 08 | 32 | 4" | VA | 00073 | B-1 | N | 0 | 2131-ACW-SM-074 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00079 | 08 | 32 | 4" | VA | 00079 | B-1 | N | 0 | 4221-ACW-SM-089 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00108 | 08 | 32 | 4" | VA | 00108 | B-1 | N | 0 | 2121-ACW-SM-128 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA11005 | 08 | 32 | 3" | VA | 11005 | B4S2 | N | 0 | VA11006 | To SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.47 | 2 | NA | NA | NA | 6 | N | 32-P-020-01 |  | E | N | 000 | N | 183
VA14008 | 08 | 32 | 1" | VA | 14008 | B4S2 | N | 0 | CHWR14005 | AT SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.7 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA20001 | 08 | 32 | 1" | VA | 20001 | B4S2 | N | 0 | CHWS20005 | TO BUCKET AT GROUND | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.11 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VA33003 | 08 | 32 | 3/4" | VA | 33003 | B-1 | N | 0 | TO ATMOSPHERE | 32-P-3300A | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.25 | 2 | NA | NA | NA | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 181
FW68A85 | 08 | 45 | 12" | FW | 68A85 | PEB-69 | N | 0 | FW68A46 | FW68A0M | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B02 | 08 | 45 | 20" | FW | 68B02 | PEB-69 | N | 0 | FW68A17 | IP-TCM/OFF-PIP-004 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | TP-FW-02 |  | - | N | 000 | - | 73 | 76
FW68B0N | 08 | 45 | 6" | FW | 68B0N | UGB-1PE | N | 0 | FW68B33 | FW68B34 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0Q | 08 | 45 | 6" | FW | 68B0Q | UGB-1PE | N | 0 | FW68B31 | 45-HY-6826 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0Y | 08 | 45 | 6" | FW | 68B0Y | UGB-1PE | N | 0 | FW68B89 | 45-HY-6820 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B20 | 08 | 45 | 1-1/2" | FW | 68B20 | B-7 | N | 0 | FW68B27 | 45-HR-6805 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B31 | 08 | 45 | 6" | FW | 68B31 | PEB-69 | N | 0 | FW68A10 | FW68B0Q | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B63 | 08 | 45 | 16" | FW | 68B63 | PEB-69 | N | 0 | FW68A17 | FW68B0U | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68E20 | 08 | 32 | 3/4" | FW | 68E20 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68H25 | 08 | 32 | 1" | FW | 68H25 | B-13 | N | 0 | FW68H23 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H55 | 08 | 32 | 1" | FW | 68H55 | B-13 | N | 0 | FW68H56 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68M32 | 08 | 32 | 1" | FW | 68M32 | B-13 | N | 0 | FW68M39 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68O06 | 08 | 32 | 2" | FW | 68O06 | B-13 | N | 0 | FW68O05 | FW68O08 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68O17 | 08 | 32 | 1" | FW | 68O17 | B-13 | N | 0 | FW68O15 | SPRAY NOZZLE | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
FW68R06 | 08 | 45 | 2" | FW | 68R06 | B-13 | N | 0 | 45-XV-6820A | To Water Drain | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
FW68R11 | 08 | 45 | 3/4" | FW | 68R11 | B-13 | N | 0 | 45-XV-6820A | FW68R10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68E26 | 08 | 32 | 3/4" | FW | 68E26 | B-7 | N | 0 | FW68E28 | FW68E17 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68F02 | 08 | 32 | 1/2" | FW | 68F02 | B-13 | N | 0 | FW68R06 | FW68R06 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
FW68F23 | 08 | 32 | 3/4" | FW | 68F23 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68H35 | 08 | 32 | 2" | FW | 68H35 | B-13 | N | 0 | FW68H34 | FW68H36 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I03 | 08 | 32 | 1" | FW | 68I03 | B-13 | N | 0 | MSN-003 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
JWR71002 | 08 | 32 | 3" | JWR | 71002 | C3S1 | N | 0 | 32-E-7102 | JWR71003 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWS33001 | 08 | 32 | 1" | JWS | 33001 | C3S1 | N | 0 | JWS64022 | 32-E-3300 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS64039 | 08 | 32 | 3/4" | JWS | 64039 | B-1 | N | 0 | JWS64056 | 32-E-6300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64046 | 08 | 32 | 1" | JWS | 64046 | B-1 | N | 0 | JWS64057 | OLIGOMER REMOVAL SYSTEM | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64053 | 08 | 32 | 10" | JWS | 64053 | B-1 | N | 0 | JWS64054 | JWS64061 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
LA16008 |  | 32 | 1-1/2" | LA | 16008 | 4CS2 | ET | 30 | LA16007 | LA16028 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16027 |  | 32 | 1/2" | LA | 16027 | 1FS4 | ET | 30 | LA16026 | 32-P-1600A | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA16027 |  | 32 | 1-1/2" | LA | 16027 | 1FS4 | ET | 30 | LA16026 | 32-P-1600A | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LC20002 |  | 32 | 1/2" | LC | 20002 | B-5 | HB | 30 | LS20001 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.11 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
JWR24006 | 08 | 32 | 3/4" | JWR | 24006 | D20S1 | N | 0 | 32-E-2400 | JWR24005 | 49.0/49.0 | -45.0/150.0 | 5.0 | 40.0 |  | 73.51 | 128.56 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.20 | 2 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 000 | N | 1021
JWR24006 | 08 | 32 | 6" | JWR | 24006 | D20S1 | N | 0 | 32-E-2400 | JWR24005 | 49.0/49.0 | -45.0/150.0 | 5.0 | 40.0 |  | 73.51 | 128.56 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.20 | 2 | II | MOD.A2 | Y | 1 | Y | 32-U-022-02 |  | M | N | 000 | N | 1021
JWR32001 | 08 | 32 | 2" | JWR | 32001 | C3S1 | N | 0 | 32-E-3200 | JWR32002 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.24 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR36001 | 08 | 32 | 4" | JWR | 36001 | B-1 | N | 0 | TP-150, (WR360140) | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40003 | 08 | 32 | 1-1/2" | JWR | 40003 | B-1 | N | 0 | 32-E-4001 | JWR64043 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR40003 | 08 | 32 | 14" | JWR | 40003 | B-1 | N | 0 | 32-E-4001 | JWR64043 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.30 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR50001 | 08 | 32 | 3/4" | JWR | 50001 | B-1 | N | 0 | 32-E-5001 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.35 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR51001 | 08 | 32 | 3/4" | JWR | 51001 | B-1 | N | 0 | TO E-5102 | JWR64046 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR51001 | 08 | 32 | 3" | JWR | 51001 | B-1 | N | 0 | TO E-5102 | JWR64046 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
IW64003 | 08 | 32 | 1" | IW | 64003 | B-1 | N | 0 | IW01001 | IW02001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64031 | 08 | 32 | 3/4" | IW | 64031 | B-1 | N | 0 | IW64025 | 32-US-1121-11 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64048 | 08 | 32 | 3/4" | IW | 64048 | B-1 | N | 0 | IW64046 | 32-US-1127-004 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64072 | 08 | 32 | 3/4" | IW | 64072 | B-1 | N | 0 | IW64003 | 32-US-1124-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
IW64075 | 08 | 32 | 3/4" | IW | 64075 | B-1 | N | 0 | IW64003 | 32-US-1115-001 | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-041-01 |  | E | N | 000 | N | 43
FW68G28 | 08 | 45 | 3" | FW | 68G28 | B-13 | N | 0 | FW68D06 | FW68G49 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68H27 | 08 | 32 | 1-1/2" | FW | 68H27 | B-13 | N | 0 | FW68H30 | FW68H26 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I06 | 08 | 32 | 1" | FW | 68I06 | B-13 | N | 0 | MSN-001 | MSN-001 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I12 | 08 | 32 | 3" | FW | 68I12 | B-13 | N | 0 | FW68I09 | FW68I03 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68K12 | 08 | 32 | 6" | FW | 68K12 | B-13 | N | 0 | XV6803A | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68M13 | 08 | 32 | 3" | FW | 68M13 | B-13 | N | 0 | FW68K06 | FW68M11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M24 | 08 | 32 | 1-1/2" | FW | 68M24 | B-13 | N | 0 | FW68M23 | MSN-005 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68O12 | 08 | 32 | 2" | FW | 68O12 | B-13 | N | 0 | FW68O13 | FW68O22 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | Y | 000 | - | 74
LS13010 |  | 32 | 3/4" | LS | 13010 | B-5 | HB | 60 | 32-S-1300 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.6 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23020 |  | 32 | 1/2" | LS | 23020 | B-5 | HB | 60 | JLS23009 | ACW | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.16 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS23028 |  | 32 | 1/2" | LS | 23028 | B-5 | HB | 60 | JLS23020 | LC23043 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.15 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS31023 | 08 | 32 | 1" | LS | 31023 | B-5 | HB | 70 | PR31015 | LC31018 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS50033 |  | 32 | 1-1/2" | LS | 50033 | B-5 | HB | 30 | LS50048 | LS50031 | 1.5/-1.0 | 250.0/130.0 | 0.5 | 110.0 |  | 2.35 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 110 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | N | 000 | N | 92
JWS64057 | 08 | 32 | 2" | JWS | 64057 | B-1 | N | 0 | JWS64054 | JWS23004 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64063 | 08 | 32 | 3/4" | JWS | 64063 | B-1 | N | 0 | JWS64062 | 32-Z-2400B | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64070 | 08 | 32 | 2" | JWS | 64070 | B-1 | N | 0 | 32-Z-6400 | Funnel | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
LS6300B |  | 32 | 3/4" | LS | 6300B | B-5 | HB | 60 | LS6300A | LC6300B | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300S |  | 32 | 1" | LS | 6300S | B-5 | HB | 70 | LS63178 | HOSE CONNECTION | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63015 |  | 32 | 1" | LS | 63015 | B-5 | HB | 70 | LS63014 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63059 |  | 32 | 1-1/2" | LS | 63059 | B-5 | HB | 70 | LS63183 | LS71010 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63067 |  | 32 | 3/4" | LS | 63067 | B-5 | HB | 60 | LS63199 | 32-E-2301 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63068 |  | 32 | 1" | LS | 63068 | B-5 | HB | 70 | LS63193 | PR31016 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63081 |  | 32 | 1" | LS | 63081 | B-5 | HB | 70 | LS63203 | US-XXXX-XX | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63189 |  | 32 | 2" | LS | 63189 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS63189 |  | 32 | 3" | LS | 63189 | B-5 | HB | 80 | LS01001 | HEADER | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.81A | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS73005 |  | 32 | 1/2" | LS | 73005 | B-5 | HB | 60 | JLS73005 | LC73006 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.55 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
O15013 |  | 32 | 1/2" | O | 15013 | 1CS2 | ET | 30 | 32-S-1500 | O15001 | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 236 | 23,25
O15021 |  | 32 | 1" | O | 15021 | 1FS4 | ET | 30 | O15007 | O15022 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-05 |  | M | N | 110 | N | 245 | 23,25
O20000 |  | 32 | 1/2" | O | 20000 | 1FS4 | ET | 30 | O15008 | DO20001 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-042-01 |  | M | N | 110 | N | 245 | 23,25
O20005 |  | 32 | 3/4" | O | 20005 | 1FS4 | ET | 30 | O15008 | 32-Z-2001A | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O65010 |  | 32 | 3/4" | O | 65010 | B4S2 | ET | 30 | 32-D-6500 | O65002 | 5.0 | 180.0 | 2.0/2.0 | 40.0/50.0 |  | 7.52 | 29.4 | IO | OIL | L | - | - | <1.5 | 40 | sh.45 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-031-01 |  | E | N | 110 | N | 225 | 23,25
P23017 | 08 | 32 | 1" | P | 23017 | C42S2 | HB | 30 | P23030 | P31008 | 42.0/42.0 | 150.0/-45.0 | 30.0 | 100.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 100 | sh.15A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G-2 | N | 141 | N | 522 | 10,6,11,38,39
P23021 |  | 32 | 12" | P | 23021 | C42S5 | HB | 40 | P23025 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 30.0 | 90.0 |  | 63.01 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.16 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 523 | 10,11,38
P40029 |  | 32 | 1/2" | P | 40029 | QXC25S2 | ST | 30 | 32-Z-4004A | P40040 | 25.0 | 150.0 | 18.0 | 90.0 |  | 37.55 | 74.4 | H | POLYMER+GAS | GS | - | - | >1.5 | 90 | sh.30 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-049-01 |  | G-2 | N | 141 | N | 420 | 6,11,10,13
P40045 |  | 32 | 1" | P | 40045 | C42S1 | HB | 30 | P40025 | P40041 | 20.0/20.0 | 120.0/-45.0 | 14.0 | 80.0 |  | 30 | 76.65 | H | POLYMER+GAS | GS | - | - | >1.5 | 80 | sh.31 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-049-01 |  | G | N | 141 | N | 424 | 10
PN52022 | 7A | 32 | 3/4" | PN | 52022 | 1CS2 | HB | 30 | PN52020 | 32-Z-5201B | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PJW23005 |  | 32 | 4" | PJW | 23005 | B-1 | HB | 30 | 32-P-2300 | 32-E-2301 | 9.0 | 180.0 | 4.5/6.5 | 80.0/100.0 |  | 13.54 | 29.4 | H | JACKET WATER(E2300/E4001) | L | - | - | >1.5 | 80 | sh.18 | 2 | I | MOD.A | Y | 20 | N | 32-P-044-04 |  | E | N | 000 | N | 86
PN52017 | 7A | 32 | 6" | PN | 52017 | 1CS2 | HA | 40 | PN52016 | 32-A-5200 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.37 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-01 |  | M | N | 000 | N | 152
PN52030 | 7A | 32 | 6" | PN | 52030 | 1CS2 | HB | 40 | PN52020 | VA52016 | 1.0 | 130.0 | 0.5/0.5 | 110.0/30.0 |  | 1.33 | 25.65 | P | PROCESS NITROGEN | G | - | - | >1.5 | 30 | sh.38 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-052-02 |  | M | N | 000 | N | 152
PP81003 | 08 | 32 | 16" | PP | 81003 | 5CS7 | N | 0 | 32-ZF-8108 | TP-N11201 (32-H-8901) | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.59 | 1 | III | MOD.G | Y | NR | N | 32-P-070-01 |  | M | N | 110 | N | 439 | 6,23,25
PP83004 | 08 | 32 | 6" | PP | 83004 | 5CS7 | N | 0 | 32-PK-8300 | PP81003 | 1.0 | 100.0 | 0.2 | 80.0 |  | 1.5 | 28.5 | H | POLYMER | GS | - | - | >1.5 | 80 | sh.63 | 1 | II | MOD.A2 | Y | NR | N | 32-P-070-01 |  | M | N | 110 | N | 439 | 6,23,25
PP83005 | 08 | 32 | 8" | PP | 83005 | 5CS7 | N | 0 | 32-PK-8300 | COLLECTING BOX (GROUND LEVEL) (BY CLIENT) TO BE GROUNDED | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.63 | 1 | NA | NA | NA | NR | N | 32-P-082-07 |  | M | N | 110 | N | 443 | 6,25,23
PP89007 | 08 | 32 | 14" | PP | 89007 | 5CS7 | N | 0 | TP-N50423 (A-8900, XV-8934) | COLLECTING BOX AT GROUND FLOOR | 0.5 | 100.0 | 0.2 | 80.0 |  | .75 | 28.5 | H | POLYMER | S | - | - | <1.5 | 80 | sh.68M | 1 | NA | NA | NA | NR | N | 32-P-070-07 |  | M | N | 110 | N | 443 | 6,25,23
PR23008 | 7A | 32 | 2" | PR | 23008 | 1FS4 | HB | 30 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.14 | 1 | III | MOD.G | Y | NR | Y | 32-P-044-01 |  | G | N | 141 | N | 337 | 10
PR23008 | 7A | 32 | 6" | PR | 23008 | 1FS4 | HB | 30 | 32-R-2300 | 32-R-2300 | 42.0/42.0 | -40.0/150.0 | 30.0 | 80.0 |  | 63.09 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.14 | 1 | III | MOD.G | Y | NR | Y | 32-P-044-01 |  | G | N | 141 | N | 337 | 10
PR24040 |  | 32 | 3/4" | PR | 24040 | D20S1 | P | 50 | PR24039 | PR24041 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR31021 |  | 32 | 2" | PR | 31021 | D20S1 | HB | 30 | 32-S-3100 | PR31020 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 141.72 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
PR33007 |  | 32 | 3/4" | PR | 33007 | C42S1 | HA | 30 | 32-E-3301 | 32-D-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33011 | 08 | 32 | 3/4" | PR | 33011 | C42S1 | N | 0 | 32-P-3300B | PR33010 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33011 | 08 | 32 | 1" | PR | 33011 | C42S1 | N | 0 | 32-P-3300B | PR33010 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR36015 |  | 32 | 4" | PR | 36015 | C42S1 | P | 50 | PR36013 | 32-E-4301 | 28.0/28.0 | -45.0/150.0 | 20.0 | 120.0 |  | 42 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 120 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-047-03 |  | G | Y | 141 | N | 353 | 10
VA00031 | 08 | 32 | 4" | VA | 00031 | B-1 | N | 0 | 2121-ACW-SM-121 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00040 | 08 | 32 | 4" | VA | 00040 | B-1 | N | 0 | 2131-ACW-SM-060A | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00069 | 08 | 32 | 4" | VA | 00069 | B-1 | N | 0 | 4121-ACW-SM-013 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00070 | 08 | 32 | 4" | VA | 00070 | B-1 | N | 0 | 4121-ACW-SM-020 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00076 | 08 | 32 | 4" | VA | 00076 | B-1 | N | 0 | 4131-ACW-SM-024 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00093 | 08 | 32 | 4" | VA | 00093 | B-1 | N | 0 | 6112-SW-DM-002 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA24012 | 08 | 32 | 1" | VA | 24012 | B4S2 | N | 0 | TP-15 (VA240116) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.21A | 2 | NA | NA | NA | 6 | N | 32-P-045-03 |  | E | N | 000 | N | 183
VA50005 | 08 | 32 | 1" | VA | 50005 | B4S2 | N | 0 | JWR50001 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.35 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA52012 | 08 | 32 | 10" | VA | 52012 | B4S2 | N | 0 | PN52025 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA52012 | 08 | 32 | 18" | VA | 52012 | B4S2 | N | 0 | PN52025 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
DO12013 | 08 | 32 | 3/4" | DO | 12013 | 1CS2 | N | 0 | 32-S-1200B | N12020 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-024-01 |  | M | N | 220 | N | 270 | 23,25
DW69A11 | 08 | 32 | 1-1/2" | DW | 69A11 | B-13 | IS | 50 | DW01001 | 32-ES-6903 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
DW69B05 | 08 | 32 | 3" | DW | 69B05 | B-13 | N | 0 | DW01001 | BLIND FLANGE | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.90 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-045-01 |  | - | N | 000 | - | 22
ET71053 |  | 32 | 4" | ET | 71053 | C3S1 | HB | 30 | 32-E-7100 | 32-E-7101 | 38.3 | 250.0 | 32.6/32.6 | 50.0/100.0 |  | 59.96 | 76.65 | H | ETHYLENE | G | - | - | >1.5 | 50 | sh.48 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-006-02 |  | C | N | 041 | N | 316 | ,10
FL01001 | 08 | 32 | 1" | FL | 01001 | B32S1 | N | 0 | FL60002 | NF050016 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
FL01001 | 08 | 32 | 24" | FL | 01001 | B32S1 | N | 0 | FL60002 | NF050016 | 3.5/3.5 | -45.0/120.0 | 1.0/0.1 | 100.0/100.0 |  | 4.66 | 26.46 | P | VENT TO FLARE | G | - | - | >1.5 | 100 | sh.1 | 1 | III | MOD.G | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 490 | 10
N89071 | 08 | 32 | 3/4" | N | 89071 | B-1 | N | 0 | N01001 | N80011 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
FW68A69 | 08 | 45 | 6" | FW | 68A69 | PEB-69 | N | 0 | FW68A17 | FW68A0P | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68A80 | 08 | 45 | 1-1/2" | FW | 68A80 | B-13 | N | 0 | FW68A26 | 45-HR-6860 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-04 |  | - | Y | 000 | - | 74
FW68A84 | 08 | 45 | 10" | FW | 68A84 | B-7 | N | 0 | FW68A0N | FW68S09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A95 | 08 | 45 | 16" | FW | 68A95 | UGB-1PE | N | 0 | FW68A21 | FW68A22 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
PR53005 | 08 | 32 | 1-1/2" | PR | 53005 | B4S1 | N | 0 | PR53004 | OG53003 | 7.0 | 190.0 | 5.0/5.0 | 60.0/35.0 |  | 10.54 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 35 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-01 |  | C | N | 141 | N | 370 | 10
PR61004 | 08 | 32 | 1" | PR | 61004 | C42S1 | N | 0 | TP-008 (32-E-6101) | TP-019 (32-PSV-6177) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61004 | 08 | 32 | 3" | PR | 61004 | C42S1 | N | 0 | TP-008 (32-E-6101) | TP-019 (32-PSV-6177) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR72005 |  | 32 | 3/4" | PR | 72005 | C42S1 | ST | 30 | PR72028 | 32-D-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72005 |  | 32 | 1-1/2" | PR | 72005 | C42S1 | ST | 30 | PR72028 | 32-D-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72011 | 08 | 32 | 1" | PR | 72011 | C42S1 | N | 0 | 32-E-7202 | 32-T-7201 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PW50020 |  | 32 | 1" | PW | 50020 | B4S2 | HB | 30 | 32-T-5001 | 32-P-5001 | 5.0 | 180.0 | 0.2 | 100.0 |  | 7.52 | 29.4 | H | PROCESS WATER | L | - | - | >1.5 | 100 | sh.35 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-02 |  | E | N | 000 | N | 30
PR24032 |  | 32 | 1-1/2" | PR | 24032 | 1FS4 | JR | 0 | HCM24099 | BDL31025 | 55.0/55.0 | -40.0/200.0 | 35.0 | 78.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 78 | sh.20 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-046-01 |  | A | N | 141 | N | 336 | 10
PR24032 |  | 32 | 2" | PR | 24032 | 1FS4 | JR | 0 | HCM24099 | BDL31025 | 55.0/55.0 | -40.0/200.0 | 35.0 | 78.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 78 | sh.20 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-046-01 |  | A | N | 141 | N | 336 | 10
PR24034 | 08 | 32 | 3/4" | PR | 24034 | C42S1 | N | 0 | 32-E-2404 | P23022 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24034 | 08 | 32 | 4" | PR | 24034 | C42S1 | N | 0 | 32-E-2404 | P23022 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
PR24046 |  | 32 | 1-1/2" | PR | 24046 | D20S1 | P | 50 | PR24039 | PR24047 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 153.15 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 330 | 15
PR31023 | 08 | 32 | 1-1/2" | PR | 31023 | 1FS4 | N | 0 | HCM32020 | PR31015 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-008-01 |  | A | N | 141 | N | 335 | 10
PR31024 | 7A | 32 | 1-1/2" | PR | 31024 | 1FS4 | HB | 30 | PR31015 | JLS31006 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-047-01 |  | A | N | 141 | N | 335 | 10
PR31024 | 08 | 32 | 1-1/2" | PR | 31024 | 1FS4 | N | 0 | PR31015 | JLS31006 | 55.0/55.0 | -40.0/200.0 | 45.0 | 60.0 |  | 88.18 | 148.95 | H | PROPYLENE | G | - | - | >1.5 | 60 | sh.23 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-047-01 |  | A | N | 141 | N | 335 | 10
PR33010 | 08 | 32 | 1" | PR | 33010 | C42S1 | N | 0 | 32-P-3300A | 32-D-3300 | 25.0/25.0 | -45.0/120.0 | 18.0 | 45.0 |  | 37.5 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 45 | sh.25 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 342 | 15
PR33016 | 08 | 32 | 1" | PR | 33016 | D20S1 | N | 0 | PR33015 | 32-P-3300A | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33016 | 08 | 32 | 10" | PR | 33016 | D20S1 | N | 0 | PR33015 | 32-P-3300A | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33018 | 08 | 32 | 3/4" | PR | 33018 | D20S1 | N | 0 | PR33017 | 32-P-3300B | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33018 | 08 | 32 | 8" | PR | 33018 | D20S1 | N | 0 | PR33017 | 32-P-3300B | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 111.34 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33020 | 08 | 32 | 1/2" | PR | 33020 | D20S1 | N | 0 | 32-P-3300B | PR33025 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33020 | 08 | 32 | 1-1/2" | PR | 33020 | D20S1 | N | 0 | 32-P-3300B | PR33025 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33022 | 08 | 32 | 3/4" | PR | 33022 | D20S1 | N | 0 | PR33019 | PR33021 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | N | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
PR33022 | 08 | 32 | 6" | PR | 33022 | D20S1 | N | 0 | PR33019 | PR33021 | 55.0/55.0/42.5 | -45.0/120.0/-45.0 | 42.0/25.0 | 45.0/60.0 |  | 82.5 | 128.56 | H | PROPYLENE | L | - | - | >1.5 | 45 | sh.25 | 1 | III | MOD.G | Y | 1 | Y | 32-P-008-01 |  | F | N | 141 | N | 346 | 15
VA43010 | 08 | 32 | 1/2" | VA | 43010 | B4S2 | N | 0 | LS43010 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.33 | 2 | NA | NA | NA | 6 | N | 32-P-047-03 |  | E | N | 000 | N | 183
JWR63003 | 08 | 32 | 1-1/2" | JWR | 63003 | B-1 | N | 0 | JWR63002 | JWR64044 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64001 | 08 | 32 | 1" | JWR | 64001 | B-1 | N | 0 | 32-D-6400 | JWR64042 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64005 | 08 | 32 | 1-1/2" | JWR | 64005 | B-1 | N | 0 | JWR64006 | 32-E-6400A | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64005 | 08 | 32 | 20" | JWR | 64005 | B-1 | N | 0 | JWR64006 | 32-E-6400A | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR64007 | 08 | 32 | 20" | JWR | 64007 | B-1 | N | 0 | JWR64006 | 32-E-6400B | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR71006 | 08 | 32 | 1" | JWR | 71006 | C3S1 | N | 0 | JWR71002 | VA71005 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 44.0 |  | 45.61 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 44 | sh.48 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 1011
JWR72005 | 08 | 32 | 3/4" | JWR | 72005 | C42S1 | N | 0 | 32-E-7200 | JWR72001 | 33.7/33.7 | 150.0/-45.0 | 3.0 | 46.0 |  | 50.56 | 76.65 | H | JACKET WATER RETURN | L | - | - | >1.5 | 46 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-U-022-02 |  | M | N | 141 | N | 1033
JWR72007 | 08 | 32 | 1" | JWR | 72007 | D20S1 | N | 0 | JWR72004 | VA72002 | 33.7/33.7 | 245.0/-45.0 | 5.0 | 40.0 |  | 52.54 | 153.15 | H | JACKET WATER RETURN | L | - | - | >1.5 | 40 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-022-02 |  | M | N | 141 | N | 1031
JWS23003 | 08 | 32 | 3" | JWS | 23003 | B-1 | N | 0 | JWS64047 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS23003 | 08 | 32 | 6" | JWS | 23003 | B-1 | N | 0 | JWS64047 | JWS64047 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
FO10011 | 08 | 32 | 1" | FO | 10011 | 3DS3 | N | 0 | VG15B09 | FO11005 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO11016 | 08 | 32 | 1/2" | FO | 11016 | 3DS3 | N | 0 | TEA11011 | FO10011 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.47 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 220 | 8,23,29,25
FO20002 | 08 | 32 | 1/2" | FO | 20002 | B4S2 | N | 0 | TEA11006 | FO20001 | 6.0 | 100.0 | 3.0 | 30.0 |  | 9 | 29.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-031-02 |  | E | N | 110 | N | 212 | 23,25
FW68A0I | 08 | 45 | 12" | FW | 68A0I | UGB-1PE | N | 0 | FW68A67 | FW68A68 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A0N | 08 | 45 | 10" | FW | 68A0N | UGB-1PE | N | 0 | FW68A83 | FW68A84 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68A38 | 08 | 45 | 4" | FW | 68A38 | B-7 | N | 0 | FW68A0Q | FW68A0F | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A40 | 08 | 45 | 1-1/2" | FW | 68A40 | B-7 | N | 0 | 45-HR-6801 | FW68A38 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A51 | 08 | 45 | 6" | FW | 68A51 | PEB-69 | N | 0 | FW68A46 | FW68A0L | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
CWR86011 |  | 32 | 1" | CWR | 86011 | B-1 | HB | 30 | CWR86001 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86011 |  | 32 | 2" | CWR | 86011 | B-1 | HB | 30 | CWR86001 | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR89009 | 08 | 32 | 14" | CWR | 89009 | B-1 | N | 0 | TP-N50904 (E-8900A) | CWR89010 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68O | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWS86021 | 08 | 32 | 1/2" | CWS | 86021 | B-1 | N | 0 | CWS86016 | JCW86016 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89041 | 08 | 32 | 16" | CWS | 89041 | B-1 | N | 0 | CWS64010 | TP-N50903 (E-8900A) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
LC31043 |  | 32 | 3/4" | LC | 31043 | B-5 | HB | 30 | LS31042 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50003 |  | 32 | 1/2" | LC | 50003 | B-5 | HB | 30 | LS50046 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50013 |  | 32 | 3/4" | LC | 50013 | B-5 | HB | 30 | LS50045 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | Y | 000 | N | 130
LC51007 |  | 32 | 3/4" | LC | 51007 | B-5 | HB | 30 | LS51003 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC52006 |  | 32 | 3/4" | LC | 52006 | B-5 | HB | 30 | LS52008 | WW52010 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC63001 |  | 32 | 4" | LC | 63001 | B-5 | P | 50 | LC63092 | LC63104 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63090 |  | 32 | 3/4" | LC | 63090 | B-5 | HB | 30 | LS63198 | LC63091 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63093 |  | 32 | 1" | LC | 63093 | B-5 | HB | 40 | HEADER | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC72005 |  | 32 | 1" | LC | 72005 | B-5 | HB | 40 | LS72003 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.51 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC89049 |  | 32 | 3/4" | LC | 89049 | B-5 | HB | 30 | LS89059 | Funnel | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.85A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
JWS23004 | 08 | 32 | 3/4" | JWS | 23004 | B-1 | N | 0 | JWS64057 | 32-E-2350 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS24012 | 08 | 32 | 6" | JWS | 24012 | B-1 | N | 0 | JWS64049 | JWS64049 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.19 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
HCM23043 |  | 32 | 4" | HCM | 23043 | C42S1 | HB | 40 | HCM23003 | HCM24084 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23048 |  | 32 | 1-1/2" | HCM | 23048 | 1FS4 | JP | 0 | JLS23008 | JLS23008 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.16 | 1 | II | MOD.A2 | Y | 27 | Y | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM23082 | 08 | 32 | 1/2" | HCM | 23082 | 1FS4 | N | 0 | JLS23021 | HCM23083 | 55.0/55.0 | -40.0/200.0 | 30.0 | 100.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-044-01 |  | A | N | 141 | N | 333 | 10
HCM24052 |  | 32 | 3" | HCM | 24052 | D20S1 | P | 50 | HCM24077 | BDL24080 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24055 | 08 | 32 | 1-1/2" | HCM | 24055 | 3FS4 | N | 0 | HCM24064 | OG01004 | 42.0/42.0 | -40.0/150.0 | 31.0/4.0 | 20.0/70.0 |  | 63.09 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 20 | sh.19 | 1 | II | MOD.A2 | Y | 5 | N | 32-U-034-01 |  | H | N | 141 | N | 367 | 15,36,5
FW68R19 | 08 | 45 | 3/4" | FW | 68R19 | B-13 | N | 0 | 45-XV-6824A | FW68R10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
HCM23056 |  | 32 | 1/2" | HCM | 23056 | 1FS4 | HB | 30 | P23023 | P23024 | 55.0/55.0 | 200.0/-40.0 | 40.0 | 120.0 |  | 88.18 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.16 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-044-01 |  | G | N | 141 | N | 332 | 10
HCM23086 |  | 32 | 1/2" | HCM | 23086 | D20S1 | HB | 30 | HCM23083 | 32-HV-2303C | 55.0/55.0 | 280.0/-45.0 | 30.0 | 100.0 |  | 88.69 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 100 | sh.15 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-044-01 |  | G | N | 141 | N | 321 | 10
HCM24084 |  | 32 | 4" | HCM | 24084 | D20S1 | P | 50 | HCM24085 | PR24039 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 150.8 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM24086 |  | 32 | 1" | HCM | 24086 | D20S1 | P | 50 | HCM43001 | HCM24085 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 153.15 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | Art 4.3 | NA | N | 1 | N | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM32025 |  | 32 | 1" | HCM | 32025 | C42S1 | HB | 30 | HCM32026 | BDL32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
IA02008 | 08 | 32 | 1" | IA | 02008 | B-13 | N | 0 | IA02002 | 32-IAM-047 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
LC23026 |  | 32 | 1/2" | LC | 23026 | B-5 | HB | 30 | LS23026 | LC31017 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.14 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23033 |  | 32 | 1/2" | LC | 23033 | B-5 | HB | 30 | LS23014 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.17 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23041 |  | 32 | 3/4" | LC | 23041 | B-5 | HB | 30 | LS23022 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23048 |  | 32 | 1/2" | LC | 23048 | B-5 | HB | 30 | LS23034 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.17 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC23061 |  | 32 | 1" | LC | 23061 | B-5 | HB | 40 | LS630AM | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.16 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31030 |  | 32 | 1/2" | LC | 31030 | B-5 | HB | 30 | LS31031 | ACW | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC31032 |  | 32 | 1/2" | LC | 31032 | B-5 | P | 50 | LS31034 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31034 | 08 | 32 | 1" | LC | 31034 | B-5 | P | 50 | LS31039 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50008 |  | 32 | 1" | LC | 50008 | B-5 | P | 50 | P50015 | TO TRENCH | 3.5 | 280.0 | 0.01 | 120.0 |  | 5.64 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 120 | sh.34 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-050-01 |  | E | Y | 000 | N | 133 | 77
N01003 | 08 | 32 | 1" | N | 01003 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | PR01002 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-007-01 |  | E | N | 000 | N | 140
N01011 | 08 | 32 | 1" | N | 01011 | B-1 | N | 0 | NITROGEN CONNECTION OF NEAREST UTILITY STATION SHALL BE UTILIZED. | OG00A01 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.1 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-034-01 |  | E | N | 000 | N | 140
N12025 | 08 | 32 | 1/2" | N | 12025 | 1CS2 | N | 0 | N67058 | N12030 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.5 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-024-01 |  | M | N | 000 | N | 166
BDL01001 | 08 | 32 | 3" | BDL | 01001 | B32S1 | N | 0 | OG01004 | BDL01009 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL23052 | 08 | 32 | 3/4" | BDL | 23052 | B32S1 | N | 0 | BDL23064 | BDL24097 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78A | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
PA62046 | 08 | 32 | 3/4" | PA | 62046 | B-1 | N | 0 | PA62045 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62065 | 08 | 32 | 3/4" | PA | 62065 | B-1 | N | 0 | PA62071 | HOSE CONNECTION | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA62084 | 08 | 32 | 3/4" | PA | 62084 | B-1 | N | 0 | PA01001 | 32-US-1111-002 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89034 | 08 | 32 | 3/4" | PA | 89034 | B-1 | N | 0 | PA01001 | IW89027 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89040 | 08 | 32 | 3/4" | PA | 89040 | B-1 | N | 0 | PA01001 | 32-PK-8700 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89054 |  | 32 | 3/4" | PA | 89054 | B-1 | HA | 30 | PA89038 | PA89050 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.85A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PR40027 |  | 32 | 1" | PR | 40027 | C42S1 | ST | 30 | PR40028 | PR40023 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR40027 |  | 32 | 1-1/2" | PR | 40027 | C42S1 | ST | 30 | PR40028 | PR40023 | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR40035 |  | 32 | 1" | PR | 40035 | C42S1 | ST | 30 | HN40002 | TP-5 (PR400100) | 28.0/28.0 | -45.0/180.0 | 20.0/20.0 | 25.0/10.0 |  | 42.12 | 76.65 | H | PROPYLENE | G | - | - | >1.5 | 10 | sh.30 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | G | N | 141 | N | 359 | 10
PR72014 | 08 | 32 | 1" | PR | 72014 | C42S1 | N | 0 | 32-T-7201 | 32-E-7202 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72026 | 08 | 32 | 1-1/2" | PR | 72026 | C42S1 | N | 0 | 32-T-7203 | DRAIN | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.53 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-03 |  | F | N | 141 | N | 347 | ,15
PX86025 | 08 | 32 | 1/2" | PX | 86025 | QXC25S1 | N | 0 | PX86027 | JCW86017 | 10.0 | 100.0 | 3.0 | 20.0 |  | 15 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | A | N | 1X4 | N | 606 | 7
PX86036 | 08 | 32 | 1/2" | PX | 86036 | QXC25S1 | N | 0 | PX86035 | 32-D-8600 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
PX86036 | 08 | 32 | 2" | PX | 86036 | QXC25S1 | N | 0 | PX86035 | 32-D-8600 | 10.0 | 180.0 | 3.0/0.0 | 20.0/36.0 |  | 15.61 | 74.4 | H | PEROXIDE | L | - | - | <1.5 | 20 | sh.65 | 1 | Art 4.3 | NA | N | NR | N | 32-P-062-01 |  | M | N | 1X4 | N | 605 | 7
SA81020 | 08 | 32 | 4" | SA | 81020 | 1CS2 | N | 0 | UN LOADING | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
SA81020 | 08 | 32 | 6" | SA | 81020 | 1CS2 | N | 0 | UN LOADING | 32-D-8106 | 1.0 | 120.0 | 0.05 | 40.0 |  | 1.5 | 28.5 | H | SOLID ADDITIVE | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 406 | 6,10,23,25
VA52013 | 08 | 32 | 3" | VA | 52013 | B4S2 | N | 0 | N52043 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.38 | 2 | NA | NA | NA | 6 | N | 32-P-052-02 |  | E | N | 000 | N | 183
VA61006 | 08 | 32 | 1" | VA | 61006 | B4S2 | N | 0 | CHWS61030 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42E | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA62003 | 08 | 32 | 4" | VA | 62003 | B4S2 | N | 0 | IA62092 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.43 | 2 | NA | NA | NA | 6 | N | 32-U-094-01 |  | E | N | 000 | N | 183
VA63001 | 08 | 32 | 1" | VA | 63001 | B4S2 | N | 0 | JWS63002 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.87 | 2 | NA | NA | NA | 6 | N | 32-U-022-01 |  | E | N | 000 | N | 183
VA64006 | 08 | 32 | 1" | VA | 64006 | B4S2 | N | 0 | JWS64003 | SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.44 | 2 | NA | NA | NA | 6 | N | 32-U-022-01 |  | E | N | 000 | N | 183
VA71005 | 08 | 32 | 2" | VA | 71005 | B4S2 | N | 0 | JWR71006 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.48 | 2 | NA | NA | NA | 6 | N | 32-U-022-02 |  | E | N | 000 | N | 183
VA72004 | 08 | 32 | 1" | VA | 72004 | B4S2 | N | 0 | TP-026 (LS720156) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.52A | 2 | NA | NA | NA | 6 | N | 32-P-007-04 |  | E | N | 000 | N | 183
FW68B0C | 08 | 45 | 6" | FW | 68B0C | UGB-1PE | N | 0 | FW68B04 | 45-HY-6813 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0L | 08 | 45 | 8" | FW | 68B0L | UGB-1PE | N | 0 | FW68B39 | FW68B40 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0U | 08 | 45 | 16" | FW | 68B0U | UGB-1PE | N | 0 | FW68B63 | FW68B64 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0V | 08 | 45 | 16" | FW | 68B0V | UGB-1PE | N | 0 | FW68B61 | FW68B62 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | I | MOD.A | Y | 3LPE | N | TP-FW-02 |  | E | N | 000 | N | 76
FW68B37 | 08 | 45 | 6" | FW | 68B37 | PEB-69 | N | 0 | FW68A10 | FW68B0P | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B40 | 08 | 45 | 2" | FW | 68B40 | B-7 | N | 0 | FW68B0L | SPRINKLER SYSTEM FOR PP EXTRUSION | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-02 |  | E | N | 000 | N | 75
FW68B52 | 08 | 45 | 6" | FW | 68B52 | B-7 | N | 0 | FW68B0K | XV-6801B | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B62 | 08 | 45 | 12" | FW | 68B62 | B-7 | N | 0 | FW68B0V | FW68S15 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | TP-FW-02 |  | E | N | 000 | N | 75
FW68B70 | 08 | 45 | 6" | FW | 68B70 | PEB-69 | N | 0 | FW68B69 | FW68B0T | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B79 | 08 | 45 | 1-1/2" | FW | 68B79 | B-7 | N | 0 | FW68B36 | 45-HR-6813 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-01 |  | E | N | 000 | N | 75
FW68B89 | 08 | 45 | 6" | FW | 68B89 | PEB-69 | N | 0 | FW68B69 | FW68B0Y | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68C04 | 08 | 32 | 1/2" | FW | 68C04 | B-7 | N | 0 | FW68C01 | 32-XV-6810A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D01 | 08 | 45 | 1/2" | FW | 68D01 | B-7 | N | 0 | FW68D09 | 45-XV-6815A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D04 | 08 | 45 | 1/2" | FW | 68D04 | B-7 | N | 0 | FW68D09 | 45-XV-6818A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D06 | 08 | 45 | 1" | FW | 68D06 | B-13 | N | 0 | 45-XV-6817A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68D08 | 08 | 45 | 1" | FW | 68D08 | B-13 | N | 0 | 45-XV-6815A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68D08 | 08 | 45 | 4" | FW | 68D08 | B-13 | N | 0 | 45-XV-6815A | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-03 |  | - | Y | 000 | - | 74
FW68D09 | 08 | 45 | 2" | FW | 68D09 | B-7 | N | 0 | FW68A56 | FW68D01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68D10 | 08 | 45 | 3/4" | FW | 68D10 | B-13 | N | 0 | HEADER | TO WATER DRAIN | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68E01 | 08 | 32 | 6" | FW | 68E01 | B-7 | N | 0 | FW68J01 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
PR34020 |  | 32 | 3/4" | PR | 34020 | B4S1 | ET | 40 | PR34021 | 32-D-3400 | 8.0/8.0 | 250.0/0.0 | 5.0/5.0 | 80.0/170.0 |  | 12.52 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 80 | sh.26 | 1 | I | MOD.A | Y | 20 | N | 32-P-048-01 |  | C | N | 141 | N | 380 | 10
HN24005 | 08 | 32 | 1-1/2" | HN | 24005 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24073 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.20 | 2 | I | MOD.A | Y | 1 | N | 32-P-046-01 |  | E | N | 000 | N | 170
HN31001 |  | 32 | 1-1/2" | HN | 31001 | C6S1 | ST | 30 | NITROGEN CONNECTION | HCM31014 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.23 | 2 | I | MOD.A | Y | 20 | N | 32-P-047-01 |  | E | N | 000 | N | 170
HN33001 | 08 | 32 | 1-1/2" | HN | 33001 | C6S1 | N | 0 | VZ33002 | SP-04-13300-03 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.25 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
HN67004 | 08 | 32 | 3/4" | HN | 67004 | C6S1 | N | 0 | HN67001 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84A | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67007 | 08 | 32 | 1-1/2" | HN | 67007 | C6S1 | N | 0 | HN67011 | HEADER | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67023 | 08 | 32 | 1-1/2" | HN | 67023 | C6S1 | N | 0 | HN67013 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN72007 | 08 | 32 | 1-1/2" | HN | 72007 | C6S1 | N | 0 | NITROGEN CONNECTION | PR72009 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.51 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 170
HN72010 | 08 | 32 | 1" | HN | 72010 | C6S1 | N | 0 | PR720105 | SP-04-172B1-09 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.52D | 2 | I | MOD.A | Y | 1 | N | 32-P-007-04 |  | E | N | 000 | N | 170
HOR89001 | 08 | 32 | 3" | HOR | 89001 | C-2 | HA | 90 | TP-N42902 (32-S-8900A/B) | TP-N60202 (32-P-8908A) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL RETURN | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 209
HOR89001 | 08 | 32 | 4" | HOR | 89001 | C-2 | HA | 90 | TP-N42902 (32-S-8900A/B) | TP-N60202 (32-P-8908A) | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | HOT OIL RETURN | L | - | - | <1.5 | 280 | sh.68I | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 209
IA02011 | 08 | 32 | 1" | IA | 02011 | B-13 | N | 0 | IA02002 | TO DCP SYSTEM (TEAL AREA) | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62003 | 08 | 32 | 1/2" | IA | 62003 | C3S1 | N | 0 | 32-D-6200 | IA62004 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA62003 | 08 | 32 | 1-1/2" | IA | 62003 | C3S1 | N | 0 | 32-D-6200 | IA62004 | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA62004 | 08 | 32 | 2" | IA | 62004 | B-13 | N | 0 | IA62003 | IA62904 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62007 | 08 | 32 | 1" | IA | 62007 | C3S1 | N | 0 | 32-D-6200 | TO SAFE LOCATION | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA62007 | 08 | 32 | 2" | IA | 62007 | C3S1 | N | 0 | 32-D-6200 | TO SAFE LOCATION | 28.0 | 150.0 | 25.0 | 40.0 |  | 37.5 | 37.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.43 | 2 | I | MOD.A | Y | 1 | N | 32-U-094-02 |  | E | N | 000 | N | 205
IA6200M | 08 | 32 | 1" | IA | 6200M | B-13 | N | 0 | IA62077 | 32-IAM-001 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA6200U | 08 | 32 | 1" | IA | 6200U | B-13 | N | 0 | IA62073 | 32-IAM-042 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620AB | 08 | 32 | 3/4" | IA | 620AB | B-13 | N | 0 | IA62016 | 32-IAT-049 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AM | 08 | 32 | 3/4" | IA | 620AM | B-13 | N | 0 | IA620AL | 32-IAT-095 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA68C04 | 08 | 32 | 1" | IA | 68C04 | B-13 | N | 0 | IA68C05 | AIR MAINTENANCE DEVICE | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-18 |  | - | N | 000 | - | 200
IA68C09 | 08 | 32 | 1" | IA | 68C09 | B-13 | N | 0 | 32-XV-6801A | IA68H12 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68F03 | 08 | 32 | 1/2" | IA | 68F03 | B-13 | N | 0 | IA68F02 | IA68F02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | N | 000 | - | 200
JWS43001 | 08 | 32 | 3" | JWS | 43001 | C3S1 | N | 0 | JWS64027 | 32-E-4301 | 29.5/28.0 | 235.0/-10.0 | 5.0 | 30.0 |  | 45.61 | 76.65 | H | JACKET WATER SUPPLY | L | - | - | >1.5 | 30 | sh.33 | 2 | I | MOD.A | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 1010
JWS52001 | 08 | 32 | 3" | JWS | 52001 | B-1 | N | 0 | JWS64054 | Seal Pot | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS63002 | 08 | 32 | 3/4" | JWS | 63002 | B-1 | N | 0 | JWS64039 | VA63001 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64014 | 08 | 32 | 2" | JWS | 64014 | B-1 | N | 0 | JWS64054 | TP-12,JWS710118 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64032 | 08 | 32 | 2" | JWS | 64032 | B-1 | N | 0 | JWS64058 | TP-007 (JWS530127) | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64055 | 08 | 32 | 14" | JWS | 64055 | B-1 | N | 0 | JWS64008 | JWS64025 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64064 | 08 | 32 | 1-1/2" | JWS | 64064 | B-1 | N | 0 | JWS64065 | 32-Z-3300A | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64074 | 08 | 32 | 1-1/2" | JWS | 64074 | B-1 | N | 0 | JWS64004 | 32-P-6400C | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.44 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
FW68A98 | 08 | 45 | 8" | FW | 68A98 | UGB-1PE | N | 0 | FW68A25 | FW68A26 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.3 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0B | 08 | 45 | 6" | FW | 68B0B | UGB-1PE | N | 0 | FW68B29 | 45-HY-6810 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0R | 08 | 45 | 6" | FW | 68B0R | UGB-1PE | N | 0 | 45-HY-6816 | FW68B57 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B0T | 08 | 45 | 6" | FW | 68B0T | UGB-1PE | N | 0 | FW68B70 | 45-M-6802 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76
FW68B16 | 08 | 45 | 6" | FW | 68B16 | PEB-69 | N | 0 | FW68B99 | FW68A10 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B26 | 08 | 45 | 1-1/2" | FW | 68B26 | B-7 | N | 0 | FW68B27 | 45-HR-6810 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A88 | 08 | 45 | 2" | FW | 68A88 | B-7 | N | 0 | FW68B0D | 45-HR-6811 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68A88 | 08 | 45 | 6" | FW | 68A88 | B-7 | N | 0 | FW68B0D | 45-HR-6811 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B33 | 08 | 45 | 8" | FW | 68B33 | PEB-69 | N | 0 | FW68A10 | FW68B0N | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B59 | 08 | 45 | 6" | FW | 68B59 | PEB-69 | N | 0 | FW68B0Z | FW68A17 | 16.0 | 35.0 | 12.0/7.0 | 20.0/12.0 |  | 15 | 15 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | NR | N | 45-U-043-01 |  | - | N | 000 | - | 73 | 76
FW68B74 | 08 | 45 | 1-1/2" | FW | 68B74 | B-7 | N | 0 | FW68B15 | 45-HR-6816 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-03 |  | E | N | 000 | N | 75
FW68B78 | 08 | 45 | 1-1/2" | FW | 68B78 | B-7 | N | 0 | FW68B36 | 45-HR-6812 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-01 |  | E | N | 000 | N | 75
FW68C08 | 08 | 32 | 4" | FW | 68C08 | B-13 | N | 0 | 32-XV-6802A | FW68I20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68C08 | 08 | 32 | 6" | FW | 68C08 | B-13 | N | 0 | 32-XV-6802A | FW68I20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68C15 | 08 | 32 | 3/4" | FW | 68C15 | B-13 | N | 0 | 32-XV-6808A | FW68C11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.92 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68E11 | 08 | 32 | 3/4" | FW | 68E11 | B-7 | N | 0 | FW68E02 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E21 | 08 | 32 | 3/4" | FW | 68E21 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E22 | 08 | 32 | 3/4" | FW | 68E22 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E23 | 08 | 32 | 2" | FW | 68E23 | B-7 | N | 0 | FW68E28 | FW68E28 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
CWR89036 | 08 | 32 | 1/2" | CWR | 89036 | B-1 | N | 0 | TP-N11211 (32-H-8901) | CWR89008 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.68A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
LN81010 | 08 | 32 | 1/2" | LN | 81010 | 1CS2 | N | 0 | LN89004 | 32-ZF-8100A | 2.0 | 80.0 | 0.5 | 25.0 |  | 2.66 | 25.65 | P | NITROGEN L.P. | G | - | - | >1.5 | 25 | sh.59 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 175
LO23005 | 08 | 32 | 6" | LO | 23005 | QXB-55 | P | 50 | TP-22 (LO230125) | TP-23 (D-2500) | 15.0/16.0 | 120.0/80.0 | 2.0 | 65.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 65 | sh.16B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-044-03 |  | M | N | 110 | N | 801
LO32007 | 08 | 32 | 1/2" | LO | 32007 | QXB-55 | N | 0 | TP 18B (LO320115) | TP 17B (32-PK-3200 B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LO32007 | 08 | 32 | 1-1/2" | LO | 32007 | QXB-55 | N | 0 | TP 18B (LO320115) | TP 17B (32-PK-3200 B) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.24I | 2 | Art 4.3 | NA | N | 5 | N | 32-P-047-07 |  | M | N | 110 | N | 800
LO89005 | 08 | 32 | 6" | LO | 89005 | QXB-55 | N | 0 | TP-N20450 (32-E-8902) | TP-N20350 (32-Z-8900) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.68B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-070-08 |  | M | N | 110 | N | 800
LPN10002 | 08 | 32 | 1/2" | LPN | 10002 | 3DS3 | N | 0 | LPN10001 | LPN10006 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.4 | 1 | Art 4.3 | NA | N | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
LPN11012 | 08 | 32 | 1-1/2" | LPN | 11012 | 3DS3 | N | 0 | 32-Z-1100 | 32-D-1102 | 5.0 | 150.0 | 3.0 | 25.0 |  | 6.65 | 66.96 | P | L.P. PURIFIED NITROGEN | G | - | - | >1.5 | 25 | sh.47 | 1 | I | MOD.A | Y | 5 | N | 32-P-020-01 |  | F | N | 343 | N | 165 | 8,29,23,25
IA68F07 | 08 | 32 | 1" | IA | 68F07 | B-13 | N | 0 | IA68R03 | SFP-001 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-14 |  | - | N | 000 | - | 200
IA68K11 | 08 | 32 | 3/4" | IA | 68K11 | B-13 | N | 0 | 20 LTR TANK | IA68K01 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-17 |  | - | N | 000 | - | 200
IA68L16 | 08 | 32 | 1" | IA | 68L16 | B-13 | N | 0 | FUSIBLE GLASS BULB | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68N13 | 08 | 32 | 1" | IA | 68N13 | B-13 | N | 0 | IA68K07 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N34 | 08 | 32 | 1" | IA | 68N34 | B-13 | N | 0 | IA68N33 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
HCM24058 |  | 32 | 3/4" | HCM | 24058 | C42S1 | P | 50 | HCM24063 | HCM23046 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 1 | N | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24058 |  | 32 | 6" | HCM | 24058 | C42S1 | P | 50 | HCM24063 | HCM23046 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.19 | 1 | III | MOD.G | Y | 1 | Y | 32-P-045-01 |  | G | Y | 141 | N | 520 | 10
HCM24059 |  | 32 | 6" | HCM | 24059 | D20S1 | P | 50 | HCM24080 | HCM23046 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM31013 |  | 32 | 1-1/2" | HCM | 31013 | C42S1 | ST | 30 | 32-S-3100 | 32-PDT-3102 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31017 |  | 32 | 1" | HCM | 31017 | C42S1 | ST | 30 | PR31022 | 32-D-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM31017 |  | 32 | 2" | HCM | 31017 | C42S1 | ST | 40 | PR31022 | 32-D-3100 | 35.0/35.0 | -45.0/250.0 | 30.0 | 120.0 |  | 54.8 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | G | - | - | >1.5 | 120 | sh.23 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 345 | 10
HCM32038 | 08 | 32 | 1" | HCM | 32038 | C42S1 | HB | 30 | TP-05A (32-D-3202A) | HCM32031 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HCM32038 | 08 | 32 | 2" | HCM | 32038 | C42S1 | HB | 30 | TP-05A (32-D-3202A) | HCM32031 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24A | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HN23004 | 08 | 32 | 1-1/2" | HN | 23004 | C6S1 | N | 0 | NITROGEN CONNECTION | P23027 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.16 | 2 | I | MOD.A | Y | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 170
HN23007 | 08 | 32 | 1-1/2" | HN | 23007 | C6S1 | N | 0 | CD, N, HN | HCM23018 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.17 | 2 | I | MOD.A | Y | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 170
HN23009 | 08 | 32 | 1" | HN | 23009 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM23052 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.16 | 2 | I | MOD.A | Y | 1 | N | 32-P-044-01 |  | E | N | 000 | N | 170
HN24003 | 08 | 32 | 1" | HN | 24003 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24092 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.19 | 2 | I | MOD.A | Y | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 170
HN24004 | 08 | 32 | 1" | HN | 24004 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24093 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.19 | 2 | I | MOD.A | Y | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 170
HN24004 | 08 | 32 | 1-1/2" | HN | 24004 | C6S1 | N | 0 | NITROGEN CONNECTION | HCM24093 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.19 | 2 | I | MOD.A | Y | 1 | N | 32-P-045-01 |  | E | N | 000 | N | 170
HN40002 |  | 32 | 1-1/2" | HN | 40002 | C6S1 | ST | 30 | NITROGEN CONNECTION | PR40035 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.30 | 2 | I | MOD.A | Y | 20 | N | 32-P-047-03 |  | E | N | 000 | N | 170
HN62017 | 08 | 32 | 1-1/2" | HN | 62017 | C6S1 | N | 0 | HN | PR33019 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.13 | 2 | I | MOD.A | Y | 1 | N | 32-P-008-01 |  | E | N | 000 | N | 170
IA6200V | 08 | 32 | 1" | IA | 6200V | B-13 | N | 0 | IA62073 | 32-IAM-037 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62012 | 08 | 32 | 1" | IA | 62012 | B-13 | N | 0 | IA62074 | 32-IAM-038 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA62081 | 08 | 32 | 1-1/2" | IA | 62081 | B-13 | N | 0 | IA62089 | 32-IAM-016 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01 |  | - | N | 000 | - | 200
IA620AG | 08 | 32 | 3/4" | IA | 620AG | B-13 | N | 0 | IA62081 | 32-IAT-082 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA620AR | 08 | 32 | 1-1/2" | IA | 620AR | B-13 | N | 0 | IA62084 | 32-IAT-093 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.80 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-094-01A |  | - | N | 000 | - | 200
IA68D03 | 08 | 45 | 1" | IA | 68D03 | B-13 | N | 0 | IA68D05 | IA68D08 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.5 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68H02 | 08 | 32 | 1" | IA | 68H02 | B-13 | N | 0 | IA68C09 | IA68H01 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I29 | 08 | 32 | 1" | IA | 68I29 | B-13 | N | 0 | IA68I03 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68K02 | 08 | 32 | 1" | IA | 68K02 | B-13 | N | 0 | IA68K11 | IA68K05 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-17 |  | - | N | 000 | - | 200
IA68L19 | 08 | 32 | 1" | IA | 68L19 | B-13 | N | 0 | IA68L21 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | N | 000 | - | 200
IA68M26 | 08 | 32 | 1" | IA | 68M26 | B-13 | N | 0 | IA68K08 | IA68M21 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68N02 | 08 | 32 | 1" | IA | 68N02 | B-13 | N | 0 | IA68N06 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N37 | 08 | 32 | 1" | IA | 68N37 | B-13 | N | 0 | IA68M11 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68N44 | 08 | 32 | 1" | IA | 68N44 | B-13 | N | 0 | IA68N24 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68O10 | 08 | 32 | 1" | IA | 68O10 | B-13 | N | 0 | IA68O19 | IA68O12 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68O17 | 08 | 32 | 1" | IA | 68O17 | B-13 | N | 0 | IA68O15 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
LC51004 |  | 32 | 3/4" | LC | 51004 | B-5 | HB | 30 | LS51001 | LC63088 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.36 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC52003 |  | 32 | 1/2" | LC | 52003 | B-5 | HB | 30 | LS52006 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.37 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300I |  | 32 | 1-1/2" | LC | 6300I | B-5 | HB | 40 | 32-1121-R-014 | LC63078 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63063 |  | 32 | 3/4" | LC | 63063 | B-5 | HB | 30 | LS63160 | LC72004 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC63085 |  | 32 | 2" | LC | 63085 | B-5 | HB | 40 | LC24015 | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC71001 |  | 32 | 1/2" | LC | 71001 | B-5 | HB | 30 | LS71011 | LC63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.48 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC91A70 | 08 | 32 | 3/4" | LC | 91A70 | B-5 | P | 50 | LC91A53 | LS89056 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.85 | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
BDL31037 | 08 | 32 | 1/2" | BDL | 31037 | B32S1 | N | 0 | HCM31023 | BDL31040 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.23 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL32031 | 08 | 32 | 2" | BDL | 32031 | B32S1 | HB | 30 | TP-02A (32-D-3201A) | BDL32030 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.24A | 1 | I | MOD.A | Y | 20 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL36015 | 08 | 32 | 2" | BDL | 36015 | B32S1 | N | 0 | TP-107, (32-D-3602) | BDL36013 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.28A | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL51017 | 08 | 32 | 3" | BDL | 51017 | B4S1 | N | 0 | PW51013 | BDL51015 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.36 | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
BDL60050 | 08 | 32 | 1" | BDL | 60050 | B32S1 | N | 0 | N67101 | BDL60028 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL60061 | 08 | 32 | 2" | BDL | 60061 | B32S1 | N | 0 | BDL23055 | BDL60029 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.78B | 1 | I | MOD.A | Y | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL61003 | 08 | 32 | 3/4" | BDL | 61003 | B32S1 | N | 0 | TP-034 (32-S-6100) | BDL61004 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.42B | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL71040 | 08 | 32 | 1" | BDL | 71040 | B4S1 | N | 0 | TP-021 (N720162) | BDL71033 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.48 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 470 | ,10
N63001 | 08 | 32 | 1/2" | N | 63001 | B-1 | N | 0 | N67071 | 32-AFR-6301 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.87 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-02 |  | E | N | 000 | N | 140
N66001 | 08 | 32 | 1" | N | 66001 | 1CS2 | N | 0 | N67070 | 32-D-6600 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.46 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-03 |  | M | N | 000 | N | 166
N66004 | 08 | 32 | 1" | N | 66004 | 1CS2 | N | 0 | N66001 | N66001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.46 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-03 |  | M | N | 000 | N | 166
N67005 | 08 | 32 | 2" | N | 67005 | B-1 | N | 0 | N01001 | HEADER | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N6700Z | 08 | 32 | 1" | N | 6700Z | B-1 | N | 0 | N67005 | HOSE CONNECTION | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67030 | 08 | 32 | 1/2" | N | 67030 | B-1 | N | 0 | N67031 | N13003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.6 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67038 | 08 | 32 | 3/4" | N | 67038 | B-1 | N | 0 | N67039 | N14001 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-05 |  | E | N | 000 | N | 140
N67045 | 08 | 32 | 1-1/2" | N | 67045 | B-1 | N | 0 | N67029 | N67043 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.84A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N67091 | 08 | 32 | 3/4" | N | 67091 | B-1 | N | 0 | N67104 | BDL60040 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.78A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-01 |  | E | N | 000 | N | 140
N80024 | 08 | 32 | 1/2" | N | 80024 | 1CS2 | N | 0 | N80018 | TP-005 (N81030) | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.58 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81040 | 08 | 32 | 3/4" | N | 81040 | 1CS2 | N | 0 | N89057 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81054 | 08 | 32 | 1/2" | N | 81054 | 1CS2 | N | 0 | N89066 | 32-PK-8101 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.60 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
N81057 | 08 | 32 | 1/2" | N | 81057 | 1CS2 | N | 0 | N89064 | 32-Z-8105 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-U-003-06 |  | M | N | 000 | N | 166
BDL71030 | 08 | 32 | 3/4" | BDL | 71030 | B4S1 | N | 0 | BDL71039 | BDL61018 | 3.5 | 120.0 | 0.2/1.4 | 100.0/100.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 100 | sh.78 | 1 | I | MOD.A | Y | 1 | N | 32-P-006-02 |  | G | N | 141 | N | 470 | ,10
BDL72022 | 08 | 32 | 1" | BDL | 72022 | B32S1 | N | 0 | PR72009 | BDL72021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72030 | 08 | 32 | 1/2" | BDL | 72030 | B32S1 | N | 0 | PR72027 | BDL60021 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72032 | 08 | 32 | 3" | BDL | 72032 | B32S1 | N | 0 | PR72037 | BDL60020 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.51 | 1 | II | MOD.A2 | Y | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72060 | 08 | 32 | 1" | BDL | 72060 | B32S1 | N | 0 | TP-016 (PR720126) | BDL72067 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52D | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL72072 | 08 | 32 | 2" | BDL | 72072 | B32S1 | HA | 30 | PR72060 | BDL72038 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.52C | 1 | I | MOD.A | Y | 20 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
SWW92003 | 08 | 32 | 2" | SWW | 92003 | 1CS2 | N | 0 | SWW92005 | 32-D-9005 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92012 | 08 | 32 | 1-1/2" | SWW | 92012 | 1CS2 | N | 0 | SWW92026 | 32-H-9001B | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
SWW92017 | 08 | 32 | 8" | SWW | 92017 | 1CS2 | N | 0 | DETAIL A | SWW92004 | 11.0 | 80.0 | 8.0 | 20.0 |  | 16.5 | 28.5 | H | SILO WASHING WATER | L | - | - | <1.5 | 20 | sh.72 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-082-08 |  | M | N | 000 | N | 24 | 28
TEA20003 |  | 32 | 1/2" | TEA | 20003 | 3FS3 | CF | 25 | N20001 | 32-R-2000 | 70.0 | 150.0 | 50.15/50.15 | 20.0/30.0 |  | 105.15 | 148.95 | IO | TEAL | L | - | - | <1.5 | 20 | sh.11 | 1 | Art 4.3 | NA | N | NR | N | 32-P-040-01 |  | F | N | 343 | N | 266 | 8,29
VA00007 | 08 | 32 | 4" | VA | 00007 | B-1 | N | 0 | 1123-ACW-DM-004 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00035 | 08 | 32 | 4" | VA | 00035 | B-1 | N | 0 | 2121-ACW-SM-108 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00055 | 08 | 32 | 4" | VA | 00055 | B-1 | N | 0 | 3221-ACW-SM-093 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00089 | 08 | 32 | 4" | VA | 00089 | B-1 | N | 0 | 6111-ACW-SM-064 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VA00094 | 08 | 32 | 4" | VA | 00094 | B-1 | N | 0 | 6112-SW-DM-002 | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
FW68E05 | 08 | 32 | 3/4" | FW | 68E05 | B-7 | N | 0 | FW68E41 | FW68E13 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E13 | 08 | 32 | 3/4" | FW | 68E13 | B-7 | N | 0 | FW68E02 | FW68E03 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68E41 | 08 | 32 | 3/4" | FW | 68E41 | B-7 | N | 0 | FW68E03 | FW68E02 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.93 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68F03 | 08 | 32 | 1/2" | FW | 68F03 | B-13 | N | 0 | FW68R06 | FW68F02 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | Y | 000 | - | 74
FW68F19 | 08 | 32 | 3/4" | FW | 68F19 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68G48 | 08 | 45 | 3" | FW | 68G48 | B-13 | N | 0 | HV | HV | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.6 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-05 |  | - | Y | 000 | - | 74
FW68H21 | 08 | 32 | 1" | FW | 68H21 | B-13 | N | 0 | FW68H26 | FW68H24 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H24 | 08 | 32 | 1" | FW | 68H24 | B-13 | N | 0 | FW68H21 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I09 | 08 | 32 | 3" | FW | 68I09 | B-13 | N | 0 | FW68I08 | FW68I12 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I31 | 08 | 32 | 1-1/2" | FW | 68I31 | B-13 | N | 0 | FW68I27 | FW68I39 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I40 | 08 | 32 | 1" | FW | 68I40 | B-13 | N | 0 | FW68I39 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I41 | 08 | 32 | 1" | FW | 68I41 | B-13 | N | 0 | FW68I32 | MSN-002 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68J02 | 08 | 45 | 6" | FW | 68J02 | B-7 | N | 0 | XV-6802B | FW68T73 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-043-10 |  | E | N | 000 | N | 75
FW68K02 | 08 | 32 | 1/2" | FW | 68K02 | B-7 | N | 0 | XV6809A | XV6809A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K02 | 08 | 32 | 6" | FW | 68K02 | B-7 | N | 0 | XV6809A | XV6809A | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68K17 | 08 | 32 | 3/4" | FW | 68K17 | B-13 | N | 0 | XV6806A | FW68K13 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68M07 | 08 | 32 | 1" | FW | 68M07 | B-13 | N | 0 | FW68M08 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M08 | 08 | 32 | 1" | FW | 68M08 | B-13 | N | 0 | FW68M47 | FW68M05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M08 | 08 | 32 | 1-1/2" | FW | 68M08 | B-13 | N | 0 | FW68M47 | FW68M05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
HCM00002 | 08 | 45 | 1" | HCM | 00002 | B4S1 | N | 0 | FUEL TANK | FUEL TANK | 5.0 | 120.0 | 0.8 | 85.0 |  | 7.5 | 29.4 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.106 | 1 | Art 4.3 | NA | N | 1 | N | 45-U-002-01 |  | C | N | 141 | N | 383 | 10
HCM23004 |  | 32 | 4" | HCM | 23004 | C42S1 | HB | 40 | HCM23003 | 32-Z-2300A | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23018 |  | 32 | 1/2" | HCM | 23018 | C42S1 | ST | 30 | HN23007 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23018 |  | 32 | 1" | HCM | 23018 | C42S1 | ST | 30 | HN23007 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23018 |  | 32 | 2" | HCM | 23018 | C42S1 | ST | 40 | HN23007 | 32-S-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23065 | 08 | 32 | 1" | HCM | 23065 | C42S1 | HB | 30 | HCM23004 | HCM24095 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15A | 1 | III | MOD.G | Y | 20 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23065 | 08 | 32 | 6" | HCM | 23065 | C42S1 | HB | 40 | HCM23004 | HCM24095 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.15A | 1 | III | MOD.G | Y | 20 | Y | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HCM23075 |  | 32 | 1/2" | HCM | 23075 | 3FS4 | HB | 30 | HCM23072 | PR24043 | 50.0/50.0 | -40.0/200.0 | 40.0 | 55.0 |  | 80.16 | 148.95 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 55 | sh.15 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-045-02 |  | H | Y | 141 | N | 525 | 15,36,5
HCM23078 | 08 | 32 | 1" | HCM | 23078 | C42S1 | N | 0 | PR24041 | 32-R-2300 | 42.0/42.0 | -45.0/150.0 | 35.0/35.0 | 120.0/10.0 |  | 63.01 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 10 | sh.14 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-044-01 |  | G | Y | 141 | N | 520 | 10
HTF89008 | 08 | 32 | 1" | HTF | 89008 | C-2 | HA | 80 | HOS89004 | COLLECTION DRUM | 10.0 | 315.0 | 6.5/7.5 | 280.0/280.0 |  | 16.75 | 76.65 | IO | DIATHERMIC OIL/HOT THERMAL FLUID | L | - | - | <1.5 | 280 | sh.68R | 2 | Art 4.3 | NA | N | NR | N | 32-P-070-05 |  | E | N | 110 | N | 207
IA68H13 | 08 | 32 | 1" | IA | 68H13 | B-13 | N | 0 | IA68H11 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | N | 000 | - | 200
IA68I05 | 08 | 32 | 1" | IA | 68I05 | B-13 | N | 0 | IA68I09 | GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | N | 000 | - | 200
IA68K10 | 08 | 32 | 1/2" | IA | 68K10 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68L04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09,32-U-043-17 |  | - | N | 000 | - | 200
IA68K10 | 08 | 32 | 1" | IA | 68K10 | B-13 | N | 0 | AIR MAINTENANCE DEVICE | IA68L04 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09,32-U-043-17 |  | - | N | 000 | - | 200
IA68M23 | 08 | 32 | 1" | IA | 68M23 | B-13 | N | 0 | IA68M08 | SWIVEL JOINT | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
IA68M29 | 08 | 32 | 1" | IA | 68M29 | B-13 | N | 0 | IA68M28 | IA68M31 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | N | 000 | - | 200
PR61005 | 08 | 32 | 1" | PR | 61005 | C42S1 | N | 0 | TP-015 (32-D-6108) | TP-021 (32-PSV-6180) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61005 | 08 | 32 | 4" | PR | 61005 | C42S1 | N | 0 | TP-015 (32-D-6108) | TP-021 (32-PSV-6180) | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 14.7/14.7 | 58.0/22.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | 22 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 141 | N | 395 | 15
PR61006 | 08 | 32 | 2" | PR | 61006 | C42S1 | CF | 50 | TP-012 (E-6102) | BDL61023 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 4.1 | -4.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | -4 | sh.42E | 1 | II | MOD.A2 | Y | 20 | N | 32-P-055-03 |  | F | N | 141 | N | 396 | 15
PR61006 | 08 | 32 | 4" | PR | 61006 | C42S1 | CF | 50 | TP-012 (E-6102) | BDL61023 | 18.7/18.7/-1.0 | 120.0/-45.0/120.0 | 4.1 | -4.0 |  | 28.05 | 76.65 | H | PROPYLENE | LG | - | - | >1.5 | -4 | sh.42E | 1 | II | MOD.A2 | Y | 20 | N | 32-P-055-03 |  | F | N | 141 | N | 396 | 15
PR72004 |  | 32 | 1" | PR | 72004 | C42S1 | HB | 30 | PR01001 | TP-011 (PR720159) | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | Art 4.3 | NA | N | 20 | N | 32-P-007-01 |  | F | N | 141 | N | 347 | ,15
PR72016 | 08 | 32 | 1/2" | PR | 72016 | C42S1 | N | 0 | 32-E-7202 | 32-E-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | N | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
PR72016 | 08 | 32 | 6" | PR | 72016 | C42S1 | N | 0 | 32-E-7202 | 32-E-7203 | 43.7/43.7 | 150.0/-45.0 | 26.0/26.0 | 42.0/0.0 |  | 65.56 | 76.65 | H | PROPYLENE | L | - | - | >1.5 | 0 | sh.51 | 1 | III | MOD.G | Y | 1 | Y | 32-P-007-02 |  | F | N | 141 | N | 347 | ,15
LA16006 |  | 32 | 1" | LA | 16006 | 4CS2 | HH | 30 | LA16005 | 32-D-1600 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16006 |  | 32 | 4" | LA | 16006 | 4CS2 | HH | 30 | LA16005 | 32-D-1600 | 6.0 | 180.0 | 5.0 | 50.0 |  | 9.37 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 402
LA16009 |  | 32 | 1-1/2" | LA | 16009 | 4CS2 | ET | 30 | 32-D-1601 | LA16007 | 0.5 | 180.0 | 0.05 | 50.0 |  | .78 | 28.5 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | NA | NA | NA | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 401
LA16012 |  | 32 | 3/4" | LA | 16012 | 1FS4 | ET | 30 | LA16011 | LA16013 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.10 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA23006 |  | 32 | 1/2" | LA | 23006 | 1FS4 | ET | 30 | LA16031 | LA23004 | 60.0 | 180.0 | 45.0 | 50.0 |  | 93.67 | 148.95 | IO | LIQUID ADDITIVES | L | - | - | <1.5 | 50 | sh.16 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-023-01 |  | M | N | 210 | N | 405
LA84010 |  | 32 | 1/2" | LA | 84010 | 4CS2 | ET | 30 | 32-P-8402A | 32-S-8402A | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
LA84010 |  | 32 | 1" | LA | 84010 | 4CS2 | ET | 30 | 32-P-8402A | 32-S-8402A | 6.0 | 150.0 | 5.0/5.0 | 25.0/60.0 |  | 9.01 | 28.5 | H | LIQUID ADDITIVES | L | - | - | <1.5 | 25 | sh.64 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-062-02 |  | M | N | 210 | N | 603
VZ13006 |  | 32 | 1/2" | VZ | 13006 | B4S2 | ST | 30 | 32-D-1300 | 32-D-1300 | 0.5 | 180.0 | 0.05 | 100.0 |  | .75 | 29.4 | IO | VESSEL TRIM | L | - | - | <1.5 | 100 | sh.6 | 2 | NA | NA | NA | 20 | N | 32-P-025-01 |  | E | N | 110 | N | 223 | 23,25
VZ14016 |  | 32 | 1" | VZ | 14016 | QXC25S1 | CF | 25 | 32-D-1401B | CT14009 | 20.0 | 190.0 | 10.0/0.03 | 6.0/70.0 |  | 31.64 | 74.4 | H | VESSEL TRIM | L | - | - | <1.5 | 6 | sh.8 | 1 | Art 4.3 | NA | N | 27 | N | 32-P-026-03 |  | M | N | 231 | N | 284
VZ24004 | 08 | 32 | 3/4" | VZ | 24004 | C42S1 | N | 0 | 32-E-2404 | BDL24075 | 42.0/42.0 | -45.0/150.0 | 31.0/31.0 | 10.0/40.0 |  | 63.01 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 10 | sh.19 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-045-01 |  | F | N | 141 | N | 355 | 15
VZ32002 |  | 32 | 3/4" | VZ | 32002 | C42S1 | HB | 30 | 32-D-3200 | HCM32017 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.24 | 1 | II | MOD.A2 | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
VZ50008 |  | 32 | 12" | VZ | 50008 | 1CR9 | HB | 40 | 32-D-5001 | 32-D-5001 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | VESSEL TRIM | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-2 | N | 141 | N | 441 | 16,10,11,13
FW68F22 | 08 | 32 | 2" | FW | 68F22 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68F27 | 08 | 32 | 3/4" | FW | 68F27 | B-13 | N | 0 | FW68F30 | FW68F30 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.94 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-15 |  | - | Y | 000 | - | 74
FW68H02 | 08 | 32 | 1" | FW | 68H02 | B-13 | N | 0 | FW68H03 | FW68H03 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H15 | 08 | 32 | 1-1/2" | FW | 68H15 | B-13 | N | 0 | FW68H29 | FW68H20 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68H49 | 08 | 32 | 2" | FW | 68H49 | B-13 | N | 0 | FW68H33 | FW68H38 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.95 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-05 |  | - | Y | 000 | - | 74
FW68I05 | 08 | 32 | 1" | FW | 68I05 | B-13 | N | 0 | FW68I20 | FW68I22 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I08 | 08 | 32 | 3" | FW | 68I08 | B-13 | N | 0 | FW68I18 | FW68I11 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I20 | 08 | 32 | 1-1/2" | FW | 68I20 | B-13 | N | 0 | FW68C08 | FW68I05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68I36 | 08 | 32 | 1" | FW | 68I36 | B-13 | N | 0 | FW68I05 | FW68I26 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.96 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68J01 | 08 | 45 | 6" | FW | 68J01 | B-7 | N | 0 | XV-6801B | FW68E01 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.2 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-043-16 |  | E | N | 000 | N | 75
FW68K16 | 08 | 32 | 3/4" | FW | 68K16 | B-13 | N | 0 | XV6804A | FW68K13 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68K07 | 08 | 32 | 6" | FW | 68K07 | B-13 | N | 0 | XV6809A | FW68P09 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | Y | 000 | - | 74
FW68K08 | 08 | 32 | 3/4" | FW | 68K08 | B-7 | N | 0 | FW68A22 | FW68K09 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.91 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68L24 | 08 | 32 | 1" | FW | 68L24 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68L24 | 08 | 32 | 1-1/2" | FW | 68L24 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-06 |  | - | Y | 000 | - | 74
FW68L26 | 08 | 32 | 1-1/2" | FW | 68L26 | B-13 | N | 0 | FW68L05 | FW68L05 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.97 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-09 |  | - | Y | 000 | - | 74
FW68N10 | 08 | 32 | 1" | FW | 68N10 | B-13 | N | 0 | FW68N09 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N34 | 08 | 32 | 2" | FW | 68N34 | B-13 | N | 0 | FW68N30 | MSN-009 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
CWS86016 | 08 | 32 | 1/2" | CWS | 86016 | B-1 | N | 0 | CWS89042 | 32-D-8600 | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
CWS89031 | 08 | 32 | 3" | CWS | 89031 | B-1 | N | 0 | CWS64010 | TP-N60103 (32-E-8906) | 7.5 | 100.0 | 5.5 | 26.0 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.85A | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
DO12008 |  | 32 | 1" | DO | 12008 | 1CS2 | ET | 30 | 32-S-1200A | DO12022 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DO12024 | 08 | 32 | 1" | DO | 12024 | 1CS2 | N | 0 | DO12002 | 32-S-1201 | 8.8 | 150.0 | 1.65 | 30.0 |  | 13.22 | 28.5 | IO | DONOR | L | - | - | <1.5 | 30 | sh.5 | 2 | Art 4.3 | NA | N | NR | N | 32-P-022-01 |  | M | N | 220 | N | 270 | 23,25
DW69A01 | 08 | 32 | 1-1/2" | DW | 69A01 | B-13 | IS | 50 | DW01001 | 32-ES-6901 | 10.0 | 40.0 | 7.5 | 30.0 |  | 15 | 29.4 | H | DRINKING WATER | L | - | - | <1.5 | 30 | sh.89 | 2 | Art 4.3 | NA | N | NR | N | 32-U-045-01 |  | - | N | 000 | - | 22
IA68N41 | 08 | 32 | 1" | IA | 68N41 | B-13 | N | 0 | IA68N24 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | N | 000 | - | 200
IA68O14 | 08 | 32 | 1" | IA | 68O14 | B-13 | N | 0 | IA68O19 | FUSIBLE GLASS BULB | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.100 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-08 |  | - | N | 000 | - | 200
IA68P07 | 08 | 32 | 1" | IA | 68P07 | B-13 | N | 0 | IA68P06 | IA68P06 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.101 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-10 |  | - | N | 000 | - | 200
IA68Q07 | 08 | 32 | 1" | IA | 68Q07 | B-13 | N | 0 | IA68Q06 | IA68Q09 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-07 |  | - | N | 000 | - | 200
IA68R03 | 08 | 45 | 1/2" | IA | 68R03 | B-13 | N | 0 | 45-XV-6821A | IA68F07 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-14 |  | - | N | 000 | - | 200
IA68R10 | 08 | 45 | 1/2" | IA | 68R10 | B-13 | N | 0 | 45-XV-6820A | IA68F02 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.1 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-13 |  | - | N | 000 | - | 200
HN67019 | 08 | 32 | 3/4" | HN | 67019 | C6S1 | N | 0 | HN67012 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN71002 | 08 | 32 | 1" | HN | 71002 | C6S1 | N | 0 | NITROGEN CONNECTION | ET71039 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.49 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN71002 | 08 | 32 | 1-1/2" | HN | 71002 | C6S1 | N | 0 | NITROGEN CONNECTION | ET71039 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.49 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN72006 | 08 | 32 | 1-1/2" | HN | 72006 | C6S1 | N | 0 | NITROGEN CONNECTION | PR72014 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.51 | 2 | I | MOD.A | Y | 1 | N | 32-P-007-02 |  | E | N | 000 | N | 170
HCM24089 |  | 32 | 6" | HCM | 24089 | D20S1 | P | 50 | HCM23060 | PR23013 | 48.0/48.0/52.0/52.0 | -45.0/150.0/-45.0/150.0 | 35.0/35.0 | 55.0/80.0 |  | 78.01 | 128.56 | H | HYDROCARBON MIX FOR MULT.SERV. | L | - | - | >1.5 | 55 | sh.20 | 1 | III | MOD.G | Y | 1 | Y | 32-P-046-01 |  | F | N | 141 | N | 530 | 15
HCM32031 | 08 | 32 | 1" | HCM | 32031 | C42S1 | HB | 30 | HCM32038 | HCM32037 | 25.0/25.0 | -45.0/190.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | HYDROCARBON MIX FOR MULT.SERV. | LG | - | - | >1.5 | 85 | sh.24A | 1 | Art 4.3 | NA | N | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 349 | 10
HN22001 | 08 | 32 | 1-1/2" | HN | 22001 | C6S1 | N | 0 | HN | ET22010 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.13 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN22002 | 08 | 32 | 1-1/2" | HN | 22002 | C6S1 | N | 0 | HN | ET22008 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.13 | 2 | I | MOD.A | Y | 1 | N | 32-P-006-03 |  | E | N | 000 | N | 170
HN67009 | 08 | 32 | 3/4" | HN | 67009 | C6S1 | N | 0 | HN67007 | NITROGEN CONNECTION | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
HN67013 | 08 | 32 | 1-1/2" | HN | 67013 | C6S1 | N | 0 | HEADER | HN67023 | 42.0 | 80.0 | 40.0/39.6 | 25.0/25.0 |  | 55.86 | 68.99 | P | HP NITROGEN | G | - | - | >1.5 | 25 | sh.84 | 2 | I | MOD.A | Y | 1 | N | 32-U-004-01 |  | E | N | 000 | N | 170
LC31016 |  | 32 | 3/4" | LC | 31016 | B-5 | HB | 30 | LS31021 | LC31036 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31016 |  | 32 | 1" | LC | 31016 | B-5 | HB | 40 | LS31021 | LC31036 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31019 |  | 32 | 3/4" | LC | 31019 | B-5 | HB | 30 | LS31024 | LC63092 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31021 |  | 32 | 1-1/2" | LC | 31021 | B-5 | HB | 40 | LS31028 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.23 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC31041 | 08 | 32 | 1/2" | LC | 31041 | B-5 | P | 50 | LS31035 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81A | 2 | Art 4.3 | NA | N | 6 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34004 | 08 | 32 | 1/2" | LC | 34004 | B-5 | HB | 30 | LS34004 | LC24015 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC34005 |  | 32 | 1/2" | LC | 34005 | B-5 | HB | 30 | LS34005 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.26 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50001 |  | 32 | 1/2" | LC | 50001 | B-5 | HB | 30 | LC5001A | LC63001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.81 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50004 |  | 32 | 3/4" | LC | 50004 | B-5 | HB | 30 | LS50045 | LC63085 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC50009 |  | 32 | 1/2" | LC | 50009 | B-5 | HB | 30 | LS50038 | LC43001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.34 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LO23001 | 08 | 32 | 1-1/2" | LO | 23001 | QXB-55 | N | 0 | TP 20 (LO230117) | TP 21 (LO230120) | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.16B | 2 | Art 4.3 | NA | N | 5 | N | 32-P-044-03 |  | M | N | 110 | N | 800
LO24001 | 08 | 32 | 3/4" | LO | 24001 | QXB-55 | N | 0 | TP-11 (LUBE OIL DRAIN TO TEMPORARY TANK ) | TO PORTABLE POT | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.21C | 2 | Art 4.3 | NA | N | 5 | N | 32-P-045-04 |  | M | N | 110 | N | 800
LO62001 | 08 | 32 | 3/4" | LO | 62001 | QXB-55 | N | 0 | TP-11 (LO-620109) | LUBE OIL DRAIN TO TEMPORARY TANK | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.43C | 2 | Art 4.3 | NA | N | 5 | N | 32-U-094-01 |  | M | N | 110 | N | 800
LO71001 | 08 | 32 | 1/2" | LO | 71001 | QXB-55 | N | 0 | ET710108 | DRAIN TO TEMPORARY TANK | 15.0/16.0 | 120.0/80.0 | 2.0 | 50.0 |  | 24 | 28.5 | H | LUBE OIL | L | - | - | <1.5 | 50 | sh.50A | 2 | Art 4.3 | NA | N | 5 | N | 32-P-006-05 |  | M | N | 110 | N | 800
BDL72059 | 08 | 32 | 1/2" | BDL | 72059 | B32S1 | N | 0 | TP-015 (PR720128) | BDL72067 | 3.5 | 300.0 | 1.37 | 280.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 280 | sh.52D | 1 | Art 4.3 | NA | N | 7 | N | 32-U-031-01 |  | G | N | 141 | N | 462 | 10
CD24001 | 08 | 32 | 1" | CD | 24001 | 1CS2 | N | 0 | 32-SP-04-124A0-10 | HCM24069 | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.19 | 2 | Art 4.3 | NA | N | NR | N | 32-P-045-01 |  | F | N | 100 | N | 288
CHWR61002 |  | 32 | 10" | CHWR | 61002 | B-1 | CF | 40 | CHWR43011 | CHWR61014 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CO42020 | 08 | 32 | 1/2" | CO | 42020 | 1IS5 | N | 0 | REACTOR EMERGENCY KILLER | CO42018 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CWR86012 |  | 32 | 1/2" | CWR | 86012 | B-1 | HB | 30 | JCW86015 | CWR86011 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-021-03 |  | E | N | 000 | N | 13
CWR86021 | 08 | 32 | 1" | CWR | 86021 | B-1 | N | 0 | CWR86016 | VA86002 | 7.5 | 100.0 | 3.5 | 37.0 |  | 11.25 | 29.4 | H | COOLING WATER RETURN | L | - | - | <1.5 | 37 | sh.65 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-03 |  | E | N | 000 | N | 13
N89063 | 08 | 32 | 1/2" | N | 89063 | B-1 | N | 0 | N89069 | N81056 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
O13013 | 7A | 32 | 1" | O | 13013 | 1CS2 | P | 50 | O13020 | VZ14016 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O13020 | 7A | 32 | 3/4" | O | 13020 | 1CS2 | P | 50 | O13007 | O13009 | 7.0/6.0 | 180.0/180.0 | 5.26/5.26 | 40.0/60.0 |  | 10.93 | 28.5 | IO | OIL | L | - | - | <1.5 | 40 | sh.6 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-021-01 |  | M | N | 110 | N | 235 | 23,25
O15014 |  | 32 | 1" | O | 15014 | B4S2 | ET | 30 | 32-D-1501 | VZ15006 | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
O20003 | 08 | 32 | 1/4" | O | 20003 | 1FS4 | N | 0 | 32-Z-2005 | 32-R-2000 | 70.0 | 150.0 | 60.0 | 30.0 |  | 105.15 | 148.95 | IO | OIL | L | - | - | <1.5 | 30 | sh.11 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-040-01 |  | M | N | 110 | N | 245 | 23,25
O13001 |  | 32 | 1-1/2" | O | 13001 | 1CS2 | ST | 30 | 32-E-1300 | O13021 | 6.0 | 200.0 | 5.0 | 70.0 |  | 9.62 | 28.5 | IO | OIL | L | - | - | <1.5 | 70 | sh.6 | 2 | Art 4.3 | NA | N | 27 | N | 32-P-025-01 |  | M | N | 010 | N | 238 | 23,25
BU73050 | 08 | 32 | 1" | BU | 73050 | D20S1 | N | 0 | 32-D-7302 | 32-P-7300 | 46.6/46.6 | -7.0/100.0 | 32.0 | 50.0 |  | 69.9 | 153.15 | H | 1-BUTENE | L | - | - | >1.5 | 50 | sh.55 | 1 | II | MOD.A2 | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 725 | 15
BU73073 | 08 | 32 | 2" | BU | 73073 | B32S1 | N | 0 | 32-S-7302B | BU73047 | 14.0/14.0 | 110.0/-7.0 | 6.0 | 40.0 |  | 21 | 29.4 | H | 1-BUTENE | L | - | - | >1.5 | 40 | sh.54 | 1 | I | MOD.A | Y | 1 | N | 32-P-001-02 |  | F | N | 140 | N | 731 | 15
CD31002 | 08 | 32 | 1/2" | CD | 31002 | 1CS2 | N | 0 | NITROGEN CONNECTION | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD31002 | 08 | 32 | 1" | CD | 31002 | 1CS2 | N | 0 | NITROGEN CONNECTION | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.23 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CD34013 | 08 | 32 | 1/2" | CD | 34013 | 1IS5 | N | 0 | CO2 CYLINDER AT GROUND LEVEL (130 BARG MAX) | TO SAFE LOCATION | 130.0 | 150.0 | 50.0 | 80.0 |  | 75 | 75 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 80 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 292
CD34015 | 08 | 32 | 1/2" | CD | 34015 | 1CS2 | ET | 30 | CD34009 | NITROGEN CONNECTION | 3.5 | 100.0 | 1.0 | 40.0 |  | 1.5 | 1.5 | N | CARBON DIOXIDE/MODIFIER RC | G | - | - | >1.5 | 40 | sh.26 | 2 | Art 4.3 | NA | N | NR | N | 32-P-043-03 |  | F | N | 100 | N | 288
CHWR61012 |  | 32 | 3/4" | CHWR | 61012 | B-1 | CF | 25 | CHWR61013 | TP-030 (CHWR61017) | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61012 |  | 32 | 10" | CHWR | 61012 | B-1 | CF | 40 | CHWR61013 | TP-030 (CHWR61017) | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.42 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CO26029 | 08 | 32 | 3/4" | CO | 26029 | 1IS5 | N | 0 | 32-R-2300 | 32-R-2300 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO26035 | 08 | 32 | 1/2" | CO | 26035 | 1IS5 | N | 0 | 1 ST. EMERGENCY KILLER SYSTEM | CO26025 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.22 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-01 |  | F | N | 340 | N | 289 | 8
CO42016 | 08 | 32 | 3/4" | CO | 42016 | 1IS5 | N | 0 | CO42003 | 32-R-4001 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
CO42017 | 08 | 32 | 3/4" | CO | 42017 | 1IS5 | N | 0 | CO42018 | CO42003 | 180.0 | 50.0 | 150.0 | 30.0 |  | 225 | 225 | N | CARBON MONOXIDE/MODIFIER C | G | - | - | >1.5 | 30 | sh.32 | 1 | Art 4.3 | NA | N | NR | N | 32-P-043-02 |  | F | N | 340 | N | 289 | 8
VA14001 | 08 | 32 | 2" | VA | 14001 | B4S2 | N | 0 | CHWS14012 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.7 | 2 | NA | NA | NA | 6 | N | 32-U-023-02 |  | E | N | 000 | N | 183
VA14003 | 08 | 32 | 2" | VA | 14003 | B4S2 | N | 0 | N14026 | TO SAFE LOCATION OUT SIDE CATALYST BUILDING | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.7 | 2 | NA | NA | NA | 6 | N | 32-P-026-01 |  | E | N | 000 | N | 183
VA23004 | 08 | 32 | 1-1/2" | VA | 23004 | B4S2 | N | 0 | TP 7 (LO230132) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.16A | 2 | NA | NA | NA | 6 | N | 32-P-044-02 |  | E | N | 000 | N | 183
VA23005 | 08 | 32 | 6" | VA | 23005 | B4S2 | N | 0 | TP-19 (D-2500) | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.16B | 2 | NA | NA | NA | 6 | N | 32-P-044-03 |  | E | N | 000 | N | 183
VA61004 | 08 | 32 | 1" | VA | 61004 | B4S2 | N | 0 | CHWS61001 | TO SAFE LOCATION | 0.5 | 150.0 | 0.05/0.05 | 40.0/130.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.42 | 2 | NA | NA | NA | 6 | N | 32-U-023-01 |  | E | N | 000 | N | 183
VZ31006 |  | 32 | 1-1/2" | VZ | 31006 | C42S1 | HB | 30 | 32-S-3101B | O31012 | 25.0/25.0 | 190.0/-45.0 | 18.0 | 85.0 |  | 37.64 | 76.65 | H | VESSEL TRIM | LG | - | - | >1.5 | 85 | sh.23 | 1 | I | MOD.A | Y | 20 | N | 32-P-047-01 |  | G | N | 141 | N | 365 | 10
FO10010 | 08 | 32 | 1/2" | FO | 10010 | 3DS3 | N | 0 | TEA10007 | FO10002 | 12.0 | 150.0 | 6.0 | 40.0 |  | 18.03 | 74.4 | IO | FLUSHING OIL / MINERAL OIL | L | - | - | <1.5 | 40 | sh.4 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-020-01A |  | F | N | 343 | N | 220 | 8,23,29,25
BDL01004 | 08 | 32 | 1/2" | BDL | 01004 | B32S1 | N | 0 | OG01004 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01014 | 08 | 32 | 1" | BDL | 01014 | B32S1 | N | 0 | PR01002 | BDL01039 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-03 |  | G | N | 141 | N | 460 | 10
BDL01024 | 08 | 32 | 3/4" | BDL | 01024 | B32S1 | N | 0 | BU01003 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01035 | 08 | 32 | 3/4" | BDL | 01035 | B32S1 | N | 0 | ET01001 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL01035 | 08 | 32 | 1" | BDL | 01035 | B32S1 | N | 0 | ET01001 | BDL01043 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.1 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
BDL23054 | 08 | 32 | 3/4" | BDL | 23054 | B32S1 | N | 0 | PR22015 | BDL23050 | 3.5/3.5 | -45.0/180.0 | 0.2/1.4 | 60.0/31.0 |  | 4.66 | 26.46 | P | LP BLOW DOWN | G | - | - | >1.5 | 31 | sh.14 | 1 | Art 4.3 | NA | N | 1 | N | 32-U-031-01 |  | G | N | 141 | N | 460 | 10
FW68M25 | 08 | 32 | 2" | FW | 68M25 | B-13 | N | 0 | FW68K06 | FW68M23 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M25 | 08 | 32 | 4" | FW | 68M25 | B-13 | N | 0 | FW68K06 | FW68M23 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68M46 | 08 | 32 | 1-1/2" | FW | 68M46 | B-13 | N | 0 | FW68M05 | SWIVEL JOINT | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.98 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-11 |  | - | Y | 000 | - | 74
FW68N01 | 08 | 32 | 1" | FW | 68N01 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N41 | 08 | 32 | 1-1/2" | FW | 68N41 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N41 | 08 | 32 | 3" | FW | 68N41 | B-13 | N | 0 | FW68N08 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N50 | 08 | 32 | 1" | FW | 68N50 | B-13 | N | 0 | FW68N51 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
FW68N50 | 08 | 32 | 1-1/2" | FW | 68N50 | B-13 | N | 0 | FW68N51 | MSN-003 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.99 | 2 | Art 4.3 | NA | N | 4 | N | 32-U-043-12 |  | - | Y | 000 | - | 74
JWS64075 | 08 | 32 | 2" | JWS | 64075 | B-1 | N | 0 | JWS64054 | 32-E-1451 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS64047 | 08 | 32 | 8" | JWS | 64047 | B-1 | N | 0 | JWS64054 | 32-E-2300 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
N89001 | 08 | 32 | 4" | N | 89001 | B-1 | N | 0 | N01001 | N91013 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
FW68B27 | 08 | 45 | 1-1/2" | FW | 68B27 | B-7 | N | 0 | FW68A88 | 45-HR-6811 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
FW68B27 | 08 | 45 | 2" | FW | 68B27 | B-7 | N | 0 | FW68A88 | 45-HR-6811 | 16.0 | 35.0 | 12.0/2.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-043-01 |  | E | N | 000 | N | 75
PR31018 |  | 32 | 2" | PR | 31018 | D20S1 | HB | 30 | JLS31012 | PR31019 | 55.0/55.0 | -45.0/120.0 | 42.0/42.0 | 40.0/73.0 |  | 82.5 | 150.8 | H | PROPYLENE | L | - | - | >1.5 | 40 | sh.23 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-047-01 |  | F | N | 141 | N | 330 | 15
CHWS15002 |  | 32 | 1/2" | CHWS | 15002 | B-1 | CF | 25 | CHWS14007 | 32-PK-1500/N12 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
FW68D11 | 08 | 45 | 3/4" | FW | 68D11 | B-13 | N | 0 | XV-6815A/TP-07 | FW68D10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68D12 | 08 | 45 | 3/4" | FW | 68D12 | B-13 | N | 0 | XV-6816A/TP-07 | FW68D10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68D13 | 08 | 45 | 3/4" | FW | 68D13 | B-13 | N | 0 | XV-6817A/TP-07 | FW68D10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
FW68D14 | 08 | 45 | 3/4" | FW | 68D14 | B-13 | N | 0 | XV-6818A/TP-07 | FW68D10 | 16.0 | 35.0 | 12.0/2.0 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-01 |  | - | Y | 000 | - | 74
IA620BD | 08 | 32 | 3/4" | IA | 620BD | B-13 | N | 0 | IA01001 | 32-HV-0110A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BD | 08 | 32 | 1" | IA | 620BD | B-13 | N | 0 | IA01001 | 32-HV-0110A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BE | 08 | 32 | 3/4" | IA | 620BD | B-13 | N | 0 | IA62076 | 32-HV-3501 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BE | 08 | 32 | 1" | IA | 620BD | B-13 | N | 0 | IA62076 | 32-HV-3501 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BF | 08 | 32 | 3/4" | IA | 620BF | B-13 | N | 0 | IA62077 | 32-PV-6601 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BG | 08 | 32 | 3/4" | IA | 620BG | B-13 | N | 0 | IA62078 | 32-TV-1602 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BH | 08 | 32 | 1-1/2" | IA | 620BH | B-13 | N | 0 | IA620AO | 32-FV-6401 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BI | 08 | 32 | 3/4" | IA | 620BI | B-13 | N | 0 | IA62077 | 32-LP-1001 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BJ | 08 | 32 | 3/4" | IA | 620BJ | B-13 | N | 0 | IA62078 | 32-LP-1403 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BK | 08 | 32 | 3/4" | IA | 620BK | B-13 | N | 0 | IA620BJ | 32-LP-1402 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA620BL | 08 | 32 | 3/4" | IA | 620BL | B-13 | N | 0 | IA6200R | 32-LP-1401 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA68D09 | 08 | 45 | 1/2" | IA | 68D09 | B-13 | N | 0 | XV-6815A/TP04 | XV-6815A/TP-05 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68K12 | 08 | 32 | 1" | IA | 68K12 | B-13 | N | 0 | IA68K11 | XV-6803A/TP03 | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IW64013 |  | 32 | 3/4" | IW | 64013 | B-1 | N | 0 | DELETED | DELETED | 10.0 | 50.0 | 5.0 | 35.0 |  | 15 | 29.4 | H | INDUSTRIAL WATER | L | - | - | <1.5 | 35 | sh.111 | 2 | Art 4.3 | NA | N | 1 | N | deleted |  | E | N | 000 | N | 43 | DELETED
LC21002 |  | 32 | 3/4" | LC | 21002 | B-5 | HB | 30 | LS21001 | LS21001 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23051 | 08 | 32 | 1/2" | LC | 23051 | B-5 | HB | 30 | LS23048 | LS23048 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23053 | 08 | 32 | 1/2" | LC | 23053 | B-5 | HB | 30 | LS23036 | LS23036 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23054 | 08 | 32 | 1/2" | LC | 23054 | B-5 | HB | 30 | LS23037 | LS23037 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23057 | 08 | 32 | 3/4" | LC | 23057 | B-5 | HB | 30 | LS23038 | LS23038 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23058 | 08 | 32 | 3/4" | LC | 23058 | B-5 | HB | 30 | LS23040 | LS23040 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC23060 | 08 | 32 | 3/4" | LC | 23060 | B-5 | HB | 30 | LS630AM | LS630AM | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC24014 | 08 | 32 | 3/4" | LC | 24014 | B-5 | HB | 30 | LS24016 | LS24016 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
LC24016 | 08 | 32 | 3/4" | LC | 24016 | B-5 | HB | 30 | LS63073 | LS63073 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-046-01 |  | E | Y | 000 | N | 130
LC24017 | 08 | 32 | 3/4" | LC | 24017 | B-5 | HB | 30 | LS24011 | LS24011 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-046-01 |  | E | Y | 000 | N | 130
LC43004 | 08 | 32 | 3/4" | LC | 43004 | B-5 | HB | 30 | LS43010 | LS43010 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-047-03 |  | E | Y | 000 | N | 130
LC50012 | 08 | 32 | 1/2" | LC | 50012 | B-5 | HB | 30 | LS50046 | LS50046 | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-050-01 |  | E | Y | 000 | N | 130
LC6300Y | 08 | 32 | 1-1/2" | LC | 6300Y | B-5 | HB | 40 | LC6300X | LC6300Y | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300Y | 08 | 32 | 2" | LC | 6300Y | B-5 | HB | 40 | LC6300X | LC6300Y | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300Y | 08 | 32 | 1/2" | LC | 6300Y | B-5 | HB | 40 | LC6300X | LC6300Y | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LC6300Y | 08 | 32 | 3/4" | LC | 6300Y | B-5 | HB | 40 | LC6300X | LC6300Y | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-060-01 |  | E | Y | 000 | N | 130
LS31037 | 08 | 32 | 1/2" | LS | 31037 | B-5 | HB | 60 | JLS31011 | LC31040 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-P-008-01 |  | E | N | 000 | N | 90
LS89050 | 08 | 32 | 1" | LS | 89050 | B-5 | HB | 70 | LS89054 | SP-04-189A0-08 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89050 | 08 | 32 | 3/4" | LS | 89050 | B-5 | HB | 70 | LS89054 | SP-04-189A0-08 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS89055 | 08 | 32 | 2" | LS | 89055 | 3CS6 | HB | 40 | 32-S-8905/P1 | LS63202 | 6.5/-1.0 | 180.0/150.0 | 1.0/1.0 | 150.0/100.0 |  | 10.15 | 28.5 | H | STEAM - LP | G | - | - | >1.5 | 100 | sh.68N | 2 | Art 4.3 | NA | N | 27 | N | 32-P-070-11 |  | M | N | 000 | N | 91
N32026 | 08 | 32 | 1-1/2" | N | 32026 | B4S1 | N | 0 | N32017 | 32-PK-3200B/TP26B | 12.0 | 100.0 | 1.37 | 30.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 30 | sh.24K | 2 | Art 4.3 | NA | N | 1 | N | 32-P-047-05 |  | E | N | 000 | N | 148
N6700I |  | 32 | 1" | N | 6700I | B1 | N | 0 | N67020 | 32-PK-3200A/TP42A | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 26.46 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.85 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-003-06 |  | E | N | 000 | N | 140
N80027 |  | 32 | 2" | N | 80027 | 1CS2 | N | 0 | 32-PK-8102/TP-002 | 32-PK-8102/TP-003 | 12.0 | 80.0 | 6.0 | 20.0 |  | 15.96 | 25.65 | P | LP UNPURIFIED NITROGEN | G | - | - | >1.5 | 20 | sh.61 | 2 | Art 4.3 | NA | N | 5 | N | 32-P-060-01_B |  | M | N | 000 | N | 166
PA86001 |  | 32 | 1/2" | PA | 86001 | B-1 | N | 0 | PA89039 | 32-P-8601/C/TP03 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.112 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89030 |  | 32 | 3/4" | PA | 89030 | B-1 | N | 0 | PA89032 | 32-US-1211-09 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.112 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
PA89052 |  | 32 | 3/4" | PA | 89052 | B-1 | N | 0 | PA89053 | 32-US-1211-02 | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.112 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
VA0000I | 08 | 45 | 4" | VA | 0000I | B-1 | N | 0 | ACW-SM-130P/VENT | To Atm | 0.5 | 100.0 | 0.05 | 40.0 |  | .55 | 26.46 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 40 | sh.108 | 2 | NA | NA | NA | 1 | N | 45-ACW-001-01 |  | E | N | 000 | N | 181
VZ10001 | 08 | 32 | 4" | VZ | 10001 | 3DS3 | N | 0 | 2-D-1001/K1 | 32-LT-1001 | 12 | 150 | 1/0.5 | 30/30 |  | 0 | 0 | V | TEAL FEED TANK (D-1001) | L | - | - | >1.5 | 30 | sh.4 | 1 | II | MOD.A2 | Y | NR | Y | 32-P-020-01A |  | F | N | 343 | N | 264
VZ20001 | 08 | 32 | 1/4" | VZ | 20001 | 3FS3 | N | 0 | O20003 | 32-R-2000/P9 | 70/70 | 100/-45 | 40 | 10 |  | 105 | 105 | H | TRIM | L | - | - | >1.5 | 10 | sh.11 | 1 | Art 4.3 | NA | N | NR | Y | 32-P-040-01 |  | F | N | 343 | N | 267
VZ23007 | 08 | 32 | 2" | VZ | 23007 | C42S5 | HB | 30 | 32-S-2300/XXX | 32-TXE-2318 | 42 | 150/-45 | 33 | 90 |  | 0 | 0 | V | TRIM | GS | - | - | >1.5 | 90 | sh.17 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-044-01 |  | G-2 | N | 141 | N | 524
VZ50013 | 08 | 32 | 3/4" | VZ | 50013 | B-1 | N | 0 | 32-E-5001/P4 | - | 9 | 180 | 4/3.5 | 38/30 |  | 13.5 | 13.5 | H | TRIM | L | - | - | >1.5 | 38 | sh.35 | 2 | Art 4.3 | NA | N | 1 | Y | 32-P-050-02 |  | E | N | 000 | N | 20
VZ60005 | 08 | 32 | 2" | VZ | 60005 | C42S2 | HB | 30 | 32-D-6011/K1/K2/K3 | 32-PT-TE | 20 | -45/185 | 0.1 | 20 |  | 0 | 0 | V | TRIM | GS | - | - | >1.5 | 20 | sh.41 | 1 | I | MOD.A1 | Y | 20 | Y | 32-U-031-02 |  | F-2 | N | 141 | N | 484
VZ60005 | 08 | 32 | 3" | VZ | 60005 | C42S2 | HB | 30 | 32-D-6011/K1/K2/K3 | 32-PT-TE | 20 | -45/185 | 0.1 | 20 |  | 0 | 0 | V | TRIM | GS | - | - | >1.5 | 20 | sh.41 | 1 | II | MOD.A2 | Y | 20 | Y | 32-U-031-02 |  | F-2 | N | 141 | N | 484
VZ60006 | 08 | 32 | 2" | VZ | 60006 | B32S1 | ST | 30 | 32-D-6002/K1/K2 | 32-TI/TE | 3.5 | -45/185 | 0.1 | 20 |  | 0 | 0 | V | TRIM | G | - | - | >1.5 | 20 | sh.41 | 1 | I | MOD.A1 | Y | 20 | N | 32-U-031-02 |  | G | N | 141 | N | 491
VZ61001 | 08 | 32 | 2" | VZ | 61001 | B-1 | CF | 25 | 32-D-6100_K1/K2 | 32-TI/TE | 9 | 190 | 4.5 | 2 |  | 0 | 0 | V | TRIM | L | - | - | <1.5 | 2 | sh.42 | 2 | Art 4.3 | NA | N | 20 | Y | 32-U-031-02 |  | E | N | 010 | N | 58
VZ71008 | 08 | 32 | 2" | VZ | 71008 | C3S1 | HA | 70 | 32-T-7110B/K1A | 32-TE | 30/38.3 | 100/250 | 2/12 | 210/250 |  | 0 | 0 | V | TRIM | G | - | - | >1.5 | 100 | sh.48 | 1 | II | MOD.A2 | Y | 28 | Y | 32-P-006-02 |  | C | N | 041 | N | 318
VZ81006 | 08 | 32 | 3" | VZ | 81006 | 1CS2 | N | 0 | 32-S-8106/K1A | 32-PDT-81106 | 0.1 | 100 | 0.15 | 40 |  | 0 | 0 | V | TRIM | S | - | - | <1.5 | 40 | sh.62 | 2 | NA | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 446
VZ81006 | 08 | 32 | 3/4" | VZ | 81006 | 1CS2 | N | 0 | 32-S-8106/K1B | 32-PDT-8115 | 0.1 | 100 | 0.15 | 40 |  | 0 | 0 | V | TRIM | S | - | - | <1.5 | 40 | sh.62 | 2 | Art 4.3 | NA | N | NR | N | 32-P-061-04 |  | G | N | 200 | N | 446
VZ86002 | 08 | 32 | 3" | VZ | 86002 | QXC25S1 | N | 0 | 32-D-8600 | 32-TE | 10 | 180 | 0/0.5 | 36/100 |  | 0 | 0 | V | TRIM | L | - | - | <1.5 | 36 | sh.65 | 1 | Art 4.3 | NA | N | NR | Y | 32-P-062-01 |  | M | N | 1X4 | N | 604
VZ86002 | 08 | 32 | 2" | VZ | 86002 | QXC25S1 | N | 0 | 32-D-8600 | 32-TE | 10 | 180 | 0/0.5 | 36/100 |  | 0 | 0 | V | TRIM | L | - | - | <1.5 | 36 | sh.65 | 1 | Art 4.3 | NA | N | NR | Y | 32-P-062-01 |  | M | N | 1X4 | N | 604
WW69002 | 08 | 32 | 2" | WW | 69002 | B4S2 | N | 0 | 32-ES-6907 | - | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.90 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-045-01 |  | E | N | 000 | N | 87
WW69D01 | 08 | 32 | 2" | WW | 69D01 | B4S2 | N | 0 | 32-ES-6907 | - | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.118 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-045-01 |  | E | N | 000 | N | 87
WW80012 |  | 32 | 1/2" | WW | 80012 | B4S2 | N | 0 | 32-S-8011 | TO OD FUNNEL | 1.0 | 82.0 | 0.0 | 40.0 |  | 0 | 29.4 | V | WASTE WATER | L | - | - | <1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-060-01_A |  | E | N | 000 | N | 4145
WW80013 |  | 32 | 1/2" | WW | 80013 | B4S2 | N | 0 | 32-E-8000 | TO OD FUNNEL | 1.0 | 82.0 | 0.0 | 40.0 |  | 0 | 29.4 | V | WASTE WATER | L | - | - | <1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-060-01_A |  | E | N | 000 | N | 4145
WW90F03 |  | 32 | 1/2" | WW | 90F03 | B4S2 | N | 0 | 19-S-9052 | TO OD FUNNEL | 1.0 | 82.0 | 0.0 | 40.0 |  | 0 | 29.4 | V | WASTE WATER | L | - | - | <1.5 | 40 | sh.102 | 2 | Art 4.3 | NA | N | 1 | N | 32-P-060-01_A |  | E | N | 000 | N | 4145
FW68B93 | 08 | 45 | 10" | FW | 68B93 | UGB-1PE | N | 0 | FW68A53 | FW68A54 | 16.0 | 35.0 | 12.0/7.5 | 20.0/12.0 |  | 24 | 29.4 | H | FIRE WATER | L | - | - | <1.5 | 12 | sh.4 | 2 | Art 4.3 | NA | N | 3LPE | N | 45-U-043-01 |  | E | N | 000 | N | 76 | 9
LS02004 | 08 | 32 | 3/4" | LS | 2004 | B-5 | HB | 60 | LS63177 | LS02004 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
IA620AT | 08 | 32 | 3/4" | IA | 620AT | B-13 | N | 0 | IA62083 | - | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
LS02004 | 08 | 32 | 1/2" | LS | 2004 | B-5 | HB | 60 | LS63177 | LC02004 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-052-01 |  | E | N | 000 | N | 90
LS6300X | 08 | 32 | 2" | LS | 6300X | B-5 | HB | 80 | LS63189 | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-060-01 |  | E | N | 000 | N | 90
LS6300X | 08 | 32 | 1/2" | LS | 6300X | B-5 | HB | 80 | LS63189 | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-060-01 |  | E | N | 000 | N | 90
LS6300X | 08 | 32 | 3/4" | LS | 6300X | B-5 | HB | 80 | LS63189 | - | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-U-060-01 |  | E | N | 000 | N | 90
LS31036 | 08 | 32 | 1/2" | LS | 31036 | B-5 | HB | 60 | JLS31011 | LC31039 | 6.5/-1.0 | 250.0/170.0 | 4.5/4.0 | 230.0/200.0 |  | 10.18 | 29.4 | H | STEAM - LP | G | - | - | >1.5 | 200 | sh.117 | 2 | Art 4.3 | NA | N | NR | N | 32-P-008-01 |  | E | N | 000 | N | 90
PA62070 | 08 | 32 | 3/4" | PA | 62070 | B-1 | N | 0 | PA62072 | - | 10.0 | 60.0 | 8.0 | 40.0 |  | 13.3 | 26.46 | P | PLANT AIR | G | - | - | >1.5 | 40 | sh.112 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-091-01 |  | E | N | 000 | N | 190
WW64014 | 08 | 32 | 1" | WW | 64014 | B4S2 | N | 0 | - | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-050-01 |  | E | N | 000 | N | 87
WW64014 | 08 | 32 | 2" | WW | 64014 | B4S2 | N | 0 | - | WW64001 | 9.0 | 180.0 | 3.0 | 100.0 |  | 13.54 | 29.4 | H | WASTE WATER | L | - | - | >1.5 | 100 | sh.106 | 2 | Art 4.3 | NA | N | 1 | N | 45-U-050-01 |  | E | N | 000 | N | 87
PR36041 | 08 | 32 | 1" | PR | 36041 | B4S1 | N | 0 | E-3601 | D-3605 | 10.0/10.0 | 180.0/-10.0 | 5.5/0.6 | 107.0/45.0 |  | 15.04 | 29.4 | H | PROPYLENE | G | - | - | >1.5 | 45 | sh.28 | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-021-02 |  | C | Y | 141 | N | 397 | ,10
LC71005 | 08 | 32 | 1/2" | LC | 71005 | B-5 | HB | 30 | LS71012 | - | 6.5 | 180.0 | 4.0/2.0 | 150.0/133.0 |  | 9.78 | 29.4 | H | STEAM CONDENSATE LP | LG | - | - | >1.5 | 133 | sh.117 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-052-01 |  | E | Y | 000 | N | 130
VZ71009 | 08 | 32 | 3/4" | VZ | 71009 | C3S1 | HB | 30 | 32-E-7100 | - | 38.3 | 250 | 32.6/32.6 | 50/100 |  | 0 | 0 | V | ETHYLENE | G | - | - | >1.5 | 50 | sh.48 | 1 | Art 4.3 | NA | N | 20 | Y | 32-P-006-02 |  | C | N | 041 | N | 316 | 10
VZ71009 | 08 | 32 | 1-1/2" | VZ | 71009 | C3S1 | HB | 30 | 32-E-7100 | - | 38.3 | 250 | 32.6/32.6 | 50/100 |  | 0 | 0 | V | ETHYLENE | G | - | - | >1.5 | 50 | sh.48 | 1 | II | MOD.A2 | Y | 20 | Y | 32-P-006-02 |  | C | N | 041 | N | 316 | 10
VZ81005 | 08 | 32 | 2" | VZ | 81005 | 5CS7 | N | 0 | 32-D-8107 | - | 0.1/0.5 | 100 | 0 | 90 |  | 0 | 0 | V | TRIM | GS | - | - | >1.5 | 90 | sh.62 | 1 | NA | NA | N | NR | N | 32-P-082-07 |  | M | N | 110 | N | 445
VZ91017 | 08 | 32 | 2" | VZ | 91017 | 5CS7 | N | 0 | 32-H-9001D | - | 0.1/-0.01 | 100.0/100.0 | 0.01/0.01 | 60.0/80.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 60 | sh.70 | 1 | NA | NA | NA | NR | N | 32-P-082-04 |  | M | N | 110 | N | 447 | 6,25,23
VZ91018 | 08 | 32 | 2" | VZ | 91018 | 5CS7 | N | 0 | 32-H-9001E | - | 0.1/-0.01 | 100.0/100.0 | 0.01/0.01 | 60.0/80.0 |  | 0 | 0 | V | VESSEL TRIM | S | - | - | <1.5 | 60 | sh.70 | 1 | NA | NA | NA | NR | N | 32-P-082-04 |  | M | N | 110 | N | 447 | 6,25,23
IA68R08 | 08 | 45 | 1/2" | IA | 68R08 | B-13 | N | 0 | 45-XV-6819A/ | 45-XV-6819A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68R09 | 08 | 45 | 1/2" | IA | 68R09 | B-13 | N | 0 | 45-XV-6824A | 45-XV-6824A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68D06 | 08 | 45 | 1/2" | IA | 68D06 | B-13 | N | 0 | XV-6816A | XV-6816A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68D07 | 08 | 45 | 1/2" | IA | 68D07 | B-13 | N | 0 | XV-6817A | XV-6817A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
IA68D08 | 08 | 45 | 1/2" | IA | 68D08 | B-13 | N | 0 | XV-6818A | XV-6818A | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 45-U-043-07 |  | - | N | 000 | - | 200
CHWR61018 | 08 | 32 | 1/2" | CHWR | 61018 | B-1 | CF | 25 | JCHW15001 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWR61019 | 08 | 32 | 1/2" | CHWR | 61019 | B-1 | CF | 25 | JCHW15001 | CHWR61002 | 9.0 | 100.0 | 5.5 | 6.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER RETURN | L | - | - | <1.5 | 6 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-02 |  | E | N | 010 | N | 51
CHWS61031 | 08 | 32 | 1/2" | CHWS | 61031 | B-1 | CF | 25 | JCHW15001 | CHWS61002 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
CHWS61032 | 08 | 32 | 1/2" | CHWS | 61032 | B-1 | CF | 25 | CHWS61002 | JCHW15001 | 9.0 | 100.0 | 6.0 | 2.0 |  | 13.5 | 29.4 | H | REFRIGERATION WATER SUPPLY | L | - | - | <1.5 | 2 | sh.79 | 2 | Art 4.3 | NA | N | 20 | N | 32-U-023-01 |  | E | N | 010 | N | 50
VA81004 | 08 | 32 | 6" | VA | 81004 | 4CS2 | N | 0 | 32-S-8108 | - | 0.5 | 80.0 | 0.05 | 60.0 |  | .55 | 25.65 | P | VENT TO ATMOSPHERE | G | - | - | >1.5 | 60 | sh.59 | 2 | NA | NA | NA | NR | N | 32-P-070-01 |  | M | N | 000 | N | 180
IA89078 | 08 | 32 | 1" | IA | 89078 | B-13 | N | 0 | IA62006 | - | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
IA89078 | 08 | 32 | 1-1/2" | IA | 89078 | B-13 | N | 0 | IA62006 | - | 10.0 | 60.0 | 7.0/4.5 | 40.0/40.0 |  | 10.5 | 10.5 | N | INSTRUMENT AIR | G | - | - | >1.5 | 40 | sh.126 | 2 | Art 4.3 | NA | N | 4 | N | 19-U-043-07 |  | - | N | 000 | - | 200
P50012 | 08 | 32 | 12" | P | 50012 | 1CR9 | P | 100 | 32-D-5001 | 32-D-5011 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 436 | ,16,10,18,13
CWS89008 | 08 | 32 | 1/2" | CWS | 89008 | B-1 | N | 0 | CWS64010 | JCW86011 | 7.5 | 100 | 5.5 | 26 |  | 11.25 | 29.4 | H | COOLING WATER SUPPLY | L | - | - | <1.5 | 26 | sh.107 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-021-02 |  | E | N | 000 | N | 12
P50012 | 08 | 32 | 1-1/2" | P | 50012 | 1CR9 | P | 100 | 32-D-5001 | 32-D-5011 | 5.0/-1.0 | 200.0/200.0 | 0.2 | 105.0 |  | 8.06 | 30 | H | POLYMER+GAS | GS | - | - | >1.5 | 105 | sh.34 | 1 | II | MOD.A2 | Y | NR | N | 32-P-050-01 |  | F-4 | N | 141 | N | 436 | ,16,10,18,13
PR36017 | 08 | 32 | 6" | PR | 36017 | B4S1 | N | 0 | E-3601 | D-3605 | 10 | 0 /+181 | 5.52 | 45 | <51 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y |  | >1.6 | 0 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | E | Y | 011 | N | 397 | REV04_PKG 32-PK-3600
PJW40006 | 08 | 32 | 24" | PJW | 40006 | B-1 | N | 0 | 32-E-2300 | JWR23002 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PJW40006 | 08 | 32 | 18" | PJW | 40006 | B-1 | N | 0 | 32-E-2300 | JWR23002 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PJW40006 | 08 | 32 | 14" | PJW | 40006 | B-1 | N | 0 | 32-E-2300 | JWR23002 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PJW40006 | 08 | 32 | 8" | PJW | 40006 | B-1 | N | 0 | 32-E-2300 | JWR23002 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 86
PJW40006 | 08 | 32 | 1-1/2" | PJW | 40006 | B-1 | N | 0 | JWS64047 | 32-E-2300 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW40003 | 08 | 32 | 24" | PJW | 40003 | B-1 | N | 0 | JWS64047 | 32-E-2300 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW40003 | 08 | 32 | 18" | PJW | 40003 | B-1 | N | 0 | JWS64047 | 32-E-2300 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW40003 | 08 | 32 | 14" | PJW | 40003 | B-1 | N | 0 | JWS64047 | 32-E-2300 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW40003 | 08 | 32 | 8" | PJW | 40003 | B-1 | N | 0 | JWS64047 | 32-E-2300 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 86
PJW40003 | 08 | 32 | 1-1/2" | PJW | 40003 | B-1 | N | 0 | JWS64047 | 32-E-2300 | 9.0 | 180.0 | 4.5/6.5 | 80/100 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | >1.5 | 80 | sh.16 | 2 | III | G | Y | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 86
O150101 | 08 | 32 | 1/2" | O | 150101 | HYS_O/2 | ET | 40 | TP1 (Battery Limit) | Line Number 150102/150103 | 0.5 | 150 | 0.05 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL FROM D-1501 | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150102 | 08 | 32 | 1/2" | O | 150102 | HYS_O/2 | ET | 40 | Line Number 150101 | 32-P-1500A (Metering Pump) | 0.5 | 150 | 0.05 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150103 | 08 | 32 | 1/2" | O | 150103 | HYS_O/2 | ET | 40 | Line Number 150101 | 32-P-1500B (Metering Pump) | 0.5 | 150 | 0.05 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150104 | 08 | 32 | 3/8" | O | 150104 | HYS_O | ET | 40 | 32-P-1500A (Metering Pump) | Line Number 150106 | 70 | 150 | 60.5 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150105 | 08 | 32 | 3/8" | O | 150105 | HYS_O | ET | 40 | 32-P-1500B (Metering Pump) | Line Number 150106 | 70 | 150 | 60.5 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150106 | 08 | 32 | 3/8" | O | 150106 | HYS_O | ET | 40 | Line Number 150104/150105 | 32-HV-1501 (V1 Valve) | 70 | 150 | 60.5 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150107 | 08 | 32 | 3/8" | O | 150107 | HYS_O | ET | 40 | 32-HV-1501 (V1 Valve) | 32-D-1500A (Metering Syringe) | 70 | 150 | 60.5 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150108 | 08 | 32 | 3/8" | O | 150108 | HYS_O | ET | 40 | 32-HV-1501 (V1 Valve) | 32-D-1500B (Metering Syringe) | 70 | 150 | 60.5 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150109 | 08 | 32 | 3/8" | O | 150109 | HYS_O | ET | 40 | TP10 (Battery Limit) | 32-HV-1505 (V4 Valve) | 70 | 150 | 60.253 | 30 | - | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | NA | N | - | N | - | REV05_PKG 32-PK-1500
O150110 | 08 | 32 | 1" | O | 150110 | HYS_O/2 | ET | 40 | 32-HV-1505 (V4 Valve) | TP2 (Battery Limit) | 0.5 | 150 | 0.05 | 30 | 880 | - | 105 | IO | HYDRAULIC OIL | L | N | - | <1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | - | N | - | REV05_PKG 32-PK-1500
CT150111 | 08 | 32 | 1" | CT | 150111 | HYS_C | CF | 40 | TP4 (Battery Limit) | Line Number 150112/150113 | 20 | 190 | 10 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 | N | - | REV05_PKG 32-PK-1500
CT150112 | 08 | 32 | 1" | CT | 150112 | HYS_C | CF | 40 | Line Number 150111 | 32-HV-1502A1/A2 (V2A Valves) | 20 | 190 | 10 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 | N | - | REV05_PKG 32-PK-1500
CT150113 | 08 | 32 | 1" | CT | 150113 | HYS_C | CF | 40 | Line Number 150111 | 32-HV-1502B1/B2 (V2B Valves) | 20 | 190 | 10 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 | N | - | REV05_PKG 32-PK-1500
CT150114 | 08 | 32 | 1" | CT | 150114 | HYS_C | CF | 40 | 32-HV-1502A1/A2 (V2A Valves) | Line Number 150116 | 20 | 190 | 10 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | - | N | - | REV05_PKG 32-PK-1500
CT150115 | 08 | 32 | 1/2" | CT | 150115 | HYS_C | CF | 40 | 32-HV-1503A1/A2 (V3A Valves) | Line Number 150116 | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 | N | - | REV05_PKG 32-PK-1500
CT150116 | 08 | 32 | 1/2" | CT | 150116 | HYS_C | CF | 40 | Line Number 150114 / 150115 | 32-D-1500A (Metering Syringe) | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CT150117 | 08 | 32 | 1" | CT | 150117 | HYS_C | CF | 40 | 32-HV-1502B1/B2 (V2B Valves) | Line Number 150119 | 20 | 190 | 10 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CT150118 | 08 | 32 | 1/2" | CT | 150118 | HYS_C | CF | 40 | 32-HV-1503B1/B2 (V3B Valves) | Line Number 150119 | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CT150119 | 08 | 32 | 1/2" | CT | 150119 | HYS_C | CF | 40 | Line Number 150117 / 150118 | 32-D-1500B (Metering Syringe) | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CT150120 | 08 | 32 | 1/2" | CT | 150120 | HYS_C | CF | 40 | 32-HV-1503A1/A2 (V3A Valves) | Line Number 150121 | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CT150121 | 08 | 32 | 1/2" | CT | 150121 | HYS_C | CF | 40 | 32-HV-1503B1/B2 (V3B Valves) | Line Number 150122 | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CT150122 | 08 | 32 | 1/2" | CT | 150122 | HYS_C | CF | 40 | Line Number 150120 | TP5 (Battery Limit) | 70 | 190 | 50 | 6 | 970 | - | 105 | IO | CATALYST MUD | SL | N | - | <1.5 | - | sh.9A | 1 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | Acute. Tox. 4 Flam. Sol. 1 - | N | - | REV05_PKG 32-PK-1500
CHW150123 | 08 | 32 | 1/2" | CHW | 150123 | HYS_W | CF | 40 | TP7 (Battery Limit) | 32-D-1500A (Metering Syringe) | 9 | 190 | 5 | 6 | 1022 | - | 13,5 | IO | REFRIGERATED WATER | L | N | - | >1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | - | N | - | REV05_PKG 32-PK-1500
CHW150124 | 08 | 32 | 1/2" | CHW | 150124 | HYS_W | CF | 40 | TP6 (Battery Limit) | 32-D-1500A (Metering Syringe) | 9 | 190 | 5 | 6 | 1022 | - | 13,5 | IO | REFRIGERATED WATER | L | N | - | >1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | - | N | - | REV05_PKG 32-PK-1500
CHW150125 | 08 | 32 | 1/2" | CHW | 150125 | HYS_W | CF | 40 | TP9 (Battery Limit) | 32-D-1500A (Metering Syringe) | 9 | 190 | 5 | 6 | 1022 | - | 13,5 | IO | REFRIGERATED WATER | L | N | - | >1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | - | N | - | REV05_PKG 32-PK-1500
CHW150126 | 08 | 32 | 1/2" | CHW | 150126 | HYS_W | CF | 40 | TP8 (Battery Limit) | 32-D-1500A (Metering Syringe) | 9 | 190 | 5 | 6 | 1022 | - | 13,5 | IO | REFRIGERATED WATER | L | N | - | >1.5 | - | sh.9A | 2 | Art.4.3 | NA | N | NA | N | 32-P-026-04 |  | A | N | - | N | - | REV05_PKG 32-PK-1500
HCM240162 | 08 | 32 | 1-1/2" | HCM | 240162 | 3FS4 | N | 0 | TP 1 | 32-D-2400 | 45 | 150 | 31 | 10 | <50 | - | 68 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | II | MOD.H | Y | NA | Y | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
HCM240102 | 08 | 32 | 1-1/2" | HCM | 240102 | 3FS4 | N | 0 | 32-D-2400 | 32-C-2400 | 45 | 150 | 31 | 10 | <50 | - | 68 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | II | MOD.H | Y | NA | Y | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
HCM240104 | 08 | 32 | 1-1/2" | HCM | 240104 | 3FS4 | N | 0 | 32-C-2400 | 32-D-2401 | 50 | 200 | 39.7 | 36.1 | <50 | - | 75 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | II | MOD.H | Y | NA | Y | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
HCM240161 | 08 | 32 | 1-1/2" | HCM | 240161 | 3FS4 | N | 0 | 32-D-2401 | TP 2 | 50 | 200 | 39.7 | 36.1 | <50 | - | 75 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | II | MOD.H | Y | NA | Y | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
HCM240108 | 08 | 32 | 3/4" | HCM | 240108 | 3FS4 | N | 0 | 3/4"-HCM-240113-3FS4 | TP 5 | 17.7 | 100 | 1.37 | 50 | <50 | - | -27 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | A | N | 141 | N | - | REV3_PKG 32-PK-2400
HCM240109 | 08 | 32 | 3/4" | HCM | 240109 | 3FS4 | N | 0 | 3/4"-HCM-240114-3FS4 | 3/4"-HCM-240108-3FS4 | 17.7 | 100 | 1.37 | 50 | <50 | - | -27 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | A | N | 141 | N | - | REV3_PKG 32-PK-2400
HCM240113 | 08 | 32 | 3/4" | HCM | 240113 | 3FS4 | N | 0 | 32-D-2400 | 3/4"-HCM-240108-3FS4 | 42 | 150 | 1.37 | 50 | <50 | - | -63 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
HCM240114 | 08 | 32 | 3/4" | HCM | 240114 | 3FS4 | N | 0 | 32-D-2401 | 3/4"-HCM-240109-3FS4 | 49 | 150 | 1.37 | 50 | <50 | - | -74 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
HCM240120 | 08 | 32 | 1" | HCM | 240120 | 3FS4 | N | 0 | 1 1/2"-HCM-240161-3FS4 | 32-PSV-2494 | 50 | 200 | 39.7 | 36.1 | <50 | - | 75 | H | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | A | P | 141 | N | - | REV3_PKG 32-PK-2400
FL240157 | 08 | 32 | 2" | FL | 240157 | 3FS4 | N | 0 | 32-PSV-2494 | TP 3 | 50 | 200 | 1.37 | 50 | <50 | - | 75 | H | VENT TO FLARE | G | N | - | >1.5 | 0 | sh.21B | 1 | II | MOD.H | Y | NA | Y | 32-P-045-03 |  | A | P | 041 | N | - | REV3_PKG 32-PK-2400
N240173 | 08 | 32 | 1/2" | N | 240173 | TUBING | N | 0 | TP 6 | HEADER | 12 | 80 | 5.5 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.21A | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
N240103 | 08 | 32 | 1/2" | N | 240103 | TUBING | N | 0 | 1/2"-N-240173-TUBING | HEADER | 12 | 80 | 1 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.21A | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
N240105 | 08 | 32 | 1/2" | N | 240105 | TUBING | N | 0 | HEADER (1/2"-N-240173-TUBING) | 32-C-2400 | 12 | 80 | 5.5 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.21A | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
N240104 | 08 | 32 | 1/2" | N | 240104 | TUBING | N | 0 | HEADER (1/2"-N-240103-TUBING) | 32-C-2400 | 12 | 80 | 1 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.21A | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
HCM240112 | 08 | 32 | 1/2" | HCM | 240112 | TUBING | N | 0 | 32-C-2400 | 32-D-2404 | 12 | 80 | 1.37 | 50 | <50 | NA | NA | NA | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21B | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 141 | N | - | REV3_PKG 32-PK-2400
N240114 | 08 | 32 | 1/2" | N | 240114 | TUBING | N | 0 | 32-C-2400 | 32-D-2403 | 12 | 80 | 1 | 50 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.21B | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
VA240116 | 08 | 32 | 1" | VA | 240116 | TUBING | N | 0 | 32-PSV-2476 32-PSV-2480 32-D-2403 | TP 15 | 10 | 80 | 1 | 50 | <50 | NA | NA | NA | VENT TO ATM | G | N | - | >1.5 | 0 | sh.21A | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
FL240117 | 08 | 32 | 1" | FL | 240117 | 3FS4 | N | 0 | 32-D-2404 | 2"-FL-240157-3FS4 | 50 | 200 | 1.37 | 50 | <50 | - | 75 | H | VENT TO FLARE | G | - | - | >1.5 | - | sh.21A | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | A | N | 041 | N | - | REV3_PKG 32-PK-2400
HCM240110 | 08 | 32 | 1/2" | HCM | 240110 | TUBING | N | 0 | 32-D-2403 32-D-2404 | TP16 | 9 | 80 | 3 | 60 | <50 | NA | NA | NA | HYDROCARBON MIX FOR MULT. SERV. | G | N | - | >1.5 | 0 | sh.21A | 1 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 141 | N | - | REV3_PKG 32-PK-2400
LO240109 | 08 | 32 | 3/4" | LO | 240109 | TUBING | N | 0 | TP 11 | 32-LSL-2463 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240111 | 08 | 32 | 1/2" | LO | 240111 | TUBING | N | 0 | 32-LSL-2463 | 32-C-2400 | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240112 | 08 | 32 | 1" | LO | 240112 | TUBING | N | 0 | 32-LSL-2463 | 32-C-2400 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240103 | 08 | 32 | 3/4" | LO | 240103 | TUBING | N | 0 | 1"-LO-240112-TUBING | 32-P-2402 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240104 | 08 | 32 | 3/4" | LO | 240104 | TUBING | N | 0 | 32-P-2402 | 32-E-2405 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240101 | 08 | 32 | 3/4" | LO | 240101 | TUBING | N | 0 | 32-P-2401 | 3/4"-LO-240104-TUBING | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240108 | 08 | 32 | 1/2" | LO | 240108 | TUBING | N | 0 | 3/4"-LO-240101-TUBING | 3/4"-LO-240101-TUBING | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240107 | 08 | 32 | 3/4" | LO | 240107 | TUBING | N | 0 | 1/2"-LO-240108-TUBING | 32-PSV-2495 | 10 | 90 | 6 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240102 | 08 | 32 | 3/4" | LO | 240102 | TUBING | N | 0 | 3/4"-LO-240104-TUBING | 32-TCV-2461 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240105 | 08 | 32 | 3/4" | LO | 240105 | TUBING | N | 0 | 32-E-2405 | 32-TCV-2461 | 10 | 90 | 6 | 50 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240110 | 08 | 32 | 3/4" | LO | 240110 | TUBING | N | 0 | 32-TCV-2461 | 32-S-2401A/B | 10 | 90 | 6 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240106 | 08 | 32 | 3/4" | LO | 240106 | TUBING | N | 0 | 32-S-2401A/B | OIL HEADER | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240113 | 08 | 32 | 1/4" | LO | 240113 | TUBING | N | 0 | 3/4"-LO-240104-TUBING | 32-PCV-2499 | 10 | 90 | 6 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
LO240114 | 08 | 32 | 1/4" | LO | 240114 | TUBING | N | 0 | 32-PCV-2431 | 3/4"-LO-240106-TUBING | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-04 |  | - | N | 110 | N | - | REV3_PKG 32-PK-2400
JWS240150 | 08 | 32 | 3/4" | JWS | 240150 | TUBING | N | 0 | TP 12 | 1/2"-JWS-240116-TUBING | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWS240116 | 08 | 32 | 1/2" | JWS | 240116 | TUBING | N | 0 | 3/4"-JWS-240150-TUBING | 32-E-2405 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWS240103 | 08 | 32 | 1/2" | JWS | 240103 | TUBING | N | 0 | 3/4"-JWS-240150-TUBING | 32-C-2400 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWS240105 | 08 | 32 | 1/2" | JWS | 240105 | TUBING | N | 0 | 3/4"-JWS-240103-TUBING | 32-C-2400 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240106 | 08 | 32 | 1/2" | JWR | 240106 | TUBING | N | 0 | 32-C-2400 | 3/4"-JWR-240102-TUBING | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240104 | 08 | 32 | 1/2" | JWR | 240104 | TUBING | N | 0 | 32-C-2400 | 3/4"-JWR-240106-TUBING | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240117 | 08 | 32 | 1/2" | JWR | 240117 | TUBING | N | 0 | 32-E-2405 | 3/4"-JWR-240102-TUBING | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21C | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240102 | 08 | 32 | 3/4" | JWR | 240102 | TUBING | N | 0 | 1/2"-JWR-240106-TUBING 1/2"-JWR-240117-TUBING | 1"-JWR-240115-TUBING | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240111 | 08 | 32 | 3/4" | JWR | 240111 | TUBING | N | 0 | 3/4"-JWR-240102-TUBING | 32-TSV-2474 | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240112 | 08 | 32 | 1" | JWR | 240112 | TUBING | N | 0 | 32-TSV-2474 | BASEPLATE DRAIN | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
JWR240115 | 08 | 32 | 1" | JWR | 240115 | TUBING | N | 0 | 3/4"-JWR-240102-TUBING | TP 13 | 9 | 180 | 5 | 42 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.21D | 2 | Art.4.3 | NA | N | NA | N | 32-P-045-03 |  | - | N | 000 | N | - | REV3_PKG 32-PK-2400
P240100 | 08 | 32 | 36" | P | 240100 | C42S5 | N | 0 | 230022/TP1 | C-2500 | 42 | -45/150 | 27 | 85 | 35.5999 | 63 | 63 | H | POLYPROPYLENE | G | N | NA | >1.5 | -10 | sh.16A | 1 | III | MOD.G | Y | Y | Y | 32-P-044-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
P240101 | 08 | 32 | 36" | P | 240101 | C42S5 | N | 0 | C-2500 | 23024/TP2 | 42 | -45/150 | 28.8 | 89.13 | 37.699 | 63 | 63 | H | POLYPROPYLENE | G | N | NA | >1.5 | -10 | sh.16A | 1 | III | MOD.G | Y | Y | Y | 32-P-044-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
P230102 | 08 | 32 | 3/4" | P | 230102 | C42S5 | N | 0 | C-2500 | TP27 | 42 | -45/150 | 28.8 | 89.13 | 37.699 | 63 | 63 | H | POLYPROPYLENE | G | N | NA | >1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
LO230100 | 08 | 32 | 2" | LO | 230100 | SS316L | N | 0 | D-2500 | P-2500A | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230101 | 08 | 32 | 1-1/2" | LO | 230101 | SS316L | N | 0 | P-2500A | 230103 | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230102 | 08 | 32 | 2" | LO | 230102 | SS316L | N | 0 | D-2500 | P-2500B | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230103 | 08 | 32 | 1-1/2" | LO | 230103 | SS316L | N | 0 | P-2500B | E-2500A/B | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230104 | 08 | 32 | 1-1/2" | LO | 230104 | SS316L | N | 0 | 230101 | PSV 2568 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230105 | 08 | 32 | 2" | LO | 230105 | SS316L | N | 0 | PSV 2568 | D-2500 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230106 | 08 | 32 | 1-1/2" | LO | 230106 | SS316L | N | 0 | 230103 | PSV 2567 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230107 | 08 | 32 | 2" | LO | 230107 | SS316L | N | 0 | PSV 2567 | D-2500 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230108 | 08 | 32 | 1-1/2" | LO | 230108 | SS316L | N | 0 | 230103 | PCV 2591 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230109 | 08 | 32 | 1-1/2" | LO | 230109 | SS316L | N | 0 | PCV 2591 | D-2500 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230110 | 08 | 32 | 1" | LO | 230110 | SS316L | N | 0 | 230103 | TV 2551 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230111 | 08 | 32 | 1" | LO | 230111 | SS316L | N | 0 | E-2500A/B | TV 2551 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230112 | 08 | 32 | 1" | LO | 230112 | SS316L | N | 0 | TV 2551 | S-2500A/B | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230113 | 08 | 32 | 1" | LO | 230113 | SS316L | N | 0 | S-2500A/B | PV 2566 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230115 | 08 | 32 | 1-1/2" | LO | 230115 | SS316L | N | 0 | 230113 | D-2502 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230116 | 08 | 32 | 3/4" | LO | 230116 | SS316L | N | 0 | 230115 | D-2500 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230117 | 08 | 32 | 1" | LO | 230117 | SS316L | N | 0 | PV 2566 | TP20 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230118 | 08 | 32 | 1" | LO | 230118 | SS316L | N | 0 | TP12 | 230117 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230120 | 08 | 32 | 1-1/2" | LO | 230120 | SS316L | N | 0 | TP21 | 230123 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230121 | 08 | 32 | 3/4" | LO | 230121 | SS316L | N | 0 | 230120 | ME-2500 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230123 | 08 | 32 | 1" | LO | 230123 | SS316L | N | 0 | 230120 | C-2500_BEARING CARRIER | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230124 | 08 | 32 | 1" | LO | 230124 | SS316L | N | 0 | 230123 | C-2500_BEARING CARRIER | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230125 | 08 | 32 | 6" | LO | 230125 | SS316L | N | 0 | C-2500_BEARING CARRIER | TP22 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230126 | 08 | 32 | 1-1/2" | LO | 230126 | SS316L | N | 0 | ME-2500 | 230125 | 10 | 100 | 2.1 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230131 | 08 | 32 | 4" | LO | 230131 | SS316L | N | 0 | D-2500 | Z-2508 | 10 | 100 | 2.1 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
LO230132 | 08 | 32 | 3" | LO | 230132 | SS316L | N | 0 | C-2507 | TP18 | 10 | 100 | 2.1 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
JWS230100 | 08 | 32 | 1-1/2" | JWS | 230100 | B1 | N | 0 | TP3 | 230101 | 9 | 100 | 5.5 | 30 | 1000 | 13.5 | 13.5 | H | JACKET WATER SUPPLY | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-2500
JWS230101 | 08 | 32 | 1-1/2" | JWS | 230101 | B1 | N | 0 | 230100 | E-2500A | 9 | 100 | 5.5 | 30 | 1000 | 13.5 | 13.5 | H | JACKET WATER SUPPLY | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-2500
JWS230102 | 08 | 32 | 1-1/2" | JWS | 230102 | B1 | N | 0 | 230100 | E-2500B | 9 | 100 | 5.5 | 30 | 1000 | 13.5 | 13.5 | H | JACKET WATER SUPPLY | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-2500
JWR230100 | 08 | 32 | 1-1/2" | JWR | 230100 | B1 | N | 0 | E-2500A | 230102 | 9 | 100 | 5.5 | 42 | 1000 | 13.5 | 13.5 | H | JACKET WATER RETURN | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-2500
JWR230101 | 08 | 32 | 1-1/2" | JWR | 230101 | B1 | N | 0 | E-2500B | 230102 | 9 | 100 | 5.5 | 42 | 1000 | 13.5 | 13.5 | H | JACKET WATER RETURN | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-2500
JWR230102 | 08 | 32 | 1-1/2" | JWR | 230102 | B1 | N | 0 | 230100/101 | TP4 | 9 | 100 | 5.5 | 42 | 1000 | 13.5 | 13.5 | H | JACKET WATER RETURN | L | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | N | 32-P-044-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-2500
PR230100 | 08 | 32 | 1" | PR | 230100 | SS316L | ET | 50 | TP5 | E-2502 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230101 | 08 | 32 | 1" | PR | 230101 | SS316L | ET | 50 | E-2502 | S-2502A/B | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230102 | 08 | 32 | 3/4" | PR | 230102 | SS316L | ET | 50 | S-2502A/B | FV-2334 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230103 | 08 | 32 | 3/4" | PR | 230103 | SS316L | ET | 50 | FV-2334 | C-2500 - PORT A01 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230104 | 08 | 32 | 2" | PR | 230104 | SS316L | N | 0 | C-2500 - PORT A03 | TP7 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | II | MOD.A2 | Y | NA | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230105 | 08 | 32 | 1-1/2" | PR | 230105 | SS316L | N | 0 | TP6 | S-2501A/B | 12 | 80 | 6 | 31 | 1.98 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.16A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-026-04 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
PR230106 | 08 | 32 | 1-1/2" | PR | 230106 | SS316L | N | 0 | S-2501A/B | PDV-2567 | 12 | 80 | 6 | 31 | 1.98 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.16A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-026-04 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
PR230107 | 08 | 32 | 1-1/2" | PR | 230107 | SS316L | N | 0 | PDV-2567 | C-2500 - PORT A02 | 12 | 80 | 6 | 31 | 1.98 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.16A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-026-04 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
PR230108 | 08 | 32 | 3/4" | PR | 230108 | SS316L | N | 0 | 230106 | C-2500 - PORT A06 | 12 | 80 | 6 | 31 | 1.98 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.16A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-044-02 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
PR230109 | 08 | 32 | 1-1/2" | PR | 230109 | SS316L | N | 0 | C-2500 - PORT A05 | TP8 | 12 | 80 | 1.37 | 31 | 1.98 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.16A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-026-04 |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
PR230111 | 08 | 32 | 1/2" | PR | 230111 | SS316L | ET | 50 | 230102 | 230113 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230112 | 08 | 32 | 1/2" | PR | 230112 | SS316L | ET | 50 | 230111 | 230113 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
PR230113 | 08 | 32 | 1/2" | PR | 230113 | SS316L | ET | 50 | 230111 | C-2500 - PORT A22 | 55 | -45 to 150 | 40 | 100 to 120 | 26.4 | 82.5 | 82.5 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.16A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-044-02 |  | F | N | 0FG10 | N | - | REV3_PKG 32-PK-2500
IA230100 | 08 | 32 | 2" | IA | 230100 | SS316L | N | 0 | TP9 | HEADER | 10 | 60 | 7 | 40 | 8.68 | 15 | 15 | H | INSTRUMENT AIR | G | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | Y | 32-U-094-01A |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
IA230101 | 08 | 32 | 1" | IA | 230101 | SS316L | N | 0 | TP10 | HEADER | 10 | 60 | 7 | 40 | 8.68 | 15 | 15 | H | INSTRUMENT AIR | G | N | NA | <1.5 | 0 | sh.16B | 2 | Art.4.3 | NA | N | NA | Y | 32-U-094-01A |  | M | N | 0 | N | - | REV3_PKG 32-PK-2500
HCM320101 | 08 | 32 | 2" | HCM | 320101 | C42S1 | N | 0 | cylinder 1 (P&ID - purge & vent gas system) | D-3201A | 25 | -45 /+150 | 18.01 | 55 | <50 | 35.75 | 37.5 | H | Hydrocarbon mix for multiple services | G | N | - | >1.5 | -45 | sh.24K | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-04 |  | M | P | 010 | N | - | REV03_PKG 32-PK-3200 A/B
LO320106 | 08 | 32 | 2" | LO | 320106 | NEASS | N | 0 | TP 13A (2"-LO-32055-QXB-55) | P-3202A | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320107 | 08 | 32 | 1-1/2" | LO | 320107 | NEASS | N | 0 | P-3202A | PSV3273 / 1.1/2"-LO-320109-NEASS / 1.1/2"-LO-320108-NEASS / 1.1/2"-LO-320110-NEASS / 1.1/2"-LO-320111-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24C | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320108 | 08 | 32 | 1-1/2" | LO | 320108 | NEASS | N | 0 | 1.1/2""-LO-320107-NEASS | TP 16A (1.1/2"-LO-32003-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320109 | 08 | 32 | 1-1/2" | LO | 320109 | NEASS | N | 0 | 1.1/2""-LO-320107-NEASS | 1.1/2"-LO-320115-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320110 | 08 | 32 | 1-1/2" | LO | 320110 | NEASS | N | 0 | 1.1/2""-LO-320107-NEASS | 1.1/2"-LO-320112-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24C | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320111 | 08 | 32 | 1-1/2" | LO | 320111 | NEASS | N | 0 | 1.1/2""-LO-320107-NEASS | 1.1/2"-LO-320112-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24C | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320112 | 08 | 32 | 1-1/2" | LO | 320112 | NEASS | N | 0 | 1.1/2"-LO-320110-NEASS / 1.1/2"-LO-320111-NEASS | S-3201 AA / S-3201 BA | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320113 | 08 | 32 | 1-1/2" | LO | 320113 | NEASS | N | 0 | S-3201 AA / S-3201 BA | 1.1/2"-LO-320114-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24C | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320114 | 08 | 32 | 1-1/2" | LO | 320114 | NEASS | N | 0 | 1.1/2"-LO-320113-NEASS | TP 20A ('1.1/2"-LO-32001-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320115 | 08 | 32 | 1-1/2" | LO | 320115 | NEASS | N | 0 | S-3201 AA / S-3201 BA / 1.1/2"-LO-320109-NEASS | TP 18A ('1.1/2"-LO-32002-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWS320116 | 08 | 32 | 1" | JWS | 320116 | NEACS | N | 0 | TP 21A (2"-JWS-32002-B-1) | cylinder 1 | 9 | 0 /+100 | 5 | 30/60 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.24D | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWR320121 | 08 | 32 | 1" | JWR | 320121 | NEACS | N | 0 | cylinder 1 | TP 22A (1"-JWR-32006-B-1) | 9 | 0 /+100 | 4.5 | 63 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.24J | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWS320118 | 08 | 32 | 2" | JWS | 320118 | NEACS | N | 0 | TP 23A (2"-JWS-32021-B-1) | E-3202 A / E-3212 A | 9 | 0 /+100 | 5 | 30 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.24C | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWR320124 | 08 | 32 | 2" | JWR | 320124 | NEACS | N | 0 | E-3202 A / E-3212 A | TP 24A (2"-JWR-32004-B-1) | 9 | 0 /+100 | 4.5 | 30.85 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.24C | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
N320125 | 08 | 32 | 1" | N | 320125 | NEACS | N | 0 | TP 42A (1"-N-6700I-B-1) | PCV3277 | 12 | 0 /+80 | 6 | 20 | <50 | 18 | 18 | H | Low pressure unpurified nitrogen | G | N | - | >1.5 | 0 | sh.24E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
HCM320301 | 08 | 32 | 2" | HCM | 320301 | C42S1 | N | 0 | cylinder 1 (P&ID - purge & vent gas system) | D-3201 B | 25 | -45 /+150 | 18.01 | 55 | <50 | 35.75 | 37.5 | H | Hydrocarbon mix for multiple services | G | N | - | >1.5 | -45 | sh24a | 1 | II | MOD.A2 | Y | 1 | N | 32-P-047-04 |  | M | P | 010 | N | - | REV03_PKG 32-PK-3200 A/B
LO320306 | 08 | 32 | 2" | LO | 320306 | NEASS | N | 0 | TP 13B (2"-LO-32155-QXB-55) | P-3202B | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24c | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320307 | 08 | 32 | 1-1/2" | LO | 320307 | NEASS | N | 0 | P-3202B | PSV3281 / 1.1/2"-LO-320309-NEASS / 1.1/2"-LO-320308-NEASS / 1.1/2"-LO-320310-NEASS / 1.1/2"-LO-320311-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24l | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320308 | 08 | 32 | 1-1/2" | LO | 320308 | NEASS | N | 0 | 1.1/2"-LO-320307-NEASS | TP 16B (1.1/2"-LO-32103-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320309 | 08 | 32 | 1-1/2" | LO | 320309 | NEASS | N | 0 | 1.1/2"-LO-320307-NEASS | 1.1/2"-LO-320315-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320310 | 08 | 32 | 1-1/2" | LO | 320310 | NEASS | N | 0 | 1.1/2"-LO-320307-NEASS | 1.1/2"-LO-320312-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320311 | 08 | 32 | 1-1/2" | LO | 320311 | NEASS | N | 0 | 1.1/2"-LO-320307-NEASS | 1.1/2"-LO-320312-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320312 | 08 | 32 | 1-1/2" | LO | 320312 | NEASS | N | 0 | 1.1/2"-LO-320310-NEASS / 1.1/2"-LO-320311-NEASS | S-3201 AB / S-3201 BB | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320313 | 08 | 32 | 1-1/2" | LO | 320313 | NEASS | N | 0 | S-3201 AB / S-3201 BB | 1.1/2"-LO-320314-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320314 | 08 | 32 | 1-1/2" | LO | 320314 | NEASS | N | 0 | 1.1/2"-LO-320313-NEASS | TP 20B ('1.1/2"-LO-32101-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
LO320315 | 08 | 32 | 1-1/2" | LO | 320315 | NEASS | N | 0 | S-3201 AB / S-3201 BB / 1.1/2"-LO-320309-NEASS | TP 18B ('1.1/2"-LO-32102-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.24I | 1 | Art.4.3 | NA | N | 5 | N | 32-P-047-06 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWS320316 | 08 | 32 | 1" | JWS | 320316 | NEACS | N | 0 | TP 21B (2"-JWS-32002-B-1) | cylinder 1 | 9 | 0 /+100 | 5 | 30/60 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.24I | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWR320321 | 08 | 32 | 1" | JWR | 320321 | NEACS | N | 0 | cylinder 1 | TP 22B (1"-JWR-32006-B-1) | 9 | 0 /+100 | 4.5 | 63 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.24I | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWS320318 | 08 | 32 | 2" | JWS | 320318 | NEACS | N | 0 | TP 23B (2"-JWS-32021-B-1) | E-3202 B / E-3212 B | 9 | 0 /+100 | 5 | 30 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.24I | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
JWR320324 | 08 | 32 | 2" | JWR | 320324 | NEACS | N | 0 | E-3202 B / E-3212 B | TP 24B (2"-JWR-32004-B-1) | 9 | 0 /+100 | 4.5 | 30.85 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.24I | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
N320325 | 08 | 32 | 1" | N | 320325 | NEACS | N | 0 | TP 42B (1"-N-6700I-B-1) | PCV3298 | 12 | 0 /+80 | 6 | 20 | <50 | 18 | 18 | H | Low pressure unpurified nitrogen | G | N | - | >1.5 | 0 | sh.24I | 2 | Art.4.3 | NA | N | 1 | N | 32-P-047-04 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3200 A/B
HCM360102 | 08 | 32 | 14" | HCM | 360102 | C42S1 | N | 0 | D-3601 | cylinder 1 - stage 1 | 10 | -10 /+180 | 0.61 | 45 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
HCM360103 | 08 | 32 | 14" | HCM | 360103 | C42S1 | N | 0 | D-3603 | cylinder 3 - stage 1 | 10 | -10 /+180 | 0.61 | 45 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
HCM360104 | 08 | 32 | 10" | HCM | 360104 | C42S1 | P | 0 | cylinder 1 - stage 1 | D-3602 | 10 | -10 /+180 | 5.82 | 107 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
HCM360105 | 08 | 32 | 10" | HCM | 360105 | C42S1 | P | 0 | cylinder 3 - stage 1 | D-3604 | 10 | -10 /+180 | 5.82 | 107 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
HCM360112 | 08 | 32 | 12" | HCM | 360112 | B42S1 | N | 0 | D-3606 | cylinder 2 - stage 2 | 10 | -10 /+180 | 5.52 | 45 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
HCM360113 | 08 | 32 | 8" | HCM | 360113 | C42S1 | P | 0 | cylinder 2 - stage 2 | D-3607 | 25 | -45 /+180 | 22.01 | 106 | <50 | 35.75 | 37.5 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -45 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-03 |  | M | P | 010 | Y | - | REV03_PKG 32-PK-3600
HCM360118 | 08 | 32 | 2" | HCM | 360118 | B42S1 | N | 0 | D-3605 | TP116 ( 2"-BDL-36027-B32S1) | 10 | -10 /+180 | 5.52 | 45 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28B | 1 | I | MOD.A | Y | 1 | N | 32-P-048-03 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
LO320120 | 08 | 32 | 3" | LO | 320120 | NEASS | N | 0 | TP 137 ('3"-LO-36006-QXB-55) | P-3602 | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360120 | 08 | 32 | 1-1/2" | LO | 360120 | NEASS | N | 0 | P-3602 | PSV3693(2"-LO-360122-NEASS) 1.1/2"-LO-360121-NEASS '1.1/2"-LO-360123-NEASS '1.1/2"-LO-360124-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360122 | 08 | 32 | 1-1/2" | LO | 360122 | NEASS | N | 0 | PSV3693 (1.1/2"-LO-360120-NEASS) | 1.1/2"-LO-360127-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360121 | 08 | 32 | 1-1/2" | LO | 360121 | NEASS | N | 0 | 1.1/2"-LO-360120-NEASS | TP 140 (1.1/2"-LO-36006-QXB-55) | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360123 | 08 | 32 | 1-1/2" | LO | 360123 | NEASS | N | 0 | 1.1/2"-LO-360120-NEASS | 1.1/2"-LO-360125-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360124 | 08 | 32 | 1-1/2" | LO | 360124 | NEASS | N | 0 | 1.1/2"-LO-360120-NEASS | 1.1/2"-LO-360125-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360125 | 08 | 32 | 1-1/2" | LO | 360125 | NEASS | N | 0 | 1.1/2"-LO-360123-NEASS 1.1/2"-LO-360124-NEASS | 1.1/2"-LO-360126-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360126 | 08 | 32 | 1-1/2" | LO | 360126 | NEASS | N | 0 | 1.1/2"-LO-360125-NEASS | 1.1/2"-LO-360127-NEASS 1.1/2"-LO-360128-NEASS | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360127 | 08 | 32 | 1-1/2" | LO | 360127 | NEASS | N | 0 | 1.1/2"-LO-360126-NEASS | 1.1/2"-LO-36003-QXB-55 | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
LO360128 | 08 | 32 | 1-1/2" | LO | 360128 | NEASS | N | 0 | 1.1/2"-LO-360126-NEASS | 1.1/2"-LO-36002-QXB-55 | 10 | 0 /+100 | 6 | 50 | 872 | 15 | 15 | H | Lube Oil | L | N | - | >1.5 | 0 | sh.28D | 1 | Art.4.3 | NA | N | 5 | N | 32-P-048-04 |  | M | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360129 | 08 | 32 | 2" | JWS | 360129 | NEACS | N | 0 | TP 145 (2"-JWS-64079-B-1) | 1"-JWS-320130-NEACS 1"-JWS-320131-NEACS 1"-JWS-320132-NEACS | 9 | 0 /+100 | 5 | 30/50 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360130 | 08 | 32 | 1" | JWS | 360130 | NEACS | N | 0 | 2"-JWS-320129-NEACS | cylinder 1 stage 1 | 9 | 0 /+100 | 5 | 50 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360131 | 08 | 32 | 1" | JWS | 360131 | NEACS | N | 0 | 2"-JWS-320129-NEACS | cylinder 2 stage 2 | 9 | 0 /+100 | 5 | 50 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360132 | 08 | 32 | 1" | JWS | 360132 | NEACS | N | 0 | 2"-JWS-320129-NEACS | cylinder 3 stage 1 | 9 | 0 /+100 | 5 | 50 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWR360133 | 08 | 32 | 1" | JWR | 360133 | NEACS | N | 0 | cylinder 1 stage 1 | 2"-JWS-320136-NEACS | 9 | 0 /+100 | 4.5 | 53 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWR360134 | 08 | 32 | 1" | JWR | 360134 | NEACS | N | 0 | cylinder 2 stage 2 | 2"-JWS-320136-NEACS | 9 | 0 /+100 | 4.5 | 53 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWR360135 | 08 | 32 | 1" | JWR | 360135 | NEACS | N | 0 | cylinder 3 stage 1 | 2"-JWS-320136-NEACS | 9 | 0 /+100 | 4.5 | 53 | 997 | 13.5 | 13.5 | H | Jacket water return | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360136 | 08 | 32 | 2" | JWS | 360136 | NEACS | N | 0 | 1"-JWR-320133-NEACS 1"-JWR-320134-NEACS 1"-JWR-320135-NEACS | TP 146 (2"-JWS-36136-NEACS) | 9 | 0 /+100 | 4.5 | 53 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28E | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360137 | 08 | 32 | 2" | JWS | 360137 | NEACS | N | 0 | TP 147 (2"-JWS-64078-B-1) | E-3604 A / E-3604 B | 9 | 0 /+100 | 5 | 30 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28D | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360138 | 08 | 32 | 2" | JWS | 360138 | NEACS | N | 0 | E-3604 A / E-3604 B | TP 148 (2"-JWR-36003-B-1) | 9 | 0 /+100 | 5 | 31.24 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28D | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360139 | 08 | 32 | 4" | JWS | 360139 | NEACS | N | 0 | TP 149 (4"-JWS-64023-B-1) | E-3601 | 9 | 0 /+100 | 5 | 30 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28A | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360140 | 08 | 32 | 4" | JWS | 360140 | NEACS | N | 0 | E-3601 | TP 150 (4"-JWR-36001-B-1) | 9 | 0 /+100 | 5 | 33.4 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28A | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
N360141 | 08 | 32 | 1" | N | 360141 | NEACS | N | 0 | TP 151 (1"-N-67059-B-1) | PCV3699 | 12 | 0 /+80 | 6 | 20 | <50 | 18 | 18 | H | Low pressure unpurified nitrogen | G | N | - | >1.5 | 0 | sh.28F | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360137 | 08 | 32 | 2" | JWS | 360137 | NEACS | N | 0 | TP 147 (2"-JWS-64078-B-1) | E-3604 A / E-3604 B | 9 | 0 /+100 | 5 | 30 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28D | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
JWS360139 | 08 | 32 | 4" | JWS | 360139 | NEACS | N | 0 | TP 149 (4"-JWS-64023-B-1) | E-3601 | 9 | 0 /+100 | 5 | 30 | 997 | 13.5 | 13.5 | H | Jacket water supply | L | N | - | >1.5 | 0 | sh.28A | 2 | Art.4.3 | NA | N | 1 | N | 32-P-048-03 |  | E | N | 000 | N | - | REV03_PKG 32-PK-3600
PR360301 | 08 | 32 | 6" | PR | 360301 | B42S1 | N | 0 | TP 117 (D-3605) | TP119 (D-3606) | 10 | -10 /+180 | 5.52 | 45 | <50 | 14.3 | 15 | H | Hydrocarbon mix for multiple services | G | Y | - | >1.5 | -10 | sh.28B | 1 | II | MOD.A2 | Y | 1 | N | 32-P-048-05 |  | E | P | 010 | N | - | REV03_PKG 32-PK-3600
P400100 | 08 | 32 | 32" | P | 400100 | C42S3 | N | 0 | 40024 (HB)/TP1 | C-4001 | 20 | -45 to 150 | 15 | 80 | 20.7478 | 30 | 30 | H | POLYPROPYLENE | G | N | NA | >1.5 | -10 | sh.30A | 1 | III | MOD.G | Y | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
P400101 | 08 | 32 | 32" | P | 400101 | C42S3 | N | 0 | C-4001 | 400031 (HB) / TP2 | 20 | -45 to 150 | 16 | 84.31 | 21.5688 | 30 | 30 | H | POLYPROPYLENE | G | N | NA | >1.5 | -10 | sh.30A | 1 | III | MOD.G | Y | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
P400102 | 08 | 32 | 3/4" | P | 400102 | C42S3 | N | 0 | C-4001 - PORT A20 | TP27 | 20 | -45 to 150 | 15 | 80 | 20.7478 | 30 | 30 | H | POLYPROPYLENE | G | N | NA | >1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
LO400100 | 08 | 32 | 2" | LO | 400100 | SS316L | N | 0 | D-4001 | P-4002A | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400101 | 08 | 32 | 1-1/2" | LO | 400101 | SS316L | N | 0 | P-4002A | 400103 | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400102 | 08 | 32 | 2" | LO | 400102 | SS316L | N | 0 | D-4001 | P-4002B | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400103 | 08 | 32 | 1-1/2" | LO | 400103 | SS316L | N | 0 | P-4002B | E-4002A/B | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400104 | 08 | 32 | 1-1/2" | LO | 400104 | SS316L | N | 0 | 400101 | PSV 4087 | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400105 | 08 | 32 | 2" | LO | 400105 | SS316L | N | 0 | PSV 4087 | D-4001 | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400106 | 08 | 32 | 1-1/2" | LO | 400106 | SS316L | N | 0 | 400103 | PSV 4088 | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400107 | 08 | 32 | 2" | LO | 400107 | SS316L | N | 0 | PSV 4088 | D-4001 | 10 | 100 | 9 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400108 | 08 | 32 | 1-1/2" | LO | 400108 | SS316L | N | 0 | 400103 | PCV 4083 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400109 | 08 | 32 | 1-1/2" | LO | 400109 | SS316L | N | 0 | PCV 4083 | D-4001 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400110 | 08 | 32 | 1" | LO | 400110 | SS316L | N | 0 | 400103 | TV 4052 | 10 | 100 | 5.5 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400111 | 08 | 32 | 1" | LO | 400111 | SS316L | N | 0 | E-4002A/B | TV 4052 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400112 | 08 | 32 | 1" | LO | 400112 | SS316L | N | 0 | TV 4052 | S-4003A/B | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400113 | 08 | 32 | 1" | LO | 400113 | SS316L | N | 0 | S-4003A/B | PV 4086 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400115 | 08 | 32 | 1-1/2" | LO | 400115 | SS316L | N | 0 | 400113 | D-4003 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400116 | 08 | 32 | 3/4" | LO | 400116 | SS316L | N | 0 | D-4003 | D-4001 | 10 | 100 | 5.5 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400117 | 08 | 32 | 1" | LO | 400117 | SS316L | N | 0 | PV 4086 | TP20 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400118 | 08 | 32 | 1" | LO | 400118 | SS316L | N | 0 | TP12 | 400117 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400120 | 08 | 32 | 1-1/2" | LO | 400120 | SS316L | N | 0 | TP21 | 400123 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400121 | 08 | 32 | 3/4" | LO | 400121 | SS316L | N | 0 | 400120 | ME-4001 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400123 | 08 | 32 | 1" | LO | 400123 | SS316L | N | 0 | 400120 | C-4001-BEARING CARRIER CS | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400124 | 08 | 32 | 1" | LO | 400124 | SS316L | N | 0 | 400120 | C-4001-BEARING CARRIER DS | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400125 | 08 | 32 | 6" | LO | 400125 | SS316L | N | 0 | C-4001-BEARING CARRIER | TP22 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400126 | 08 | 32 | 1-1/2" | LO | 400126 | SS316L | N | 0 | ME-4001 | 400125 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400130 | 08 | 32 | 4" | LO | 400130 | SS316L | N | 0 | D-4001 | Z-4008 | 10 | 100 | 2.1 | 48 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
LO400131 | 08 | 32 | 3" | LO | 400131 | SS316L | N | 0 | 400130 | TP18 | 10 | 100 | 2.1 | 63 | 850 | 15 | 15 | H | LUBE OIL | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
JWS400100 | 08 | 32 | 1-1/2" | JWS | 400100 | B1 | N | 0 | TP3 | 400101 | 9 | 100 | 5.5 | 30 | 1000 | 13.5 | 13.5 | H | JACKET WATER SUPPLY | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-4001
JWS400101 | 08 | 32 | 1-1/2" | JWS | 400101 | B1 | N | 0 | 400100 | E-4002A/B | 9 | 100 | 5.5 | 30 | 1000 | 13.5 | 13.5 | H | JACKET WATER SUPPLY | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-4001
JWS400102 | 08 | 32 | 1-1/2" | JWS | 400102 | B1 | N | 0 | 400100 | E-4002A/B | 9 | 100 | 5.5 | 30 | 1000 | 13.5 | 13.5 | H | JACKET WATER SUPPLY | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-4001
JWR400100 | 08 | 32 | 1-1/2" | JWR | 400100 | B1 | N | 0 | E-4002A/B | 400102 | 9 | 100 | 5.5 | 42 | 1000 | 13.5 | 13.5 | H | JACKET WATER RETURN | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-4001
JWR400101 | 08 | 32 | 1-1/2" | JWR | 400101 | B1 | N | 0 | E-4002A/B | 400102 | 9 | 100 | 5.5 | 42 | 1000 | 13.5 | 13.5 | H | JACKET WATER RETURN | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-4001
JWR400102 | 08 | 32 | 1-1/2" | JWR | 400102 | B1 | N | 0 | 400100 | TP4 | 9 | 100 | 5.5 | 42 | 1000 | 13.5 | 13.5 | H | JACKET WATER RETURN | L | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | N | 32-P-049-03 |  | E | N | 0 | N | - | REV3_PKG 32-PK-4001
PR400100 | 08 | 32 | 1" | PR | 400100 | SS316L | ET | 50 | TP5 | E-4003 | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400101 | 08 | 32 | 1" | PR | 400101 | SS316L | ET | 50 | E-4003 | S-4005A/B | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400102 | 08 | 32 | 3/4" | PR | 400102 | SS316L | ET | 50 | S-4005A/B | FV 4020 | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400103 | 08 | 32 | 3/4" | PR | 400103 | SS316L | ET | 50 | FV 4020 | C-4001 - PORT A01 | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400104 | 08 | 32 | 2" | PR | 400104 | SS316L | N | 0 | C-4001 - PORT A03 | TP7 | 28 | -45 to 150 | 1.37 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | I | MOD.A2 | Y | NA | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400105 | 08 | 32 | 1-1/2" | PR | 400105 | SS316L | N | 0 | TP6 | S-4004A/B | 12 | 80 | 6 | 31 | 1.99 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.30A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-02 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
PR400106 | 08 | 32 | 1-1/2" | PR | 400106 | SS316L | N | 0 | S-4004A/B | PDV 4087 | 12 | 80 | 6 | 31 | 1.99 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.30A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-02 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
PR400107 | 08 | 32 | 1-1/2" | PR | 400107 | SS316L | N | 0 | PDV 4087 | C-4001 - PORT A02 | 12 | 80 | 6 | 31 | 1.99 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.30A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-02 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
PR400108 | 08 | 32 | 3/4" | PR | 400108 | SS316L | N | 0 | 400106 | C-4001 - PORT A06 | 12 | 80 | 6 | 31 | 1.99 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.30A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-02 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
PR400109 | 08 | 32 | 1-1/2" | PR | 400109 | SS316L | N | 0 | C-4001 - PORT A05 | TP8 | 12 | 80 | 1.37 | 31 | 1.99 | 18 | 18 | H | PROCESS NITROGEN | G | N | NA | <1.5 | -10 | sh.30A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-02 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
PR400111 | 08 | 32 | 1/2" | PR | 400111 | SS316L | ET | 50 | 400102 | PDV 4005 | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400112 | 08 | 32 | 1/2" | PR | 400112 | SS316L | ET | 50 | 400111 | 400113 | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
PR400113 | 08 | 32 | 1/2" | PR | 400113 | SS316L | ET | 50 | PDV 4005 | C-4001 - PORT A22 | 28 | -45 to 150 | 20 | 40 to 100 | 19.86 | 42 | 42 | H | POLYPROPYLENE | G | N | NA | <1.5 | -10 | sh.30A | 1 | Art.4.3 | NA | N | Y | Y | 32-P-049-02 |  | M | N | 0FG10 | N | - | REV3_PKG 32-PK-4001
IA400100 | 08 | 32 | 2" | IA | 400100 | SS316L | N | 0 | TP9 | SEAL SYSTEM | 10 | 60 | 7 | 40 | 8.68 | 15 | 15 | H | INSTRUMENT AIR | G | N | NA | <1.5 | 0 | sh.30A | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
IA400101 | 08 | 32 | 1" | IA | 400101 | SS316L | N | 0 | TP10 | OIL SYSTEM | 10 | 60 | 7 | 40 | 8.68 | 15 | 15 | H | INSTRUMENT AIR | G | N | NA | <1.5 | 0 | sh.30B | 2 | Art.4.3 | NA | N | NA | Y | 32-P-049-03 |  | M | N | 0 | N | - | REV3_PKG 32-PK-4001
PR510101 | 08 | 32 | 6" | PR | 510101 | B4S1AD | N | 0 | T-5001 | C-5100 | 7 | 190 | 0.1 | 40 | 1.52 | 11.4 | 20.7 | H | Propylene Gas | G | Y | 70 | >1.5 | 0 | sh.36A | 1 | II | MOD.A2 | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PR510102 | 08 | 32 | 6" | PR | 510102 | B4S1AD | N | 0 | C-5100 | D-5110 | 7 | 190 | 5 | 57 | 163 | 11.4 | 20.7 | H | Propylene Gas + Water | LG | Y | 70 | >1.5 | 0 | sh.36A | 1 | II | MOD.A2 | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510103 | 08 | 32 | 2" | PW | 510103 | B4S1AD | N | 0 | D-5110 | E-5100 | 7 | 190 | 5 | 52 | 986 | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510104 | 08 | 32 | 2" | PW | 510104 | B4S1AD | N | 0 | E-5100 | C-5100 | 7 | 190 | 5 | 36 | 992 | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
N510105 | 08 | 32 | 1" | N | 510105 | B4S1AD | N | 0 | N2 Supply | C-5100 | 7 | 190 | 6 | 20 | 1.17 | 11.4 | 20.7 | H | Nitrogen | G | N | - | >1.5 | 0 | sh.36A | 2 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 000 | N | - | REV3_PKG 32-PK-5100
JWR510106 | 08 | 32 | 2" | JWR | 510106 | B4S1AD | N | 0 | E-5100 | JWR | 9 | 190 | 4.5 | 42 | 994 | 14.6 | 20.7 | H | Jacket Water | L | N | - | >1.5 | 0 | sh.36A | 2 | Art.4.3 | NA | N | C5 | N | 32-U-022-02 |  | E | N | 000 | N | - | REV3_PKG 32-PK-5100
JWS510107 | 08 | 32 | 2" | JWS | 510107 | B4S1AD | N | 0 | JWS | E-5100 | 9 | 190 | 5 | 30 | 994 | 14.6 | 20.7 | H | Jacket Water | L | N | - | >1.5 | 0 | sh.36A | 2 | Art.4.3 | NA | N | C5 | N | 32-U-022-01 |  | E | N | 000 | N | - | REV3_PKG 32-PK-5100
CHWR510108 | 08 | 32 | 3" | CHWR | 510108 | B4S1AD | N | 0 | E-5101 | CHWR | 9 | 190 | 5.5 | 6 | 1016 | 14.6 | 20.7 | H | Chilled Water | L | N | - | >1.5 | 0 | sh.36A | 2 | Art.4.3 | NA | N | C5 | N | 32-U-023-02 |  | E | N | 000 | N | - | REV3_PKG 32-PK-5100
CHWS510109 | 08 | 32 | 3" | CHWS | 510109 | B4S1AD | N | 0 | CHWS | E-5101 | 9 | 190 | 6 | 2 | 1018 | 14.6 | 20.7 | H | Chilled Water | L | N | - | >1.5 | 0 | sh.36A | 2 | Art.4.3 | NA | N | C5 | N | 32-U-023-01 |  | E | N | 000 | N | - | REV3_PKG 32-PK-5100
PR510110 | 08 | 32 | 3" | PR | 510110 | B4S1AD | N | 0 | E-5101 | Gas Outlet | 7 | 190 | 5 | 10 | 10.1 | 11.4 | 20.7 | H | Propylene Gas | G | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PR510111 | 08 | 32 | 3" | PR | 510111 | B4S1AD | N | 0 | D-5110 | E-5101 | 7 | 190 | 5 | 57 | 157 | 11.4 | 20.7 | H | Propylene Gas | G | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510112 | 08 | 32 | 1" | PW | 510112 | B4S1AD | N | 0 | C-5100 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510113 | 08 | 32 | 2" | PW | 510113 | B4S1AD | N | 0 | D-5110 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510114 | 08 | 32 | 3/4" | PW | 510114 | B4S1AD | N | 0 | E-5100 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
DMW510115 | 08 | 32 | 1" | DMW | 510115 | B4S1AD | N | 0 | DMW Supply | E-5100 | 7 | 190 | 6.5 | 35 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 2 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510116 | 08 | 32 | 3/4" | PW | 510116 | B4S1AD | N | 0 | LT-5159 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510117 | 08 | 32 | 1/2" | PW | 510117 | B4S1AD | N | 0 | LI-5157 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510118 | 08 | 32 | 2" | PW | 510118 | B4S1AD | N | 0 | D-5110 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510119 | 08 | 32 | 1" | PW | 510119 | B4S1AD | N | 0 | E-5101 | Condensate Outlet | 7 | 190 | 6 | 10 | - | 11.4 | 20.7 | H | Water + HC | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510120 | 08 | 32 | 2" | PW | 510120 | B4S1AD | N | 0 | D-5110 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510121 | 08 | 32 | 1/2" | PW | 510121 | B4S1AD | N | 0 | LI-5158 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PW510122 | 08 | 32 | 3/4" | PW | 510122 | B4S1AD | N | 0 | LT-5101 | HC Outlet | 7 | 190 | 5 | 57 | - | 11.4 | 20.7 | H | Water | L | N | - | >1.5 | 0 | sh.36A | 1 | Art.4.3 | NA | N | C5 | N | 32-P-050-03 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
BDL510123 | 08 | 32 | 3" | BDL | 510123 | B4S1AD | N | 0 | D-5110 | PSV-5160 | 7 | 190 | 6 | 57 | - | 11.4 | 20.7 | H | Propylene Gas | G | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-U-031-01 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
BDL510124 | 08 | 32 | 3" | BDL | 510124 | B4S1AD | N | 0 | PSV-5160 | PSV Outlet | 7 | 190 | 6 | 57 | - | 11.4 | 20.7 | H | Propylene Gas | G | N | - | >1.5 | 0 | sh.36A | 1 | I | MOD.A | Y | C5 | N | 32-U-031-01 |  | E | N | 0FG10 | N | - | REV3_PKG 32-PK-5100
PN 530100 | 08 | 32 | 14" | PN | 530100 | 1CS2 | JP | 0 | Blower Discharge | Discharge Silencer | 0.5 | 100 | 0.43 | 75.4 | 0.971 | 0.43 | 0.6 | H | Nitrogen | G | N | NA | <1.5 | 0 | sh.38 | 2 | NA | NA | N | NA | N | 32-P-052-02 |  | A | P | 0 0 0 | N | - | REV04_PKG 32-PK-5200
PN 530101 | 08 | 32 | 16" | PN | 530101 | 1CS2 | JP | 0 | Blower Inlet | Inlet Silencer | 0.08 | 50 | 0.068 | 40 | 0.971 | 0.08 | 0.5 | H | Nitrogen | G | N | NA | <1.5 | 0 | sh.38 | 2 | NA | NA | N | NA | N | 32-P-052-02 |  | A | P | 0 0 0 | N | - | REV04_PKG 32-PK-5200
PN 530300 | 08 | 32 | 14" | PN | 530300 | 1CS2 | JP | 0 | Blower Discharge | Discharge Silencer | 0.5 | 100 | 0.43 | 75.4 | 0.971 | 0.43 | 0.6 | H | Nitrogen | G | N | NA | <1.5 | 0 | sh.38 | 2 | NA | NA | N | NA | N | 32-P-052-02 |  | A | P | 0 0 0 | N | - | REV04_PKG 32-PK-5200
PN 530301 | 08 | 32 | 16" | PN | 530301 | 1CS2 | JP | 0 | Blower Inlet | Inlet Silencer | 0.08 | 50 | 0.068 | 40 | 0.971 | 0.08 | 0.5 | H | Nitrogen | G | N | NA | <1.5 | 0 | sh.38 | 2 | NA | NA | N | NA | N | 32-P-052-02 |  | A | P | 0 0 0 | N | - | REV04_PKG 32-PK-5200
PR530101 | 08 | 32 | 3" | PR | 530101 | B4S1 | N | 0 | TP001 | 32-T-5300A/B OFF GAS DRYER | 7 | 80 | 4÷5 | 10÷35 | 9 | 9,1 | 10,5 | H | STREAMER OFFGAS | G | N | 10÷35 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530106 | 08 | 32 | 3" | PR | 530106 | B4S1 | P | 30 | 32-T-5300A/B OFF GAS DRYER | 32-E-5300 DRY GAS COOLER | 7 | 250 | 3,9÷4,9 | 215 | 5,5 | 9,1 | 10,5 | H | STREAMER OFFGAS | G | N | 215 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530107 | 08 | 32 | 3" | PR | 530107 | B4S1 | HA | 80 | 1½"-PR-530118-B4S1-HA | 32-T-5300A OFF GAS DRYER | 7 | 250 | 0,7 | 230 | 1,8 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 230 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530108 | 08 | 32 | 3" | PR | 530108 | B4S1 | HA | 80 | 1½"-PR-530118-B4S1-HA | 32-T-5300B OFF GAS DRYER | 7 | 250 | 0,7 | 230 | 1,8 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 230 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530109 | 08 | 32 | 3" | PR | 530109 | B4S1 | HA | 80 | 3"-PR-530110-B4S1-P | 3"-PR-530108-B4S1-HA | 7 | 80 | 3,9÷4,9 | 10÷35 | 9 | 9,1 | 10,5 | H | STREAMER OFFGAS | G | N | 10÷35 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530109 | 08 | 32 | 3" | PR | 530109 | B4S1 | P | 30 | 3"-PR-530110-B4S1-P | 3"-PR-530108-B4S1-HA | 7 | 80 | 3,9÷4,9 | 10÷35 | 9 | 9,1 | 10,5 | H | STREAMER OFFGAS | G | N | 10÷35 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530110 | 08 | 32 | 3" | PR | 530110 | B4S1 | P | 30 | 32-T-5300A OFF GAS DRYER | 3"-PR-530109-B4S1 | 7 | 250 | 0,6 | 215 | 1,7 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 215 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530111 | 08 | 32 | 3" | PR | 530111 | B4S1 | P | 30 | 32-T-5300B OFF GAS DRYER | 3"-PR-530109-B4S1 | 7 | 250 | 0,6 | 215 | 1,7 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 215 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530112 | 08 | 32 | 3" | PR | 530112 | B4S1 | N | 0 | 32-E-5300 DRY GAS COOLER | 32-S-5300 DRY GAS FILTER | 7 | 80 | 3,7 | 60 | 6 | 9,1 | 10,5 | H | OFFGAS | G | N | 60 | >1.5 | 60 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530113 | 08 | 32 | 3" | PR | 530113 | B4S1 | N | 0 | 32-S-5300 DRY GAS FILTER | TP002 | 7 | 80 | 3,6 | 60 | 6 | 9,1 | 10,5 | H | OFFGAS | G | N | 60 | >1.5 | 60 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | B | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530114 | 08 | 32 | 1-1/2" | PR | 530114 | B4S1 | N | 0 | TP003 | VM-5350 | 7 | 80 | 3 | 45 | 6,7 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 45 | >1.5 | 40 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530115 | 08 | 32 | 1" | PR | 530115 | B4S1 | N | 0 | 1½"-PR-530114-B4S1 | PSV-5352 | 7 | 80 | 3 | 45 | 6,7 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 45 | >1.5 | 40 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530118 | 08 | 32 | 1-1/2" | PR | 530118 | B4S1 | HA | 70 | 32-E-5301 REG.GAS HEATER | 32-T-5300A/B OFF GAS DRYER COMMON INLET | 7 | 250 | 0,7 | 230 | 1,8 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 230 | >1.5 | 40 | sh.39B | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530119 | 08 | 32 | 1-1/2" | PR | 530119 | B4S1 | P | 30 | HV-5356 / HV-5360 | TP004 | 7 | 250 | 0,5 | 205 | 1,7 | 9,1 | 10,5 | H | REGENERATION PROPYLENE | G | N | 215 | >1.5 | 180 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530122 | 08 | 32 | 1-1/2" | PR | 530122 | B4S1 | P | 30 | 32-E-5300 DRY GAS COOLER | 32-S-5300 DRY GAS FILTER | 7 | 250 | 0,7 | 230 | 1,8 | 9,1 | 10,5 | H | STREAMER OFFGAS | G | N | 230 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530125 | 08 | 32 | 1-1/2" | PR | 530125 | B4S1 | P | 30 | 3"-PR-530108-B4S1-HA | PSV 5351 | 7 | 250 | 0,7 | 230 | 1,8 | 9,1 | 10,5 | H | STREAMER OFFGAS | G | N | 230 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 5 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
JWS530127 | 08 | 32 | 2" | JWS | 530127 | B1 | N | 0 | TP007 | 32-E-5300 DRY GAS COOLER | 9 | 80 | 5 | 30 | 1000 | 11,7 | 13,5 | H | JACKET WATER RETURN | L | N | 30 | <1.5 | 30 | sh.39B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-050-05 |  | M | N | 0 0 0 | N | - | REV06_PKG 32-PK-5300
JWR530128 | 08 | 32 | 2" | JWR | 530128 | B1 | N | 0 | 32-E-5300 DRY GAS COOLER | TP008 | 9 | 80 | 4,9 | 39,2 | 1000 | 11,7 | 13,5 | H | JACKET WATER SUPPLY | L | N | 39,2 | <1.5 | 30 | sh.39B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-050-05 |  | M | N | 0 0 0 | N | - | REV06_PKG 32-PK-5300
PR530129 | 08 | 32 | 1-1/2" | PR | 530129 | C42S1 | N | 0 | 2"-JWR-530128-B-1 | PSV-5353 | 7 | 80 | 3 | 40÷45 | 1000 | 9,1 | 10,5 | H | JACKET WATER SUPPLY | L | N | 39,2 | <1.5 | 30 | sh.39B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-050-05 |  | E | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR530131 | 08 | 32 | 1" | PR | 530131 | B4S1 | N | 0 | 32-S-5300 DRY GAS FILTER | TP006 | 3,5 | 120 | 1,37 | 60 | 1,7 | 4,55 | 5,25 | H | REGENERATION PROPYLENE | G | N | 60 | >1.5 | 10 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
IA530132 | 08 | 32 | 1" | IA | 530132 | B-13 | N | 0 | TP005 | IA USERS | 10 | 60 | 7 | 40 | 8,9 | 13 | 15 | H | INSTRUMENT AIR | G | N | 40 | >1.5 | 10 | sh.39B | 2 | Art.4.3 | NA | N | HDG | N | 32-P-050-05 |  | E | N | 0 0 0 | N | - | REV06_PKG 32-PK-5300
PR530133 | 08 | 32 | 1" | PR | 530133 | B4S1 | N | 0 | 1½"-PR-530114-B4S1 | 1"-PR-530131-B4S1 | 3,5 | 120 | 1,37 | 60 | 1,7 | 4,55 | 5,25 | H | REGENERATION PROPYLENE | G | N | 60 | >1.5 | 10 | sh.39B | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | E | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
BDL530117 | 08 | 32 | 3" | BDL | 530117 | B4S1 | ST (NOTE-B) | 0 | DISCHARGES LINES | TP006 | 3,5 | 120 | 1,37 | 60 | 1,7 | 4,55 | 5,25 | H | PROPYLENE | G | N | 60 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
BDL530118 | 08 | 32 | 2" | BDL | 530118 | B4S1 | N | 0 | PSV-5352 | 3"-BDL-5300117-B4S1-ST | 3,5 | 120 | 1,37 | 60 | 1,7 | 4,55 | 5,25 | H | PROPYLENE | G | N | 60 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
BDL530119 | 08 | 32 | 2" | BDL | 530119 | B4S1 | N | 0 | PSV-5350 | 3"-BDL-5300117-B4S1-ST | 3,5 | 120 | 1,37 | 60 | 1,7 | 4,55 | 5,25 | H | PROPYLENE | G | N | 60 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
BDL530120 | 08 | 32 | 2" | BDL | 530120 | B4S1 | N | 0 | PSV-5351 | 3"-BDL-5300117-B4S1-ST | 3,5 | 120 | 1,37 | 60 | 1,7 | 4,55 | 5,25 | H | PROPYLENE | G | N | 60 | >1.5 | 10 | sh.39A | 1 | I | MOD.A | Y | 1 | N | 32-P-050-05 |  | A | N | 0 FG1 0 | N | - | REV06_PKG 32-PK-5300
PR610100 | 08 | 32 | 6" | PR | 610100 | ML3R2 | CG | 50 | Line 6"-PR-610108-ML3R2 (CG) (Interconnecting Line) | S-6100 Suction Strainer (nozzle P1) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | Y | -4 | >1.5 | -11 | sh.42B | 1 | II | MOD.A2 | Y | 9 | Y | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610101 | 08 | 32 | 6" | PR | 610101 | ML3R2 | CG | 50 | S-6100 Suction Strainer (nozzle P2) | C-6100 Compressor Suction | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | Y | -4 | >1.5 | -11 | sh.42B | 1 | II | MOD.A2 | Y | 9 | Y | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610102 | 08 | 32 | 6" | PR | 610102 | ML3R2 | N | 0 | C-6100 Compressor Discharge | D-6109 Oil Separator (nozzle P1) | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | Y | 57,4 | >1.5 | 0 | sh.42B | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610103 | 08 | 32 | 6" | PR | 610103 | ML3R2 | N | 0 | D-6109 Oil Separator (nozzle P2) | E-6101 Condenser (nozzle P1) | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | Y | 57,4 | >1.5 | 0 | sh.42C | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610104 | 08 | 32 | 4" | PR | 610104 | ML3R2 | N | 0 | E-6101 Condenser (nozzle P2) | LV-6157 Control Valve | FV / 18,7 | -45 / 120 | 14,7 | 38 | 490.3 | 30 | 71.54 | H | PROPYLENE | L | Y | 38 | >1.5 | 0 | sh.42D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610105 | 08 | 32 | 4" | PR | 610105 | ML3R2 | CG | 25 | LV-6157 Control Valve | D-6108 Liquid Receiver (nozzle P1) | FV / 18,7 | -45 / 120 | 9,7 | 22 | 512 | 30 | 71.54 | H | PROPYLENE | L | Y | 22 | >1.5 | 0 | sh.42D | 1 | II | MOD.A2 | Y | 9 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610106 | 08 | 32 | 4" | PR | 610106 | ML3R2 | CG | 25 | D-6108 Liquid Receiver (nozzle P2) | LV-6161 Control Valve | FV / 18,7 | -45 / 120 | 9,7 | 22 | 512 | 30 | 71.54 | H | PROPYLENE | L | Y | 22 | >1.5 | 0 | sh.42D | 1 | II | MOD.A2 | Y | 9 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610107 | 08 | 32 | 4" | PR | 610107 | ML3R2 | CG | 50 | LV-6161 Control Valve | E-6102 Evaporator (nozzles P1A/P1B) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 558 | 30 | 71.54 | H | PROPYLENE | L | Y | -4 | >1.5 | -11 | sh.42E | 1 | II | MOD.A2 | Y | 9 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610108 | 08 | 32 | 6" | PR | 610108 | ML3R2 | CG | 50 | E-6102 Evaporator (nozzles P2A/P2B) | Line 6"-PR-610100-ML3R2 (CG) (Compressor Suction Line) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | Y | -4 | >1.5 | -11 | sh.42E | 1 | II | MOD.A2 | Y | 9 | Y | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610109 | 08 | 32 | 3/4" | PR | 610109 | ML3R2 | CG | 40 | Line 6"-PR-610100-ML3R2 (CG) (Compressor Suction Line) | Local Gauge Board Instruments | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | -11 | sh.42B | 1 | Art.4.3 | NA | N | 9 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR 610110 | 08 | 32 | 3/4" | PR | 610110 | ML3R2 | N | 0 | D-6109 Oil Separator (nozzles P11/P12) | Line 6"-PR-610100-ML3R2 (CG) (Compressor Suction Line) | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610111 | 08 | 32 | 3/4" | PR | 610111 | ML3R2 | N | 0 | D-6109 Oil Separator (nozzle P9) | Local Gauge Board Instruments | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610112 | 08 | 32 | 3" | PR | 610112 | ML3R2 | N | 0 | Line 6"-PR-610103-ML3R2 | PV-6156 Control Valve (Hot Gas By-pass) | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | Y | 57,4 | >1.5 | 0 | sh.42C | 1 | II | MOD.A2 | Y | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610113 | 08 | 32 | 4" | PR | 610113 | ML3R2 | CG | 25 | PV-6156 Control Valve (Hot Gas By-pass) | 4"-PR-610107-ML3R2 (CG) (Hot Gas By-pass) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | Y | -4 | >1.5 | 0 | sh.42E | 1 | II | MOD.A2 | Y | 9 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610114 | 08 | 32 | 2" | PR | 610114 | ML3R2 | N | 0 | D-6108 Liquid Receiver (nozzle P5) | PV-6181A Control Valve | FV / 18,7 | -45 / 120 | 9,7 | 22 | 512 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | I | MOD.A | Y | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610115 | 08 | 32 | 2" | PR | 610115 | ML3R2 | N | 0 | PV-6181A Control Valve | C-6100 Compressor (Economizing Line) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 22.5 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | I | MOD.A | Y | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610116 | 08 | 32 | 1" | PR | 610116 | ML3R2 | N | 0 | TP011 (Propylene Charge) | PV-6181B Control Valve | FV / 18,7 | -45 / 120 | 26 | 0 / 42 | 512 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610117 | 08 | 32 | 1" | PR | 610117 | ML3R2 | N | 0 | PV-6181B Control Valve | D-6108 Liquid Receiver (nozzle P4) | FV / 18,7 | -45 / 120 | 9,7 | 22 | 512 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610118 | 08 | 32 | 3/4" | PR | 610118 | ML3R2 | N | 0 | Line 6"-PR-610103-ML3R2 | J-6100 Ejector | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610119 | 08 | 32 | 3/4" | PR | 610119 | ML3R2 | N | 0 | E-6102 Evaporator (nozzle P8) | J-6100 Ejector | FV / 18,7 | -45 / 120 | 4,1 | -4 | 558 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | -11 | sh.42E | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610120 | 08 | 32 | 3/4" | PR | 610120 | ML3R2 | N | 0 | J-6100 Ejector | Line 6"-PR-610100-ML3R2 (CG) (Compressor Suction Line) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42E | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610125 | 08 | 32 | 1" | PR | 610125 | ML3R2 | N | 0 | E-6101 Condenser (nozzle P12A) | LI-6156 Level Gauge | FV / 18,7 | -45 / 120 | 14.7 | 38 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610126 | 08 | 32 | 1" | PR | 610126 | ML3R2 | N | 0 | Line 4"-PR-610104-ML3R2 (nozzle P12B) | LI-6156 Level Gauge | FV / 18,7 | -45 / 120 | 14,7 | 38 | 490 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42D | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610127 | 08 | 32 | 3" | PR | 610127 | ML3R2 | CG | 50 | E-6102 Evaporator (nozzle P12B) | LT-6161 Level Transmitter / LI-6163 Level Gauge | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | Y | -4 | >1.5 | -11 | sh.42E | 1 | II | MOD.A2 | Y | 9 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610128 | 08 | 32 | 3/4" | PR | 610128 | ML3R2 | N | 0 | Line 6"-PR-610103-ML3R2 | PDI-6186 | FV / 18,7 | -45 / 120 | 14,7 | 57,4 | 30.4 | 30 | 71.54 | H | PROPYLENE | G | N | - | >1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610129 | 08 | 32 | 14" | PR | 610129 | ML3R2 | CG | 65 | S-6100 Suction Strainer (nozzle P1) | S-6100 Suction Strainer (nozzle P2) | FV / 18,7 | -45 / 120 | 4,1 | -4 | 10.9 | 30 | 71.54 | H | PROPYLENE | G | Y | -4 | >1.5 | -11 | sh.42B | 1 | III | MOD.G | Y | 1 | Y | 32-P-055-03 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
LO610150 | 08 | 32 | 3" | LO | 610150 | MS3R0 | N | 0 | D-6109 Oil Separator (nozzle P3) | P-6102A/B Lube Oil Pumps Suction | FV / 23,7 | 0 / 120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | Y | -57,4 | <1.5 | -11 | sh.42C | 1 | II | MOD.A2 | Y | 9 | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610151 | 08 | 32 | 1-1/2" | LO | 610151 | MS3R0 | N | 0 | P-6102A/B Lube Oil Pumps Discharge | TV-6170 Three-way Valve / E-6104 Lube Oil Cooler (nozzle P1) | FV / 23,7 | 0 / 120 | 16,2 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | I | MOD.A | Y | 9 | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610152 | 08 | 32 | 1" | LO | 610152 | MS3R0 | N | 0 | TP004 (Oil Charge) | 3"-LO-610150-MS3R0 (ET) | FV / 23,7 | 0 / 120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610153 | 08 | 32 | 2" | LO | 610153 | MS3R0 | N | 0 | PSV-6171 Safety Valve (P-6102A Lube Oil Pump Discharge) | D-6109 Oil Separator (nozzle P7) | FV / 23,7 | 0 /120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | II | MOD.A2 | Y | NA | N | 32-P-055-03 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610154 | 08 | 32 | 2" | LO | 610154 | MS3R0 | N | 0 | PSV-6173 Safety Valve (P-6102B Lube Oil Pump Discharge) | D-6109 Oil Separator (nozzle P8) | FV / 23,7 | 0 /120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | II | MOD.A2 | Y | NA | N | 32-P-055-03 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610155 | 08 | 32 | 1" | LO | 610155 | MS3R0 | N | 0 | Line 1"1/2-LO-610151-MS3R0 (ET) | PV-6164 Control Valve | FV / 23,7 | 0 / 120 | 16,2 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610156 | 08 | 32 | 1" | LO | 610156 | MS3R0 | N | 0 | PV-6164 Control Valve | D-6109 Oil Separator (nozzle P6) | FV / 23,7 | 0 / 120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610157 | 08 | 32 | 1-1/2" | LO | 610157 | MS3R0 | N | 0 | E-6104 Lube Oil Cooler (nozzle P2) | TV-6170 Three-way Valve | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | I | MOD.A | Y | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610158 | 08 | 32 | 1-1/2" | LO | 610158 | MS3R0 | N | 0 | TV-6170 Three-way Valve | S-6101A/B Lube Oil Filters (nozzle P1) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | I | MOD.A | Y | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610159 | 08 | 32 | 1-1/2" | LO | 610159 | MS3R0 | N | 0 | S-6101A/B Lube Oil Filters (nozzle P2) | Line 2"-LO-610162-MS3R0 (Lube Oil Header) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | I | MOD.A | Y | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610160 | 08 | 32 | 3/4" | LO | 610160 | MS3R0 | N | 0 | Line 1"1/2-LO-610159-MS3R0 | Local Gauge Board Instruments | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610161 | 08 | 32 | 3/4" | LO | 610161 | MS3R0 | N | 0 | D-6109 Oil Separator (nozzle P10) | C-6100 Compressor (Oil Injection) | FV / 23,7 | 0 / 120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | 9 | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610162 | 08 | 32 | 2" | LO | 610162 | MS3R0 | N | 0 | Line 1"1/2-LO-610159-MS3R0 | Lube Oil Header | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42B | 1 | II | MOD.A2 | Y | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610163 | 08 | 32 | 1-1/2" | LO | 610163 | MS3R0 | N | 0 | Lube Oil Header (Line 2"-LO-610162-MS3R0) | C-6100 Compressor (Lubrication) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42B | 1 | I | MOD.A | Y | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610164 | 08 | 32 | 1-1/2" | LO | 610164 | MS3R0 | N | 0 | Lube Oil Drain Header | TP025 | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | I | MOD.A | Y | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610165 | 08 | 32 | 1" | LO | 610165 | MS3R0 | N | 0 | E-6104 Lube Oil Cooler (nozzle P6, Oil Drain) | Lube Oil Drain Header (1"1/2-LO-610164-MS3R0) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610166 | 08 | 32 | 3/4" | LO | 610166 | MS3R0 | N | 0 | S-6101A Lube Oil Filter (nozzle P4A, Drain) | Lube Oil Drain Header (1"1/2-LO-610164-MS3R0) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610167 | 08 | 32 | 3/4" | LO | 610167 | MS3R0 | N | 0 | S-6101B Lube Oil Filter (nozzle P4B, Drain) | Lube Oil Drain Header (1"1/2-LO-610164-MS3R0) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610168 | 08 | 32 | 1" | LO | 610168 | MS3R0 | N | 0 | E-6104 Lube Oil Cooler (nozzle P5, Oil Vent) | Lube Oil Vent Header to Flare (1"-LO-610171-MS3R0) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610169 | 08 | 32 | 3/4" | LO | 610169 | MS3R0 | N | 0 | S-6101A/B Lube Oil Filters (nozzles P3A/B, Vent) | Lube Oil Vent Header to Flare (1"-LO-610171-MS3R0) | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610170 | 08 | 32 | 3/4" | LO | 610170 | MS3R0 | N | 0 | S-6102A/B Lube Oil Strainers (Vent) | Lube Oil Vent Header to Flare (1"-LO-610171-MS3R0) | FV / 23,7 | 0 / 120 | 14,7 | 57,4 | 1064 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610171 | 08 | 32 | 1" | LO | 610171 | MS3R0 | N | 0 | Lube Oil Vent Header to Flare | TP026 | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
LO610172 | 08 | 32 | 3/4" | LO | 610172 | MS3R0 | N | 0 | Line 1"1/2-LO-610158-MS3R0 | Local Gauge Board Instruments | FV / 23,7 | 0 / 120 | 16,2 | 50 | 1078 | 41.4 | 57.96 | H | LUBE OIL | L | N | - | <1.5 | 0 | sh.42C | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
JWS610200 | 08 | 32 | 1-1/2" | JWS | 610200 | MC3R2 | N | 0 | TP006 | E-6104 Lube Oil Cooler (nozzle P3, Jacket Water Supply) | FV / 23,7 | 0 / 120 | 5 | 30 | 995 | 41.4 | 71.54 | H | JACKET WATER SUPPLY | L | N | - | >1.5 | 0 | sh.42C | 2 | Art.4.3 | NA | N | 1 | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
JWR610201 | 08 | 32 | 1-1/2" | JWR | 610201 | MC3R2 | N | 0 | E-6104 Lube Oil Cooler (nozzle P4, Jacket Water Return) | TP007 | FV / 23,7 | 0 / 120 | 5 | 35 | 995 | 41.4 | 71.54 | H | JACKET WATER RETURN | L | N | - | >1.5 | 0 | sh.42C | 2 | Art.4.3 | NA | N | 1 | N | 32-P-055-02 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
JWS610202 | 08 | 32 | 10" | JWS | 610202 | MC3R2 | N | 0 | TP013 | E-6101 Condenser (nozzle P3, Jacket Water Supply) | FV / 18,7 | -45 / 120 | 5 | 30 | 995 | 41.4 | 71.54 | H | JACKET WATER SUPPLY | L | N | - | >1.5 | 0 | sh.42D | 2 | II | MOD.A2 | Y | 1 | Y | 32-P-055-03 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
JWR610203 | 08 | 32 | 10" | JWR | 610203 | MC3R2 | N | 0 | E-6101 Condenser (nozzle P4, Jacket Water Return) | TP014 | FV / 18,7 | -45 / 120 | 5 | 34 | 995 | 41.4 | 71.54 | H | JACKET WATER RETURN | L | N | - | >1.5 | 0 | sh.42D | 2 | II | MOD.A2 | Y | 1 | Y | 32-P-055-03 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
N610250 | 08 | 32 | 1" | N | 610250 | ML3R2 | N | 0 | TP001 | Line 6"-PR-610100-ML3R2 (CG) (Compressor Suction Line) | 18,7 | 0 / 90 | 5,5 / 6,1 | 20 | 10.9 | 30 | 71.54 | H | NITROGEN | G | N | - | <1.5 | -11 | sh.42B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
N610251 | 08 | 32 | 3/4" | N | 610251 | ML3R2 | N | 0 | Line 1"-N-610250-ML3R2 | S-6103 Filter (API Plan 72) | 18,7 | 0 / 90 | 5,5 / 6,1 | 20 | 10.9 | 30 | 71.54 | H | NITROGEN | G | N | - | <1.5 | 0 | sh.42B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-055-03 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
N610252 | 08 | 32 | 3/4" | N | 610252 | ML3R2 | N | 0 | S-6103 Filter (API Plan 72) | C-6100 Compressor | 26 | 0 / 90 | 3 | 20 | 2 | 30 | 71.54 | H | NITROGEN | G | N | - | <1.5 | 0 | sh.42B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-055-01 |  | M | N | 0 0 0 | N | - | REV4_PKG 32-PK-6100
PR610253 | 08 | 32 | 1-1/2" | PR | 610253 | MS3R0 | N | 0 | C-6100 Compressor | D-6103 Seal Pot (nozzle P1) (API Plan 75) | FV / 26 | -45 / 120 | 3 | 20 | 2 | 41.4 | 57.96 | H | PROPYLENE / OIL | G/L | N | - | >1.5 | 0 | sh.42B | 1 | I | MOD.A | Y | NA | N | 32-P-055-01 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
PR610254 | 08 | 32 | 3/4" | PR | 610254 | MS3R0 | N | 0 | D-6103 Seal Pot (nozzle P2) (API Plan 75) | TP003 (to Flare) | FV / 26 | -45 / 120 | 3 | 20 | 2 | 41.4 | 57.96 | H | PROPYLENE / OIL | G | N | - | >1.5 | 0 | sh.42B | 1 | Art.4.3 | NA | N | NA | N | 32-P-055-01 |  | F | N | 0 FG1 0 | N | - | REV4_PKG 32-PK-6100
IA620105 | 08 | 32 | 1" | IA | 620105 | TUBING | N | 0 | TP 1 | 32-D-6201 | 10 | 60 | 4.8 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620109 | 08 | 32 | 1" | IA | 620109 | TUBING | N | 0 | 32-D-6201 | 32-C-6200 - 1st PHASE | 18 | 200 | 4.8 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620104 | 08 | 32 | 1" | IA | 620104 | TUBING | PG | 30 | 32-C-6200 - 1st PHASE | 32-D-6202 | 28.5 | 200 | 11.65 | 129.7 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620106 | 08 | 32 | 1" | IA | 620106 | TUBING | PG | 30 | 32-D-6202 | 32-E-6202 | 35 | 200 | 11.72 | 129.7 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620107 | 08 | 32 | 1" | IA | 620107 | TUBING | N | 0 | 32-E-6202 | 32-D-6203 | 35 | 200 | 11.72 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620103 | 08 | 32 | 1" | IA | 620103 | TUBING | N | 0 | 32-D-6203 | 32-C-6200 - 2nd PHASE | 18 | 200 | 11.32 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620112 | 08 | 32 | 1" | IA | 620112 | TUBING | PG | 30 | 32-C-6200 - 2nd PHASE | 32-D-6204 | 28.5 | 200 | 25.6 | 127.5 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620108 | 08 | 32 | 1" | IA | 620108 | TUBING | PG | 30 | 32-D-6204 | 32-E-6203 | 35 | 200 | 25.6 | 127.5 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620102 | 08 | 32 | 1" | IA | 620102 | TUBING | N | 0 | 32-E-6203 | TP 2 | 28 | 150 | 25.6 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
VA620118 | 08 | 32 | 2" | VA | 620118 | 3FS4 | N | 0 | 32-PSV-6276 | ATM SAFE LOCATION | 28 | 150 | 0 | 25 | <50 | - | 43 | H | VENT TO ATM | G | N | - | <1.5 | 0 | sh.43B | 2 | I | Mod.A2 | Y | NA | N | 32-U-094-03 |  | A | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620111 | 08 | 32 | 1" | IA | 620111 | TUBING | N | 0 | 1"-IA-620105-TUBING | BALL VALVE ON INSTRUMENT AIR LINE | 28 | 150 | 25.6 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | N | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
IA620110 | 08 | 32 | 1" | IA | 620110 | TUBING | N | 0 | 1"-IA-620102-TUBING | 1"-IA-620105-TUBING | 10 | 60 | 4.8 | 40 | <50 | NA | NA | NA | INSTRUMENT AIR | G | Y | - | <1.5 | 0 | sh.43B | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-03 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
LO620109 | 08 | 32 | 3/4" | LO | 620109 | TUBING | N | 0 | TP 12 | 32-LSL-6253 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620111 | 08 | 32 | 1/2" | LO | 620111 | TUBING | N | 0 | 32-LSL-6253 | 32-C-6200 | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620112 | 08 | 32 | 1" | LO | 620112 | TUBING | N | 0 | 32-LSL-6253 | 32-C-6200 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620103 | 08 | 32 | 3/4" | LO | 620103 | TUBING | N | 0 | 1"-LO-620112-TUBING | 32-P-6201 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620104 | 08 | 32 | 3/4" | LO | 620104 | TUBING | N | 0 | 32-P-6201 | 32-E-6201 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620101 | 08 | 32 | 3/4" | LO | 620101 | TUBING | N | 0 | 32-P-6200 | 3/4"-LO-620104-TUBING | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620108 | 08 | 32 | 1/2" | LO | 620108 | TUBING | N | 0 | 3/4"-LO-620101-TUBING | 3/4"-LO-620101-TUBING | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620107 | 08 | 32 | 3/4" | LO | 620107 | TUBING | N | 0 | 3/4"-LO-620101-TUBING | 32-C-6200 | 10 | 90 | 6 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620102 | 08 | 32 | 3/4" | LO | 620102 | TUBING | N | 0 | 3/4"-LO-620104-TUBING | 32-TCV-6261 | 10 | 90 | 8 | 50 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620105 | 08 | 32 | 3/4" | LO | 620105 | TUBING | N | 0 | 32-E-6201 | 32-TCV-6261 | 10 | 90 | 6 | 50 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620110 | 08 | 32 | 3/4" | LO | 620110 | TUBING | N | 0 | 32-TCV-6261 | 32-S-6201A/B | 10 | 90 | 6 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620106 | 08 | 32 | 3/4" | LO | 620106 | TUBING | N | 0 | 32-S-6201A/B | 32-C-6200 - OIL HEADER | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620113 | 08 | 32 | 1/4" | LO | 620113 | TUBING | N | 0 | 3/4"-LO-620104-TUBING | 32-PCV-6299 | 10 | 90 | 6 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
LO620114 | 08 | 32 | 1/4" | LO | 620114 | TUBING | N | 0 | 32-PCV-6257 | 3/4"-LO-620106-TUBING | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 110 | N | - | REV4_PKG 32-PK-6200
JWS620138 | 08 | 32 | 3/4" | JWS | 620138 | TUBING | N | 0 | TP 13 | 1/2"-JWS-620116-TUBING | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWS620116 | 08 | 32 | 1/2" | JWS | 620116 | TUBING | N | 0 | 3/4"-JWS-620138-TUBING | 32-E-6201 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWS620103 | 08 | 32 | 3/4" | JWS | 620103 | TUBING | N | 0 | 3/4"-JWS-620138-TUBING | 32-C-6200 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWS620105 | 08 | 32 | 1/2" | JWS | 620105 | TUBING | N | 0 | 1/2"-JWS-620103-TUBING | 32-C-6200 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWS620107 | 08 | 32 | 1/2" | JWS | 620107 | TUBING | N | 0 | 3/4"-JWS-620113-TUBING | 32-E-6202 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWS620109 | 08 | 32 | 1/2" | JWS | 620109 | TUBING | N | 0 | 3/4"-JWS-620113-TUBING | 32-E-6203 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620104 | 08 | 32 | 3/4" | JWR | 620104 | TUBING | N | 0 | 32-C-6200 | 3/4"-JWR-620101-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620106 | 08 | 32 | 1/2" | JWR | 620106 | TUBING | N | 0 | 32-C-6200 | 3/4"-JWR-620101-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620101 | 08 | 32 | 3/4" | JWR | 620101 | TUBING | N | 0 | 1/2"-JWR-620106-TUBING | 1"-JWR-620115-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620117 | 08 | 32 | 1/2" | JWR | 620117 | TUBING | N | 0 | 32-E-6201 | 3/4"-JWR-620101-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43C | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620108 | 08 | 32 | 1/2" | JWR | 620108 | TUBING | N | 0 | 32-E-6202 | 3/4"-JWR-620114-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620110 | 08 | 32 | 1/2" | JWR | 620110 | TUBING | N | 0 | 32-E-6203 | 3/4"-JWR-620114-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620111 | 08 | 32 | 3/4" | JWR | 620111 | TUBING | N | 0 | 3/4"-JWR-620101-TUBING | 32-TSV-6274 | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620112 | 08 | 32 | 1" | JWR | 620112 | TUBING | N | 0 | 32-TSV-6274 | BASEPLATE DRAIN | 9 | 180 | 9 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWS620113 | 08 | 32 | 3/4" | JWS | 620113 | TUBING | N | 0 | 3/4"-JWS-620138-TUBING | 1/2"-JWS-620109-TUBING | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620114 | 08 | 32 | 3/4" | JWR | 620114 | TUBING | N | 0 | 1/2"-JWR-620110-TUBING | 3/4"-JWR-620101-TUBING | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
JWR620115 | 08 | 32 | 1" | JWR | 620115 | TUBING | N | 0 | 3/4"-JWR-620101-TUBING | TP 14 | 9 | 180 | 5 | 38 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.43D | 2 | Art.4.3 | NA | N | NA | N | 32-U-094-01 |  | - | N | 000 | N | - | REV4_PKG 32-PK-6200
ET710138 | 08 | 32 | 2" | ET | 710138 | C3S1 | N | 0 | TP 1 | 32-D-7100 | 45 | 150 | 27.5 | 40 | <50 | - | 67.5 | H | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | II | Mod.A2 | Y | 1-A | Y | 32-P-006-04 |  | A | P | 041 | N | - | REV4_PKG 32-PK-7101
ET710106 | 08 | 32 | 2" | ET | 710106 | D1S1 | PG | 30 | 32-D-7101 | 32-E-7104 | 48 | 150 | 40.77 | 76.7 | <50 | - | 72 | H | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | II | Mod.A2 | Y | 1-A | Y | 32-P-006-04 |  | A | P | 041 | N | - | REV4_PKG 32-PK-7101
ET710135 | 08 | 32 | 2" | ET | 710135 | D1S1 | N | 0 | 32-E-7104 | TP 2 | 48 | 120 | 40 | 40 | <50 | - | 72 | H | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | II | Mod.A2 | Y | 1-A | Y | 32-P-006-04 |  | A | P | 041 | N | - | REV4_PKG 32-PK-7101
FL710120 | 08 | 32 | 2" | FL | 710120 | B4S1 | N | 0 | 32-PSV-7194 | TP 3 | 48 | 120 | 1.37 | 50 | <50 | - | 72 | H | FL | G | N | - | >1.5 | 0 | sh.50A | 1 | II | Mod.A2 | Y | 1-A | Y | 32-P-006-04 |  | A | P | 041 | N | - | REV4_PKG 32-PK-7101
FL710117 | 08 | 32 | 1" | FL | 710117 | B4S1 | N | 0 | 32-D-7102 | 2"-FL-710120-B4S1 | 17.7 | 100 | 1.37 | 50 | <50 | - | 26.6 | H | FL | G | N | - | >1.5 | 0 | sh.50A | 1 | Art.4.3 | NA | N | 1-A | N | 32-P-006-04 |  | A | N | 041 | N | - | REV4_PKG 32-PK-7101
ET710113 | 08 | 32 | 3/4" | ET | 710113 | C3S1 | N | 0 | 32-D-7100 | 3/4"-ET-710108-C3S1 | 38.3 | 200 | 27.5 | 40 | <50 | NA | 57.5 | H | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | Art.4.3 | NA | N | 1-A | N | 32-P-006-04 |  | A | P | 041 | N | - | REV4_PKG 32-PK-7101
ET710108 | 08 | 32 | 3/4" | ET | 710108 | C3S1 | N | 0 | 3/4"-ET-710113-C3S1 | TP 5 | 17.7 | 200 | 1.37 | 50 | <50 | - | 26.6 | H | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | Art.4.3 | NA | N | 1-A | N | 32-P-006-04 |  | A | N | 041 | N | - | REV4_PKG 32-PK-7101
ET710109 | 08 | 32 | 3/4" | ET | 710109 | D1S1 | N | 0 | 32-D-7101 | 3/4"-ET-710108-C3S1 | 46 | 200 | 40.77 | 76.7 | <50 | - | 69 | H | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | Art.4.3 | NA | N | 1-A | N | 32-P-006-04 |  | A | P | 041 | N | - | REV4_PKG 32-PK-7101
ET710110 | 08 | 32 | 1/2" | ET | 710110 | TUBING | N | 0 | 32-D-7102 | TP16 | 0 | 80 | 0 | 25 | <50 | NA | NA | NA | ETHYLENE | G | N | - | >1.5 | 0 | sh.50A | 1 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 041 | N | - | REV4_PKG 32-PK-7101
ET710111 | 08 | 32 | 1/2" | ET | 710111 | TUBING | N | 0 | 32-D-7103 | 1/2"-ET-710110-C3S1 | 10 | 80 | 1 | 50 | <50 | NA | NA | NA | ETHYLENE | G | N | - | >1.5 | 0 | sh.50A | 1 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 041 | N | - | REV4_PKG 32-PK-7101
N710146 | 08 | 32 | 1/2" | N | 710146 | TUBING | N | 0 | TP 6 | HEADER | 12 | 80 | 5.5 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.50A | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
N710103 | 08 | 32 | 1/2" | N | 710103 | TUBING | N | 0 | 1/2"-N-710146-TUBING | HEADER | 12 | 80 | 1 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.50A | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
N710105 | 08 | 32 | 1/2" | N | 710105 | TUBING | N | 0 | HEADER (1/2"-N-710146-TUBING) | 32-C-7101 | 12 | 80 | 5.5 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.50A | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
N710104 | 08 | 32 | 1/2" | N | 710104 | TUBING | N | 0 | HEADER (1/2"-N-710103-TUBING) | 32-C-7101 | 12 | 80 | 1 | 31 | <50 | NA | NA | NA | NITROGEN | G | N | - | >1.5 | 0 | sh.50A | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
ET710112 | 08 | 32 | 1/2" | ET | 710112 | TUBING | N | 0 | 32-C-7101 | 32-D-7102 | 10 | 80 | 1.37 | 50 | <50 | NA | NA | NA | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 1 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 041 | N | - | REV4_PKG 32-PK-7101
N710114 | 08 | 32 | 1/2" | N | 710114 | TUBING | N | 0 | 32-C-7101 | 32-D-7103 | 10 | 80 | 1 | 50 | <50 | NA | NA | NA | ETHYLENE | G | N | - | >1.5 | 0 | sh.50B | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 041 | N | - | REV4_PKG 32-PK-7101
VA710116 | 08 | 32 | 1" | VA | 710116 | TUBING | N | 0 | 32-D-7103 32-PSV-7176 32-PSV-7180 | TP 15 | 10 | 80 | 1 | 50 | <50 | - | 15 | NA | VENT TO ATM | G | N | - | >1.5 | 0 | sh.50A | 1 | Art.4.3 | NA | N | NA | N | 32-P-006-04 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
LO710109 | 08 | 32 | 3/4" | LO | 710109 | TUBING | N | 0 | TP 11 | 32-LSL-7153 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710111 | 08 | 32 | 1/2" | LO | 710111 | TUBING | N | 0 | 32-LSL-7153 | 32-C-7101 | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710112 | 08 | 32 | 1" | LO | 710112 | TUBING | N | 0 | 32-LSL-7153 | 32-C-7101 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710103 | 08 | 32 | 3/4" | LO | 710103 | TUBING | N | 0 | 1"-LO-710112-TUBING | 32-P-7102 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710104 | 08 | 32 | 3/4" | LO | 710104 | TUBING | N | 0 | 32-P-7102 | 32-E-7103 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710101 | 08 | 32 | 3/4" | LO | 710101 | TUBING | N | 0 | 32-P-7101 | 3/4"-LO-710104-TUBING | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710108 | 08 | 32 | 1/2" | LO | 710108 | TUBING | N | 0 | 3/4"-LO-710101-TUBING | 3/4"-LO-710101-TUBING | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710107 | 08 | 32 | 3/4" | LO | 710107 | TUBING | N | 0 | 3/4"-LO-710101-TUBING | 32-PSV-7195 | 10 | 90 | 6 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710102 | 08 | 32 | 3/4" | LO | 710102 | TUBING | N | 0 | 3/4"-LO-710104-TUBING | 32-TCV-7166 | 10 | 90 | 8 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710105 | 08 | 32 | 3/4" | LO | 710105 | TUBING | N | 0 | 32-E-7103 | 32-TCV-7166 | 10 | 90 | 6 | 50 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710110 | 08 | 32 | 3/4" | LO | 710110 | TUBING | N | 0 | 32-TCV-7166 | 32-S-7101A/B | 10 | 90 | 6 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710106 | 08 | 32 | 3/4" | LO | 710106 | TUBING | N | 0 | 32-S-7101A/B | 32-C-7101 - OIL HEADER | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710113 | 08 | 32 | 1/4" | LO | 710113 | TUBING | N | 0 | 3/4"-LO-710104-TUBING | 32-PCV-7199 | 10 | 90 | 6 | 60 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
LO710114 | 08 | 32 | 1/4" | LO | 710114 | TUBING | N | 0 | 32-PCV-7136 | 3/4"-LO-710106-TUBING | 10 | 90 | 2.5 | 49 | 892 | NA | NA | NA | LUBE OIL | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-05 |  | - | N | 110 | N | - | REV4_PKG 32-PK-7101
JWS710114 | 08 | 32 | 2" | JWS | 710114 | B1 | N | 0 | TP 12 | 3/4"-JWS-710118-TUBING | 9 | 180 | 5 | 30 | <50 | - | 13.5 | H | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | 1-A | N | 32-P-006-06 |  | A | N | 000 | N | - | REV4_PKG 32-PK-7101
JWS710118 | 08 | 32 | 3/4" | JWS | 710118 | TUBING | N | 0 | 2"-JWS-710114-B1 | 3/4"-JWS-710103-TUBING 1/2"-JWS-710116-TUBING | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWS710103 | 08 | 32 | 3/4" | JWS | 710103 | TUBING | N | 0 | 3/4"-JWS-710118-TUBING | 32-C-7101 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWS710105 | 08 | 32 | 1/2" | JWS | 710105 | TUBING | N | 0 | 3/4"-JWS-710103-TUBING | 32-C-7101 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWS710116 | 08 | 32 | 1/2" | JWS | 710116 | TUBING | N | 0 | 3/4"-JWS-710118-TUBING | 32-E-7103 | 9 | 180 | 5 | 30 | <50 | NA | NA | NA | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWS710107 | 08 | 32 | 2" | JWS | 710107 | B1 | N | 0 | 2"-JWS-710114-B1 | 32-E-7104 | 9 | 180 | 5 | 30 | <50 | - | 13.5 | H | JACKET WATER SUPPLY | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | 1-A | N | 32-P-006-06 |  | A | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710106 | 08 | 32 | 1/2" | JWR | 710106 | TUBING | N | 0 | 32-C-7101 | 3/4"-JWR-710119-TUBING | 9 | 180 | 5 | 36 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710104 | 08 | 32 | 3/4" | JWR | 710104 | TUBING | N | 0 | 32-C-7101 | 3/4"-JWR-710106-TUBING | 9 | 180 | 5 | 36 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710117 | 08 | 32 | 1/2" | JWR | 710117 | TUBING | N | 0 | 32-E-7103 | 3/4"-JWR-710119-TUBING | 9 | 180 | 5 | 36 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50C | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710119 | 08 | 32 | 3/4" | JWR | 710119 | TUBING | N | 0 | 1/2"-JWR-710106-TUBING | 2"-JWR-710101-B1 | 9 | 180 | 5 | 36 | <50 | NA | NA | NA | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | NA | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710108 | 08 | 32 | 2" | JWR | 710108 | B1 | N | 0 | 32-E-7104 | 2"-JWR-710101-B1 | 9 | 180 | 5 | 36 | <50 | - | 13.5 | H | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | 1-A | N | 32-P-006-06 |  | A | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710111 | 08 | 32 | 3/4" | JWR | 710111 | B1 | N | 0 | 2"-JWR-710101-B1 | 32-TSV-7174 | 9 | 180 | 5 | 36 | <50 | - | 13.5 | H | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | 1-A | N | 32-P-006-06 |  | A | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710112 | 08 | 32 | 1" | JWR | 710112 | TUBING | N | 0 | 32-TSV-7174 | BASEPLATE DRAIN | 9 | 180 | 5 | 36 | <50 | - | 13.5 | H | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | 1-A | N | 32-P-006-06 |  | - | N | 000 | N | - | REV4_PKG 32-PK-7101
JWR710101 | 08 | 32 | 2" | JWR | 710101 | B1 | N | 0 | 3/4"-JWR-710119-TUBING | TP 13 | 9 | 180 | 5 | 36 | <50 | - | 13.5 | H | JACKET WATER RETURN | L | N | - | <1.5 | 0 | sh.50D | 2 | Art.4.3 | NA | N | 1-A | N | 32-P-006-06 |  | A | N | 000 | N | - | REV4_PKG 32-PK-7101
FL710121 | 08 | 32 | 3" | FL | 710121 | B4S1 | N | 0 | 32-PSV-7175 | TP 14 | 9 | 180 | 5 | 36 | <50 | - | 13.5 | H | FL | G | N | - | >1.5 | 0 | sh.50D | 2 | I | Mod.A2 | Y | 1-A | N | 32-P-006-06 |  | A | N | 000 | N | - | REV4_PKG 32-PK-7101
PR720101 | 08 | 32 | 6" | PR | 720101 | C42S1 | N | 0 | TP014 | 6"-PR-720110-C42S1 and 6"-PR-720111-C42S1 | 43,7 | -45/80 | 24 | 40 | 483,6 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 1 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720104 | 08 | 32 | 6" | PR | 720104 | C42S1 | HA | 120/30 | 32-T-7202A PROPYLENE DRYING TOWER | 6"-PR-720106-C42S1 | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720104 | 08 | 32 | 6" | PR | 720104 | C42S1 | HA | 120/30 | 32-T-7202A PROPYLENE DRYING TOWER | 6"-PR-720106-C42S1 | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720105 | 08 | 32 | 6" | PR | 720105 | C42S1 | HA | 120/30 | 32-T-7202B PROPYLENE DRYING TOWER | 6"-PR-720106-C42S1 | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720105 | 08 | 32 | 6" | PR | 720105 | C42S1 | HA | 120/30 | 32-T-7202B PROPYLENE DRYING TOWER | 6"-PR-720106-C42S1 | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720106 | 08 | 32 | 6" | PR | 720106 | C42S1 | N | 0 | 6"-PR-720104-C42S1-HA and 6"-PR-720105-C42S1-HA | TP004 | 43,7 | -45/80 | 23,5 | 40 | 483,4 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 1 | Y | 32-P-007-03 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720109 | 08 | 32 | 6" | PR | 720109 | C42S1 | N | 0 | 6"-PR-720104-C42S1-HA and 6"-PR-720105-C42S1-HA | 6"-PR-720110-C42S1 and 6"-PR-720111-C42S1 | 43,7 | -45/150 | 23,8 | 40 | 483,5 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 1 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720110 | 08 | 32 | 6" | PR | 720110 | C42S1 | P | 40 | 6"-PR-720101-C42S1-P and 3"-N-720120-C42S1-P | 32-T-7202A PROPYLENE DRYING TOWER | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720110 | 08 | 32 | 6" | PR | 720110 | C42S1 | P | 40 | 6"-PR-720101-C42S1-P and 3"-N-720120-C42S1-P | 32-T-7202A PROPYLENE DRYING TOWER | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720111 | 08 | 32 | 6" | PR | 720111 | C42S1 | P | 40 | 6"-PR-720101-C42S1-P and 3"-N-720121-C42S1-P | 32-T-7202B PROPYLENE DRYING TOWER | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720111 | 08 | 32 | 6" | PR | 720111 | C42S1 | P | 40 | 6"-PR-720101-C42S1-P and 3"-N-720121-C42S1-P | 32-T-7202B PROPYLENE DRYING TOWER | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | III | MOD.B+C2 | Y | 5 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
N720112 | 08 | 32 | 3" | N | 720112 | C42S1 | HA | 90 | 3"-N-720114-B4S2-HA | 6"-PR-720104-C42S1-HA | 4,5 | 300 | 3,2 | 280 | 2,55 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720112 | 08 | 32 | 3" | N | 720112 | C42S1 | HA | 90 | 3"-N-720114-B4S2-HA | 6"-PR-720104-C42S1-HA | 4,5 | 300 | 3,2 | 280 | 2,55 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720113 | 08 | 32 | 3" | N | 720113 | C42S1 | HA | 90 | 3"-N-720114-B4S2-HA | 6"-PR-720105-C42S1-HA | 4,5 | 300 | 3,2 | 280 | 2,55 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720113 | 08 | 32 | 3" | N | 720113 | C42S1 | HA | 90 | 3"-N-720114-B4S2-HA | 6"-PR-720105-C42S1-HA | 4,5 | 300 | 3,2 | 280 | 2,55 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720114 | 08 | 32 | 3" | N | 720114 | C42S1 | HA | 90 | 3"-N-720154-B4S2-HA | 3"-N-720112-C42S1-HA and 3"-N-720113-C42S1-HA | 4,5 | 300 | 3,2 | 280 | 2,55 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
PR720115 | 08 | 32 | 2" | PR | 720115 | C42S1 | N | 0 | 6"-PR-720105-C42S1-HA | TP018 | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720116 | 08 | 32 | 1-1/2" | PR | 720116 | C42S1 | HA | 30 | 1½"-PR-720160-C42S1-HA | TP 012 | 43,7 | -45/150 | 24 | 67 | 54,18 | 62,5 | 65,5 | H | Vaporyzed propylene | V | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 5 | N | 32-P-007-05 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720117 | 08 | 32 | 1-1/2" | PR | 720117 | C42S1 | HA | 30 | 1½"-PR-720116-C42S1-HA | 6"-PR-720104-C42S1-HA | 43,7 | -45/150 | 24 | 67 | 54,18 | 62,5 | 65,5 | H | Vaporyzed propylene | V | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 5 | N | 32-P-007-05 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720118 | 08 | 32 | 1-1/2" | PR | 720118 | C42S1 | HA | 30 | 1½"-PR-720116-C42S1-HA | 6"-PR-720105-C42S1-HA | 43,7 | -45/150 | 24 | 67 | 54,18 | 62,5 | 65,5 | H | Vaporyzed propylene | V | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 5 | N | 32-P-007-05 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720119 | 08 | 32 | 4" | PR | 720119 | C42S1 | N | 0 | 6"-PR-720101-C42S1 | 6"-PR-720106-C42S1 | 43,7 | -45/80 | 24 | 40 | 483,6 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-03 |  | E | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
N720120 | 08 | 32 | 3" | N | 720120 | C42S1 | P | 30 | 6"-PR-720110-C42S1-P | 3"-N-720124-B4S2-P | 4,5 | 300 | 2,95 | 260 | 2,47 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720120 | 08 | 32 | 3" | N | 720120 | C42S1 | P | 30 | 6"-PR-720110-C42S1-P | 3"-N-720124-B4S2-P | 4,5 | 300 | 2,95 | 260 | 2,47 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720121 | 08 | 32 | 3" | N | 720121 | C42S1 | P | 30 | 6"-PR-720111-C42S1-P | 3"-N-720124-B4S2-P | 4,5 | 300 | 2,95 | 260 | 2,47 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720121 | 08 | 32 | 3" | N | 720121 | C42S1 | P | 30 | 6"-PR-720111-C42S1-P | 3"-N-720124-B4S2-P | 4,5 | 300 | 2,95 | 260 | 2,47 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720124 | 08 | 32 | 3" | N | 720124 | B4S2 | P | 30 | 3"-N-720120-B4S2-P and 3"-N-720121-B4S2-P | 32-E-7205 NITROGEN COOLER | 4,5 | 300 | 2,95 | 260 | 2,47 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
PR720125 | 08 | 32 | 1" | PR | 720125 | B32S1 | N | 0 | 3"-N-720120-C42S1-P | 1"-PR-720126-B32S1 | 3,5 | 80 | 2 | 32 | 5,22 | 4,55 | 5,25 | H | Propylene or / and Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-04 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720126 | 08 | 32 | 1" | PR | 720126 | B32S1 | N | 0 | 3"-N-720121-C42S1-P | TP016 | 3,5 | 80 | 2 | 32 | 5,22 | 4,55 | 5,25 | H | Propylene or / and Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
N720128 | 08 | 32 | 1/2" | N | 720128 | B32S1 | N | 0 | 3"-N-720114-C42S1-HA | TP015 | 3,5 | 300 | 1,37 | 280 | 1,45 | 4,55 | 5,25 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-04 |  | D | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720129 | 08 | 32 | 3" | N | 720129 | B4S2 | HA | 80 | 3"-N-720154-C42S1-HA | TP013 | 4,5 | 250 | 3,2 | 225 | 2,83 | 5,85 | 6,75 | H | External Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
PR720130 | 08 | 32 | 3/4" | PR | 720130 | C42S1 | N | 0 | 6"-PR-720107-C42S1 and 6"-PR-720108-C42S1 | TP019 | 43,7 | -45/150 | 23,8 | 40 | 483,5 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-04 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720131 | 08 | 32 | 3/4" | PR | 720131 | C42S1 | N | 0 | 6"-PR-720101-C42S1 | TP020 | 43,7 | -45/80 | 24 | 40 | 483,6 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-04 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720132 | 08 | 32 | 2" | PR | 720132 | C42S1 | N | 0 | 6"-PR-720104-C42S1-HA | TP017 | 43,7 (ads cond.) 4,5 (reg cond.) | -45/150 (ads cond.) 300 (reg cond.) | 23,8 (ads cond.) 3,2 (reg cond.) | 40 (ads cond.) 280 (reg cond.) | 483,5 (ads) 2,55 (reg) | 62,5 | 65,5 | H | Propylene (ads condition) Nitrogen (reg condition) | L G | N | - | >1.5 | -45 | sh.52D | 1 | II | MOD.A2 | Y | 1 | Y | 32-P-007-04 |  | B | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
N720133 | 08 | 32 | 3" | N | 720133 | B4S2 | P | P.G. | TP001 | 3"-N-720124-B4S2-P | 4,5 | 250 | 3 | 180 | 2,55 | 5,85 | 6,75 | H | External Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52D | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-05 |  | E |  | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720144 | 08 | 32 | 4" | N | 720144 | B4S2 | N | 0 | 32-E-7205 NITROGEN COOLER | 32-D-7202 NITROGEN/WATER DEMISTER | 4,5 | 80 | 2,84 | 42 | 4,02 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720146 | 08 | 32 | 4" | N | 720146 | B4S2 | N | 0 | Dsi | 32-S-7200 NITROGEN FILTER | 4,5 | 80 | 2,84 | 42 | 4,02 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
JWS720141 | 08 | 32 | 2" | JWS | 720141 | B1 | N | 0 | TP007 | 32-E-7205 NITROGEN COOLER | 9 | 180 | 5 | 30 | 1000 | 11,7 | 13,5 | H | Jacket water supply | L | N | - | <1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
JWR720142 | 08 | 32 | 2" | JWR | 720142 | B1 | N | 0 | 32-E-7205 NITROGEN COOLER | TP008 | 9 | 180 | 4,8 | 38 | 1000 | 11,7 | 13,5 | H | Jacket water return | L | N | - | <1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720145 | 08 | 32 | 1" | N | 720145 | B4S2 | ET | 40 | 32-D-7202 NITROGEN/WATER DEMISTER | TP010 | 4,5 | 65 | 2,7 | 42 | 1000 | 5,85 | 6,75 | H | Water | L | N | - | <1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 20 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720147 | 08 | 32 | 1" | N | 720147 | B4S2 | N | 0 | 4"-N-720146-B4S2 | 1"-N-720162-B32S1 | 4,5 | 65 | 2,84 | 42 | 4,02 | 5,85 | 6,75 | H | Regeneration Nitrogen BD | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720148 | 08 | 32 | 1-1/2" | N | 720148 | B4S2 | N | 0 | TP009 | 4"-N-720146-B4S2 | 4,5 | 65 | 2,84 | 42 | 4,02 | 5,85 | 6,75 | H | Regeneration Nitrogen MU | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720149 | 08 | 32 | 1-1/2" | N | 720149 | B4S2 | N | 0 | 4"-N-720146-B4S2 | PSV-7257 | 4,5 | 65 | 2,84 | 42 | 4,02 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720150 | 08 | 32 | 4" | N | 720150 | B4S2 | N | 0 | 32-S-7200 NITROGEN FILTER | 32-C-7200 NITROGEN RECYCLE BLOWER | 4,5 | 65 | 2,84 | 42 | 4,02 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720151 | 08 | 32 | 4" | N | 720151 | B4S2 | N | 0 | 32-C-7200 NITROGEN RECYCLE BLOWER | 32-E-7206 NITROGEN ELECTRIC HEATER | 4,5 | 80 | 3,3 | 59 | 4,3 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720152 | 08 | 32 | 2" | N | 720152 | B4S2 | N | 0 | 4"-N-720151-B4S2 | 3"-N-720124-B4S2-P | 4,5 | 80 | 3,3 | 59 | 4,3 | 5,85 | 6,75 | H | Regeneration Nitrogen Bypass | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720154 | 08 | 32 | 3" | N | 720154 | B4S2 | HA | 90 | 32-E-7206 NITROGEN ELECTRIC HEATER | 3"-N-720113-C42S1-HA and 3"-N-720114-C42S1-HA | 4,5 | 300 | 3,2 | 280 | 2,55 | 5,85 | 6,75 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
LS720155 | 08 | 32 | 1-1/2" | LS | 720155 | C42S1 | HB | 50 | TP002 | 32-E-7204 PROPYLENEVAPORIZER | 6,5 | -45/250 | 3,5 | 200 | 2,3 | 8,45 | 9,75 | H | Low Pressure Steam | V | N | - | >1.5 | -45 | sh.52A | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
LS720156 | 08 | 32 | 1" | LS | 720156 | C42S1 | HB | 50 | 1½"-LS-720155-C42S1-HB | TO SAFE LOCATION | 6,5 | -45/250 | 3,5 | 200 | 2,3 | 8,45 | 9,75 | H | Low Pressure Steam | V | N | - | >1.5 | -45 | sh.52A | 2 | Art.4.3 | NA | N | 5 | N | 32-U-052-01 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
LC720157 | 08 | 32 | 1" | LC | 720157 | C42S1 | HB | 50 | 32-E-7204 PROPYLENEVAPORIZER | 1"-LC-720158-B5-P | 6,5 | -45/250 | 3,5 | 148 | 905 | 8,45 | 9,75 | H | Low Pressure Condensate | L | N | - | >1.5 | -45 | sh.52A | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
LC720158 | 08 | 32 | 1" | LC | 720158 | B5 | P | P.G. | 1"-LC-720157-C42S1-P | TP005 | 6,5 | 180 | 3,5 | 148 | 905 | 8,45 | 9,75 | H | Low Pressure Condensate | L | N | - | >1.5 | - | sh.52A | 2 | Art.4.3 | NA | N | 5 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
PR720159 | 08 | 32 | 1-1/2" | PR | 720159 | C42S1 | N | 0 | TP011 | 32-E-7204 PROPYLENEVAPORIZER | 43,7 | -45/80 | 24 | 40 | 483,6 | 62,5 | 65,5 | H | Propylene | L | N | - | >1.5 | -45 | sh.52A | 1 | II | MOD.A2 | Y | 1 | N | 32-P-007-05 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720160 | 08 | 32 | 1-1/2" | PR | 720160 | C42S1 | HA | 30 | 32-E-7204 PROPYLENEVAPORIZER | 1½"-PR-720117-C42S1-HA and 1½"-PR-720118-C42S1-HA | 43,7 | -45/150 | 24 | 67 | 54,18 | 62,5 | 65,5 | H | Vaporyzed propylene | V | N | - | >1.5 | -45 | sh.52A | 1 | II | MOD.A2 | Y | 5 | N | 32-P-007-05 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PR720161 | 08 | 32 | 1-1/2" | PR | 720161 | C42S1 | HA | 30 | 1½"-PR-720160-C42S1-HA | TP023 | 43,7 | -45/150 | 24 | 67 | 54,18 | 62,5 | 65,5 | H | Vaporyzed propylene | V | N | - | >1.5 | -45 | sh.52A | 1 | II | MOD.A2 | Y | 5 | N | 32-P-007-05 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
N720162 | 08 | 32 | 1" | N | 720162 | B32S1 | N | 0 | 1"-N-720147-B4S2 | TP021 | 3,5 | 120 | 1,37 | 42 | 2,55 | 4,55 | 5,25 | H | Regeneration Nitrogen BD | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | D | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720163 | 08 | 32 | 2" | N | 720163 | B32S1 | N | 0 | PSV-7258 | 3"-N-720166-B32S1 | 3,5 | 250 | 1,37 | 188 | 2,55 | 4,55 | 5,25 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | D | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
N720166 | 08 | 32 | 3" | N | 720166 | B32S1 | N | 0 | PSV-7257 | TP006 | 3,5 | 250 | 1,37 | 218 | - | 4,55 | 5,25 | H | Regeneration Nitrogen | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-05 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
IA720165 | 08 | 32 | 1" | IA | 720165 | B13 | N | 0 | TP003 | PNEUMATIC USERS | 10 | 60 | 7 | 40 | 8,9 | 13 | 15 | H | Instrument Air | G | N | - | >1.5 | - | sh.52B | 2 | Art.4.3 | NA | N | 1 | N | 32-P-007-04 |  | E | N | 0 0 0 | N | - | REV05_PKG 32-PK-7200
PR720167 | 08 | 32 | 1/2" | PR | 720167 | C42S1 | N | 0 | 32-LI-7253 (PROPYLENE VAPORIZER) | TP025 | 3,5 | 120 | 2 | 32 | 54,18 | 4,55 | 5,25 | H | Propylene | G | N | - | >1.5 | - | sh.52A | 1 | II | MOD.A2 | Y | 5 | N | 32-P-007-04 |  | A | N | 0 FG1 0 | N | - | REV05_PKG 32-PK-7200
PEP520122 | 08 | 32 | 6" | PEP | 520122 | CHX4.5A1004 | P | 50 | 32-D-5200 | 32-V-5200A | -0.5 / 0.4 | 0 /120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | PP-Powder | S | N | - | >1.5 | 0 | sh.37 | 2 | NA | NA | N | 5 | N | 32-P-052-03 |  | VT | N | 110 | N | - | REV03_PKG 32-PK-8001 to 9004
PEP520122 | 08 | 32 | 10" | PEP | 520122 | CHX4.5A1004 | P | 100 | 32-D-5200 | 32-V-5200A | -0.5 / 0.4 | 0 / 120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | PP-Powder | S | N | - | >1.5 | 0 | sh.37 | 2 | NA | NA | N | 5 | N | 32-P-052-03 |  | VT | N | 110 | N | - | REV03_PKG 32-PK-8001 to 9004
PEP520123 | 08 | 32 | 10" | PEP | 520123 | CHX4.5A1004 | P | 100 | 32-V-5200A | 32-H-5201 | -0.5 / 0.4 | 0 / 120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | PP-Powder | S | N | - | >1.5 | 0 | sh.37 | 2 | NA | NA | N | 5 | N | 32-P-052-03 |  | VT | N | 110 | N | - | REV03_PKG 32-PK-8001 to 9004
PEP520124 | 08 | 32 | 10" | PEP | 520124 | CHX4.5A1004 | P | 100 | 32-HV-5203 | Collecting Box | -0.5 / 0.1 | 0 / 120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | PP-Powder | S | N | - | >1.5 | 0 | sh.37 | 2 | NA | NA | N | 5 | N | 32-P-052-03 |  | VT | N | 110 | N | - | REV03_PKG 32-PK-8001 to 9004
VG520126 | 08 | 32 | 2-1/2" | VG | 520126 | CHX4.5A1104 | P | 50 | 32-V-5200B | 32-H-5201 | -0.5 / 3.5 | 0 / 120 | 0,05 / 0.1 | 65 / 80 | NA | 0,1 | NA | N | Process Vent | G | N | - | >1.5 | 0 | sh.37 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-052-03 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VA520127 | 08 | 32 | 3" | VA | 520127 | CHX1.0A1104 | P | 50 | 32-S-5200 | ATM | -0.5 / 0.1 | 0 /120 | 0 / 0.02 | 65 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.37 | 2 | NA | NA | N | 5 | N | 32-P-052-03 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP520125 | 08 | 32 | 12" | PEP | 520125 | CHX4.5A1004 | P | 100 | 32-H-5201 | 32-V-5200B | -0.5 / 3.5 | 0 / 120 | 0 / 0.1 | 65 / 80 | NA | 0.1 | 5.25 | N/H | PP Powder | S | N | - | >1.5 | 0 | sh.37 | 2 | I | MOD.A | Y | 5 | N | 32-P-052-03 |  | VT | N | 110 | N | - | REV03_PKG 32-PK-8001 to 9004
CVA630350 | 08 | 32 | 3" | CVA | 630350 | CHX4.5A1104 | N | 0 | 32-S-8301 | 32-V-8301 | -0.5 / 0.1 | 0 / 110 | -0.3 / -0.26 | 20 / 31 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
CVA630350 | 08 | 32 | 4" | CVA | 630350 | CHX4.5A1104 | N | 0 | 32-S-8301 | 32-V-8301 | -0.5 / 0.1 | 0 / 110 | -0.3 / -0.26 | 20 / 31 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
PP630351 | 08 | 32 | 8" | PP | 630351 | CHX1.0A1004 | PP | 75 | 32-HV-8302 | 32-Z-8300 | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP630352 | 08 | 32 | 8" | PP | 630352 | CHX1.0A1004 | PP | 75 | 32-HV-8301 | 32-Z-8300 | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP630353 | 08 | 32 | 6" | PP | 630353 | CHX1.0A1004 | PP | 50 | 32-Z-8300 | 32-V-8301 | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P630355 | 08 | 32 | 3" | P | 630355 | CHX8.0A1200 | N | 0 | 32-V-8301 | 32-S-8300 | -0.5 / 0.1 | 0 / 110 | -0.3 / -0.26 | 40 / 60 | NA | NA | NA | V | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
P630355 | 08 | 32 | 4" | P | 630355 | CHX8.0A1200 | N | 0 | 32-V-8301 | 32-S-8300 | -0.5 / 0.1 | 0 / 110 | -0.3 / -0.26 | 40 / 60 | NA | NA | NA | V | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
pp630356 | 08 | 32 | 6" | pp | 630356 | CHX1.0A1004 | N | 0 | 32-S-8300 | 32-V-8300 | -0.5 / 0.1 | 0 / 110 | -0.3 / -0.26 | 20 / 31 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
PP630357 | 08 | 32 | 6" | PP | 630357 | CHX1.0A1004 | N | 0 | 32-V-8300 | Extruder K-8900 | -0.5 / 0.1 | 0 / 110 | 0 / 0 | 20 / 31 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
CVA630360 | 08 | 32 | 4" | CVA | 630360 | CHX4.5A1104 | N | 0 | 32-S-8300 | 32-XV-8320 | -0.5 / 0.1 | 0 / 110 | -0.32 / 0 | 40 / 55 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
CVA630361 | 08 | 32 | 4" | CVA | 630361 | CHX4.5A1104 | N | 0 | 32-S-8302 | 32-C-8300 | -0.5 / 0.1 | 0 / 110 | -0.32 / 0 | 40 / 55 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
CVA630361 | 08 | 32 | 5" | CVA | 630361 | CHX4.5A1104 | N | 0 | 32-S-8302 | 32-C-8300 | -0.5 / 0.1 | 0 / 110 | -0.32 / 0 | 40 / 55 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
VA630362 | 08 | 32 | 5" | VA | 630362 | CHX8.0A1104 | P | 50 | 32-C-8300 | ATM | -0.5 / 0.1 | 0 / 150 | 0 / 0.1 | 109 / 111 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | NA | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA630363 | 08 | 32 | 4" | CVA | 630363 | CHX4.5A1104 | N | 0 | 32-XV-8320 | 32-S-8302 | -0.5 / 0.1 | 0 / 110 | -0.32 / 0 | 40 / 55 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.63 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
N800100 | 08 | 32 | 10" | N | 800100 | CHX8.0A1104 | P | 40 | 32-C-8001A | 800101 | -0.5 / 3.5 | 0 /280 | 2.36 / 2.83 | 214 / 237 | NA | 2.83 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800100 | 08 | 32 | 8" | N | 800100 | CHX8.0A1104 | P | 40 | 32-C-8001A | 800101 | -0.5 / 3.5 | 0 / 280 | 2.36 / 2.83 | 214 / 237 | NA | 2.83 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800101 | 08 | 32 | 10" | N | 800101 | CHX8.0A1104 | P | 40 | 32-C-8001B | 32-E-8001 | -0.5 / 3.5 | 0 / 280 | 2.36 / 2.83 | 214 / 237 | NA | 2.83 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800101 | 08 | 32 | 8" | N | 800101 | CHX8.0A1104 | P | 40 | 32-C-8001B | 32-E-8001 | -0.5 / 3.5 | 0 / 280 | 2.36 / 2.83 | 214 / 237 | NA | 2.83 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800102 | 08 | 32 | 10" | N | 800102 | CHX4.5A1104 | P | 100 | 32-E-8001 | 32-S-8011 | -0.5 / 3.5 | 0 / 110 | 2.30 / 2.77 | 60 / 70 | NA | 2.77 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800102 | 08 | 32 | 8" | N | 800102 | CHX4.5A1104 | P | 75 | 32-E-8001 | 32-S-8011 | -0.5 / 3.5 | 0 / 110 | 2.30 / 2.77 | 60 / 70 | NA | 2.77 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800103 | 08 | 32 | 10" | N | 800103 | CHX4.5A1104 | P | 100 | 32-S-8011 | 32-V-8001A | -0.5 / 3.5 | 0 / 110 | 2.2 / 2.6 | 60 / 70 | NA | 2.6 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800103 | 08 | 32 | 6" | N | 800103 | CHX4.5A1104 | P | 50 | 32-S-8011 | 32-V-8001A | -0.5 / 3.5 | 0 / 110 | 2.2 / 2.6 | 60 / 70 | NA | 2.6 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800104 | 08 | 32 | 10" | N | 800104 | CHX4.5A1104 | P | 100 | 800103 | 800132 | -0.5 / 3.5 | 0 / 280 | 0.1 / 0.2 | 60 / 70 | NA | 0.2 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800105 | 08 | 32 | 4" | N | 800105 | CHX8.0A1104 | P | 30 | 32-PSV-8016 | 800106 | -0.5 / 3.5 | 0 / 280 | 0.1 / 0.2 | 214 / 237 | NA | 0.2 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800105 | 08 | 32 | 8" | N | 800105 | CHX8.0A1104 | P | 40 | 32-PSV-8016 | 800106 | -0.5 / 3.5 | 0 / 280 | 0.1 / 0.2 | 214 / 237 | NA | 0.2 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800106 | 08 | 32 | 4" | N | 800106 | CHX8.0A1104 | P | 30 | 32-PSV-8015 | 800104 | -0.5 / 3.5 | 0 / 280 | 0.1 / 0.2 | 214 / 237 | NA | 0.2 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800106 | 08 | 32 | 8" | N | 800106 | CHX8.0A1104 | P | 40 | 32-PSV-8015 | 800104 | -0.5 / 3.5 | 0 / 280 | 0.1 / 0.2 | 214 / 237 | NA | 0.2 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | NA | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800107 | 08 | 32 | 10" | N | 800107 | CHX1.0A1104 | N | 0 | 32-PV-8011B | ATM | -0.5 / 0,2 | 0 / 110 | 0 / 0,1 | 50 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
P800109 | 08 | 32 | 6" | P | 800109 | CHX8.0A4200 | P | 50 | 32-V-8001A | 32-V-8001B | -0.5 / 3.5 | 0 /120 | 2.2 / 2.6 | 65 / 80 | NA | 2.6 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P800110 | 08 | 32 | 6" | P | 800110 | CHX8.0A4200 | P | 50 | 32-V-8001B | 32-V-5200B | -0.5 / 3.5 | 0 / 120 | 2.2 / 2.5 | 65 / 80 | NA | 2.5 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800111 | 08 | 32 | 16" | PEP | 800111 | CHX4.5A1004 | P | 100 | A-5200 | 32-V-8000B | -0.5 / 0.2 | 0 /120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800112 | 08 | 32 | 16" | PEP | 800112 | CHX4.5A1004 | P | 100 | A-5200 | 32-V-8000A | -0.5 / 0.2 | 0 / 120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800113 | 08 | 32 | 20" | PEP | 800113 | CHX4.5A1004 | P | 100 | 32-V-8000B | 32-H-8001 | -0.5 / 0,5 | 0 /120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800114 | 08 | 32 | 20" | PEP | 800114 | CHX4.5A1004 | P | 100 | 32-V-8000A | 32-H-8001 | -0.5 /0,5 | 0 / 120 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800115 | 08 | 32 | 6" | N | 800115 | CHX1.0A1104 | P | 50 | 32-S-8000 | 800130 | -0.5 / 0.2 | 0 / 120 | 0 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_C |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800115 | 08 | 32 | 12" | N | 800115 | CHX1.0A1104 | P | 100 | 32-S-8000 | 800130 | -0.5 / 0.2 | 0 / 120 | 0 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_C |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG800117 | 08 | 32 | 5" | VG | 800117 | CHX4.5A1104 | P | 50 | 32-V-8001B | 32-H-8001 | -0.5 / 3.5 | 0 / 120 | 0.1 / 0.2 | 65 / 80 | NA | 0.2 | NA | N | Process Vent | G | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-052-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG800119 | 08 | 32 | 5" | VG | 800119 | CHX4.5A1104 | P | 50 | 32-V-8001A | 32-H-8001 | -0.5 / 3.5 | 0 / 120 | 0.1 / 0.2 | 65 / 80 | NA | 0.2 | NA | N | Process Vent | G | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-052-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800116 | 08 | 32 | 16" | PEP | 800116 | CHX4.5A1004 | P | 100 | 32-H-8001 | 32-V-8001B | -0.5 / 3.5 | 0 / 120 | 0.1 / 0.2 | 65 / 80 | NA | 0.2 | 5.25 | N/H | PP Powder | S | N | - | >1.5 | 0 | sh.56 | 2 | I | MOD.A | Y | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P800120 | 08 | 32 | 6" | P | 800120 | CHX8.0A4200 | P | 50 | 32-V-5200B | 32-D-8002A | -0.5 / 3.5 | 0 / 110 | 2.1 / 2.5 | 65 / 80 | NA | 2.5 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800118 | 08 | 32 | 16" | PEP | 800118 | CHX4.5A1004 | P | 100 | 32-H-8001 | 32-V-8001A | -0.5 / 3.5 | 0 / 120 | 0.1 / 0.2 | 65 / 80 | NA | 0.2 | 5.25 | N/H | PP Powder | S | N | - | >1.5 | 0 | sh.56 | 2 | I | MOD.A | Y | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P800120 | 08 | 32 | 7" | P | 800120 | CHX8.0A4200 | P | 75 | 32-V-5200B | 32-D-8002A | -0.5 / 3.5 | 0 / 110 | 2.1 / 2.5 | 65 / 80 | NA | 2.5 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P800120 | 08 | 32 | 8" | P | 800120 | CHX8.0A4200 | P | 75 | 32-V-5200B | 32-D-8002A | -0.5 / 3.5 | 0 / 110 | 2.1 / 2.5 | 65 / 80 | NA | 2.5 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.56 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P800121 | 08 | 32 | 8" | P | 800121 | CHX8.0A4200 | P | 75 | 800120 | 32-D-8002B | -0.5 / 3.5 | 0 / 110 | 2.1 / 2.5 | 65 / 80 | NA | 2.5 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.58 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VA800124 | 08 | 32 | 8" | VA | 800124 | XVT0604C | N | 0 | 32-PSV-8001 | ATM | -0.5 / 0.2 | 0 / 110 | 0 / 110 | 50 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
N800130 | 08 | 32 | 10" | N | 800130 | CHX1.0A1104 | P | 100 | 32-S-8001A | 32-S-8002A | -0.5 / 0.2 | 0 / 110 | 0 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.58 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800130 | 08 | 32 | 12" | N | 800130 | CHX1.0A1104 | P | 100 | 32-S-8001A | 32-S-8002A | -0.5 / 0.2 | 0 / 110 | 0 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.58 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800131 | 08 | 32 | 10" | N | 800131 | CHX1.0A1104 | P | 100 | 32-S-8001B | 800130 | -0.5 / 0.2 | 0 / 110 | 0 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.58 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800131 | 08 | 32 | 12" | N | 800131 | CHX1.0A1104 | P | 100 | 32-S-8001B | 800130 | -0.5 / 0.2 | 0 / 110 | 0 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.58 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800132 | 08 | 32 | 10" | N | 800132 | CHX1.0A1104 | P | 100 | 32-S-8002A | 32-E-8000 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800132 | 08 | 32 | 12" | N | 800132 | CHX1.0A1104 | P | 100 | 32-S-8002A | 32-E-8000 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800133 | 08 | 32 | 10" | N | 800133 | CHX1.0A1104 | N | 0 | 32-E-8000 | 32-C-8001A | -0.5 / 0.2 | 0 / 110 | 0 / 0.04 | 50 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
N800133 | 08 | 32 | 12" | N | 800133 | CHX1.0A1104 | N | 0 | 32-E-8000 | 32-C-8001A | -0.5 / 0.2 | 0 / 110 | 0 / 0.04 | 50 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
N800134 | 08 | 32 | 10" | N | 800134 | CHX1.0A1104 | N | 0 | 800133 | 32-C-8001B | -0.5 / 0.2 | 0 / 110 | 0 / 0.04 | 50 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
N800134 | 08 | 32 | 12" | N | 800134 | CHX1.0A1104 | N | 0 | 800133 | 32-C-8001B | -0.5 / 0.2 | 0 / 110 | 0 / 0.04 | 50 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
VA800135 | 08 | 32 | 6" | VA | 800135 | CHX1.0A1140 | P | 50 | 32-H-8001 | A-5200 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG800136 | 08 | 32 | 3" | VG | 800136 | CHX4.5A1104 | P | 50 | 32-V-8000A | A-5200 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-052-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG800137 | 08 | 32 | 3" | VG | 800137 | CHX4.5A1104 | P | 50 | 32-V-8000B | A-5200 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-052-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800140 | 08 | 32 | 2" | PEP | 800140 | CHX4.5A1004 | P | 50 | 800118 | Sampling Point | -0.5 / 0.1 | 0 / 110 | 0.1 / 0.5 | 65 / 80 | NA | NA | NA | V | PP Powder | S | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PEP800141 | 08 | 32 | 2" | PEP | 800141 | CHX4.5A1004 | P | 50 | 800116 | Sampling Point | -0.5 / 0.1 | 0 / 110 | 0.1 / 0.5 | 65 / 80 | NA | NA | NA | V | PP Powder | S | N | - | >1.5 | 0 | sh.56 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800142 | 08 | 32 | 12" | N | 800142 | CHX1.0A1104 | P | 100 | 800130 | 32-S-8002B | -0.5 / 0.2 | 0 / 110 | 0.1 / 0.12 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800143 | 08 | 32 | 12" | N | 800143 | CHX1.0A1104 | P | 100 | 32-S-8002B | 800132 | -0.5 / 0.2 | 0 / 110 | 0.08 / 0.1 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800144 | 08 | 32 | 6" | N | 800144 | CHX1.0A1104 | P | 50 | 32-PSV-8040 | ATM | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.58 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800145 | 08 | 32 | 6" | N | 800145 | CHX1.0A1104 | P | 50 | 32-PSV-8046 | ATM | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 65 / 80 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.58 | 2 | NA | NA | N | 5 | N | 32-P-060-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800146 | 08 | 32 | 10" | N | 800146 | CHX4.5A1104 | P | 100 | 800102 | 800103 | -0.5 / 3.5 | 0 / 110 | 2.3 / 2.77 | 60 / 70 | NA | 2.77 | NA | N | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA810266 | 08 | 32 | 12" | CVA | 810266 | CHX1.0A1104 | P | 100 | 32-S-8107 | ATM | -0.5 / 0.1 | 0 / 110 | 0.01 / 0.02 | 60 / 80 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.62 | 2 | NA | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA880200 | 08 | 32 | 8" | CVA | 880200 | CHX8.0A1104 | P | 75 | 32-C-8002B | 880201 | -0.5 / 2.8 | 0 / 300 | 1.6 / 1.9 | 156 / 171 | NA | 1.9 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | NA | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA880201 | 08 | 32 | 8" | CVA | 880201 | CHX8.0A1104 | P | 75 | 32-C-8002A | 32-E-8005 | -0.5 / 2.8 | 0 / 300 | 1.6 / 1.9 | 156 / 171 | NA | 1.9 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | NA | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA880202 | 08 | 32 | 8" | CVA | 880202 | CHX4.5A1104 | N | 0 | 32-E-8005 | 32-S-8010 | -0.5 / 2.8 | 0 / 110 | 1.5 / 1.8 | 50 | NA | 1.8 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
CVA880203 | 08 | 32 | 8" | CVA | 880203 | CHX4.5A1104 | N | 0 | 32-S-8010 | 32-V-8006A | -0.5 / 2.8 | 0 / 110 | 1.4 / 1.7 | 50 | NA | 1.7 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
CVA880203 | 08 | 32 | 6" | CVA | 880203 | CHX4.5A1104 | N | 0 | 32-S-8010 | 32-V-8006A | -0.5 / 2.8 | 0 / 110 | 1.4 / 1.7 | 50 | NA | 1.7 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
PP880204 | 08 | 32 | 16" | PP | 880204 | CHX1.0A1004 | P | 100 | 32-D-8007 | 32-V-8006B | -0.5 / 0.1 | 0 / 110 | 0.01 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.67 | 2 | NA | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG880205 | 08 | 32 | 2-1/2" | VG | 880205 | CHX4.5A1104 | P | 50 | 32-V-8006B | 32-D-8007 | -0.5 / 2.8 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | 0.1 | NA | N | Process Vent | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP880206 | 08 | 32 | 16" | PP | 880206 | CHX1.0A1004 | P | 100 | 32-D-8007 | 32-V-8006A | -0.5 / 0.1 | 0 / 110 | 0.01 / 0.01 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.67 | 2 | NA | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG880207 | 08 | 32 | 2-1/2" | VG | 880207 | CHX4.5A1104 | P | 50 | 32-V-8006A | 32-D-8007 | -0.5 / 2.8 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.67 | 2 | NA | NA | N | 5 | N | 32-P-080-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA880208 | 08 | 32 | 8" | CVA | 880208 | CHX4.5A1104 | N | 0 | 880202 | 880203 | -0.5 / 2.8 | 0 / 100 | 1.5 / 1.8 | 50 | NA | 1.8 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV02_PKG 32-PK-8001 to 9004
P880209 | 08 | 32 | 6" | P | 880209 | CHX4.5A4500 | P | 50 | 32-V-8006A | 32-V-8006B | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P880210 | 08 | 32 | 6" | P | 880210 | CHX4.5A4500 | P | 50 | 32-V-8006A | 32-H-9001E | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P880210 | 08 | 32 | 7" | P | 880210 | CHX4.5A4500 | P | 75 | 32-V-8006A | 32-H-9001E | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P880210 | 08 | 32 | 8" | P | 880210 | CHX4.5A4500 | P | 75 | 32-V-8006A | 32-H-9001E | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P880211 | 08 | 32 | 6" | P | 880211 | CHX4.5A4500 | P | 50 | 32-XV-8805 | 32-D-8107 | -0.5 / 4.5 | 0 / 100 | 1.03 / 1.24 | 60 / 80 | NA | 1.24 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P880211 | 08 | 32 | 8" | P | 880211 | CHX4.5A4500 | P | 75 | 32-XV-8805 | 32-D-8107 | -0.5 / 4.5 | 0 / 100 | 1.03 / 1.24 | 60 / 80 | NA | 1.24 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P880211 | 08 | 32 | 7" | P | 880211 | CHX4.5A4500 | P | 75 | 32-XV-8805 | 32-D-8107 | -0.5 / 4.5 | 0 / 100 | 1.03 / 1.24 | 60 / 80 | NA | 1.24 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.67 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA90F308 | 08 | 32 | 10" | CVA | 90F308 | CHX8.0A1104 | P | 100 | 910255 | 19-C-9044/9045 | -0.5 / 2.8 | 0 /250 | 1.47 / 1.67 | 150 / 169 | NA | 1.67 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA90F308 | 08 | 32 | 8" | CVA | 90F308 | CHX8.0A1104 | P | 75 | 910255 | 19-C-9044/9045 | -0.5 / 2.8 | 0 /250 | 1.47 / 1.67 | 150 / 169 | NA | 1.67 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910212 | 08 | 32 | 8" | P | 910212 | CHX4.5A4500 | P | 75 | 32-XV-9102A | 32-H-9001A | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 60 / 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910213 | 08 | 32 | 8" | P | 910213 | CHX4.5A4500 | P | 75 | 32-XV-9102B | 32-H-9001B | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 60 / 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910214 | 08 | 32 | 8" | P | 910214 | CHX4.5A4500 | P | 75 | 32-XV-9102C | 32-H-9001C | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 60 / 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910215 | 08 | 32 | 8" | P | 910215 | CHX4.5A4500 | P | 75 | 32-XV-9102D | 32-H-9001D | -0.5 / 2.8 | 0 / 100 | 1.4 / 1.7 | 60 / 80 | NA | 1.7 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-080-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910216 | 08 | 32 | 10" | P | 910216 | CHX4.5A4500 | P | 100 | 32-XV-9106A | 32-H-9001A | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910217 | 08 | 32 | 10" | P | 910217 | CHX4.5A4500 | P | 100 | 32-XV-9106B | 32-H-9001B | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910218 | 08 | 32 | 10" | P | 910218 | CHX4.5A4500 | P | 100 | 32-XV-9106C | 32-H-9001C | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910219 | 08 | 32 | 10" | P | 910219 | CHX4.5A4500 | P | 100 | 32-XV-9106D | 32-H-9001D | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP910220 | 08 | 32 | 12" | PP | 910220 | CHX1.0A1004 | P | 100 | 32-H-9001A | 32-V-9001A | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910221 | 08 | 32 | 12" | P | 910221 | CHX4.5A4500 | P | 100 | 32-XV-9103A | SP-06-191A0-04 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910221 | 08 | 32 | 16" | P | 910221 | CHX4.5A4500 | P | 100 | 32-V-9001A | 32-XV-9103A | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | 4.2 | N/H | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | I | MOD.A | Y | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910222 | 08 | 32 | 12" | P | 910222 | CHX4.5A4500 | P | 100 | 32-XV-9103A | SP-06-191A0-01 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP910223 | 08 | 32 | 12" | PP | 910223 | CHX1.0A1004 | P | 100 | 32-H-9001B | 32-V-9001B | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910224 | 08 | 32 | 12" | P | 910224 | CHX4.5A4500 | P | 100 | 32-XV-9103B | SP-06-191A0-05 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910224 | 08 | 32 | 16" | P | 910224 | CHX4.5A4500 | P | 100 | 32-V-9001B | 32-XV-9103B | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | 4.2 | N/H | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.70 | 2 | I | MOD.A | Y | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910225 | 08 | 32 | 12" | P | 910225 | CHX4.5A4500 | P | 100 | 32-XV-9103B | SP-06-191A0-02 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP910226 | 08 | 32 | 12" | PP | 910226 | CHX1.0A1004 | P | 100 | 32-H-9001C | 32-V-9001C | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910227 | 08 | 32 | 12" | P | 910227 | CHX4.5A4500 | P | 100 | 32-XV-9103C | SP-06-191A0-06 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910227 | 08 | 32 | 16" | P | 910227 | CHX4.5A4500 | P | 100 | 32-V-9001C | 32-XV-9103C | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | 4.2 | N/H | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.70 | 2 | I | MOD.A | Y | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910228 | 08 | 32 | 12" | P | 910228 | CHX4.5A4500 | P | 100 | 32-XV-9103C | SP-06-191A0-03 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP910229 | 08 | 32 | 12" | PP | 910229 | CHX1.0A1004 | P | 100 | 32-H-9001D | 32-V-9001D | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.71 | 2 | NA | NA | N | 5 | N | 32-P-082-04 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910230 | 08 | 32 | 12" | P | 910230 | CHX4.5A4500 | P | 100 | 32-XV-9103D | SP-06-191B0-03 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910230 | 08 | 32 | 16" | P | 910230 | CHX4.5A4500 | P | 100 | 32-V-9001D | 32-XV-9103D | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | 4.2 | N/H | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.71 | 2 | I | MOD.A | Y | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910231 | 08 | 32 | 12" | P | 910231 | CHX4.5A4500 | P | 100 | 32-XV-9103D | SP-06-191B0-01 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP910232 | 08 | 32 | 12" | PP | 910232 | CHX1.0A1004 | P | 100 | 32-H-9001E | 32-V-9001E | -0.5 / 0.1 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.71 | 2 | NA | NA | N | 5 | N | 32-P-082-05 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910233 | 08 | 32 | 12" | P | 910233 | CHX4.5A4500 | P | 100 | 32-XV-9103E | SP-06-191B0-04 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910233 | 08 | 32 | 16" | P | 910233 | CHX4.5A4500 | P | 100 | 32-V-9001E | 32-XV-9103E | -0.5 / 2.8 | 0 / 110 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | 4.2 | N/H | Polymer + Gas | GS | Y | - | >1.5 | 0 | sh.71 | 2 | I | MOD.A | Y | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910234 | 08 | 32 | 12" | P | 910234 | CHX4.5A4500 | P | 100 | 32-XV-9103E | SP-06-191B0-02 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910235 | 08 | 32 | 9" | P | 910235 | CHX4.5A4500 | P | 100 | SP-06-191B0-03 | SP-06-191A0-06 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910236 | 08 | 32 | 9" | P | 910236 | CHX4.5A4500 | P | 100 | 32-XV-9106F | 32-D-8107 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910236 | 08 | 32 | 10" | P | 910236 | CHX4.5A4500 | P | 100 | 32-XV-9106F | 32-D-8107 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-07 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910237 | 08 | 32 | 8" | P | 910237 | CHX4.5A4500 | P | 75 | SP-06-191B0-01 | SP-06-191A0-03 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910240 | 08 | 32 | 10" | CVA | 910240 | CHX8.0A1104 | P | 100 | 32-C-9004A | 32-E-9004 | -0.5 / 1.03 | 0 / 110 | 0.5 | 81 | NA | 0.5 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910240 | 08 | 32 | 12" | CVA | 910240 | CHX8.0A1104 | P | 100 | 32-C-9004A | 32-E-9004 | -0.5 / 1.03 | 0 / 110 | 0.5 | 81 | NA | 0.5 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910241 | 08 | 32 | 10" | CVA | 910241 | CHX8.0A1104 | P | 100 | 32-C-9004B | 910240 | -0.5 / 1.03 | 0 / 110 | 0.5 | 81 | NA | 0.5 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910241 | 08 | 32 | 12" | CVA | 910241 | CHX8.0A1104 | P | 100 | 32-C-9004B | 910240 | -0.5 / 1.03 | 0 / 110 | 0.5 | 81 | NA | 0.5 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910242 | 08 | 32 | 10" | CVA | 910242 | CHX4.5A1104 | N | 0 | 32-E-9004 | 32-S-9014 | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910243 | 08 | 32 | 10" | CVA | 910243 | CHX4.5A1104 | N | 0 | 32-S-9014 | 910244 | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910244 | 08 | 32 | 2-1/2" | CVA | 910244 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001A | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910244 | 08 | 32 | 5" | CVA | 910244 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001A | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910245 | 08 | 32 | 2-1/2" | CVA | 910245 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001B | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910245 | 08 | 32 | 5" | CVA | 910245 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001B | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910246 | 08 | 32 | 2-1/2" | CVA | 910246 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001C | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910246 | 08 | 32 | 5" | CVA | 910246 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001C | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910247 | 08 | 32 | 2-1/2" | CVA | 910247 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001D | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910247 | 08 | 32 | 5" | CVA | 910247 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001D | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910248 | 08 | 32 | 2-1/2" | CVA | 910248 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001E | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910248 | 08 | 32 | 5" | CVA | 910248 | CHX4.5A1104 | N | 0 | 910243 | 32-H-9001E | -0.5 / 1.03 | 0 / 110 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910249 | 08 | 32 | 10" | CVA | 910249 | CHX4.5A1104 | N | 0 | 910242 | 910243 | -0.5 / 1.03 | 0 / 100 | 0.45 | 50 | NA | 0.45 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.105 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-082-06 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910250 | 08 | 32 | 10" | CVA | 910250 | CHX8.0A1104 | P | 100 | 32-C-9001A | 32-E-9001A | -0.5 / 2.8 | 0 / 110 | 1.47 / 1.76 | 50 | NA | 1.76 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910250 | 08 | 32 | 8" | CVA | 910250 | CHX8.0A1104 | P | 75 | 32-C-9001A | 32-E-9001A | -0.5 / 2.8 | 0 / 300 | 1.47 / 1.76 | 150 / 169 | NA | 1.76 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910251 | 08 | 32 | 10" | CVA | 910251 | CHX4.5A1104 | P | 100 | 32-E-9001A | 32-S-9009A | -0.5 / 2.8 | 0 / 110 | 1.4 / 1.7 | 70 | NA | 1.7 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910251 | 08 | 32 | 8" | CVA | 910251 | CHX4.5A1104 | P | 75 | 32-E-9001A | 32-S-9009A | -0.5 / 2.8 | 0 / 110 | 1.4 / 1.7 | 70 | NA | 1.7 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910252 | 08 | 32 | 10" | CVA | 910252 | CHX4.5A1104 | P | 100 | 32-S-9009A | SP-06-191B0-02 | -0.5 / 2.8 | 0 / 110 | 1.32 / 1.55 | 50 | NA | 1.55 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910252 | 08 | 32 | 8" | CVA | 910252 | CHX4.5A1104 | P | 75 | 32-S-9009A | SP-06-191B0-02 | -0.5 / 2.8 | 0 / 110 | 1.32 / 1.55 | 50 | NA | 1.55 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910253 | 08 | 32 | 10" | CVA | 910253 | CHX8.0A1104 | P | 100 | 930250 | 910256 | -0.5 / 2.8 | 0 / 250 | 1.47 / 1.76 | 150 / 169 | NA | 1.76 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910254 | 08 | 32 | 10" | CVA | 910254 | CHX8.0A1104 | P | 100 | 32-C-9001C | 930253 | -0.5 / 2.8 | 0 / 250 | 1.47 / 1.76 | 150 / 169 | NA | 1.76 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910255 | 08 | 32 | 10" | CVA | 910255 | CHX8.0A1104 | P | 100 | 910254 | 90F308 | -0.5 / 2.8 | 0 / 250 | 1.47 / 1.76 | 150 / 169 | NA | 1.76 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910256 | 08 | 32 | 12" | CVA | 910256 | CHX8.0A1104 | P | 100 | 32-C-9001B | 32-E-9001B | -0.5 / 2.8 | 0 / 250 | 0.89 / 1.0 | 125 / 134 | NA | 1.0 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910256 | 08 | 32 | 10" | CVA | 910256 | CHX8.0A1104 | P | 100 | 32-C-9001B | 32-E-9001B | -0.5 / 2.8 | 0 / 250 | 0.89 / 1.0 | 125 / 134 | NA | 1.0 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | NA | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910257 | 08 | 32 | 10" | CVA | 910257 | CHX4.5A1104 | P | 100 | 32-E-9001B | 32-S-9009B | -0.5 / 2.8 | 0 / 110 | 0.83 / 0.94 | 70 | NA | 0.94 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910258 | 08 | 32 | 10" | CVA | 910258 | CHX4.5A1104 | N | 0 | 32-S-9009B | SP-06-191B0-04 | -0.5 / 2.8 | 0 / 110 | 0.77 / 0.85 | 50 | NA | 0.85 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910258 | 08 | 32 | 9" | CVA | 910258 | CHX4.5A1104 | N | 0 | 32-S-9009B | SP-06-191B0-04 | -0.5 / 2.8 | 0 / 110 | 0.77 / 0.85 | 50 | NA | 0.85 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910260 | 08 | 32 | 20" | VG | 910260 | CHX1.0A1104 | P | 100 | 910261 | RTO | -0.5 / 0.1 | 0 / 110 | 0.02 / 0.05 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-09_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910261 | 08 | 32 | 20" | VG | 910261 | CHX1.0A1104 | P | 100 | 32-H-9001A | 910260 | -0.5 / 0.1 | 0 / 110 | 0.02 / 0.05 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-09_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910262 | 08 | 32 | 20" | VG | 910262 | CHX1.0A1104 | P | 100 | 32-H-9001B | 910260 | -0.5 / 0.1 | 0 / 110 | 0.02 / 0.05 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-09_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910263 | 08 | 32 | 20" | VG | 910263 | CHX1.0A1104 | P | 100 | 32-H-9001C | 910260 | -0.5 / 0.1 | 0 / 110 | 0.02 / 0.05 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-09_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910264 | 08 | 32 | 20" | VG | 910264 | CHX1.0A1104 | P | 100 | 32-H-9001D | 910260 | -0.5 / 0.1 | 0 / 110 | 0.02 / 0.05 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.71 | 2 | NA | NA | N | 5 | N | 32-P-082-09_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910264 | 08 | 32 | 10" | CVA | 910264 | CHX4.5A1104 | P | 100 | 910251 | 910252 | -0.5 / 2.8 | 0 / 110 | 1.4 / 1.7 | 70 | NA | 1.7 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA910265 | 08 | 32 | 10" | CVA | 910265 | CHX4.5A1104 | P | 100 | 910257 | 910258 | -0.5 / 2.8 | 0 / 110 | 0.83 / 0.94 | 70 | NA | 0.94 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.73 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910265 | 08 | 32 | 20" | VG | 910265 | CHX1.0A1104 | P | 100 | 32-H-9001E | 910260 | -0.5 / 0.1 | 0 / 110 | 0.02 / 0.05 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.71 | 2 | NA | NA | N | 5 | N | 32-P-082-09_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910266 | 08 | 32 | 4" | VG | 910266 | CHX4.5A1104 | P | 50 | 32-V-9001A | 32-H-9001A | -0.5 / 0.1 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910267 | 08 | 32 | 4" | VG | 910267 | CHX4.5A1104 | P | 50 | 32-V-9001B | 32-H-9001B | -0.5 / 0.1 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910268 | 08 | 32 | 4" | VG | 910268 | CHX4.5A1104 | P | 50 | 32-V-9001C | 32-H-9001C | -0.5 / 0.1 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.70 | 2 | NA | NA | N | 5 | N | 32-P-082-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910269 | 08 | 32 | 4" | VG | 910269 | CHX4.5A1104 | P | 50 | 32-V-9001D | 32-H-9001D | -0.5 / 0.1 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.71 | 2 | NA | NA | N | 5 | N | 32-P-082-04 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG910270 | 08 | 32 | 4" | VG | 910270 | CHX4.5A1104 | P | 50 | 32-V-9001E | 32-H-9001E | -0.5 / 0.1 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.71 | 2 | NA | NA | N | 5 | N | 32-P-082-05 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910271 | 08 | 32 | 9" | P | 910271 | CHX4.5A4500 | P | 100 | SP-06-191A0-06 | SP-06-191A0-05 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910272 | 08 | 32 | 9" | P | 910272 | CHX4.5A4500 | P | 100 | SP-06-191A0-05 | SP-06-191A0-04 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910273 | 08 | 32 | 9" | P | 910273 | CHX4.5A4500 | P | 100 | SP-06-191A0-04 | 32-H-9001E | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910273 | 08 | 32 | 10" | P | 910273 | CHX4.5A4500 | P | 100 | SP-06-191A0-04 | 32-H-9001E | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910274 | 08 | 32 | 8" | P | 910274 | CHX4.5A4500 | P | 75 | SP-06-191A0-03 | SP-06-191A0-02 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910275 | 08 | 32 | 8" | P | 910275 | CHX4.5A4500 | P | 75 | SP-06-191A0-02 | SP-06-191A0-01 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910276 | 08 | 32 | 8" | P | 910276 | CHX4.5A4500 | P | 75 | SP-06-191A0-01 | 32-D-9003 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910276 | 08 | 32 | 9" | P | 910276 | CHX4.5A4500 | P | 100 | SP-06-191A0-01 | 32-D-9003 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910276 | 08 | 32 | 10" | P | 910276 | CHX4.5A4500 | P | 100 | SP-06-191A0-01 | 32-D-9003 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.70 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910277 | 08 | 32 | 9" | P | 910277 | CHX4.5A4500 | P | 100 | SP-06-191B0-04 | SP-06-191B0-03 | -0.5 / 2.8 | 0 / 100 | 0.77 / 0.85 | 60 / 80 | NA | 0.85 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-01_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910278 | 08 | 32 | 8" | P | 910278 | CHX4.5A4500 | P | 75 | SP-06-191B0-02 | SP-06-191B0-01 | -0.5 / 2.8 | 0 / 100 | 1.32 / 1.55 | 60 / 80 | NA | 1.55 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.71 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-083-02_B |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910316 | 08 | 32 | 7" | P | 910316 | CHX4.5A4500 | P | 75 | 32-XV-9405 | 53-H3001B | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P910316 | 08 | 32 | 8" | P | 910316 | CHX4.5A4500 | P | 75 | 32-XV-9405 | 53-H3001B | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940300 | 08 | 32 | 10" | CVA | 940300 | CHX8.0A1104 | P | 100 | 32-C-9002A | 32-E-9002 | -0.5 / 1.03 | 0 / 170 | 0.65 / 0.74 | 97 / 106 | NA | 0.74 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940300 | 08 | 32 | 8" | CVA | 940300 | CHX8.0A1104 | P | 75 | 32-C-9002A | 32-E-9002 | -0.5 / 1.03 | 0 / 170 | 0.65 / 0.74 | 97 / 106 | NA | 0.74 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940301 | 08 | 32 | 10" | CVA | 940301 | CHX8.0A1104 | P | 100 | 32-C-9002B | 940300 | -0.5 / 1.03 | 0 / 170 | 0.65 / 0.74 | 97 / 106 | NA | 0.74 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940301 | 08 | 32 | 8" | CVA | 940301 | CHX8.0A1104 | P | 75 | 32-C-9002B | 940300 | -0.5 / 1.03 | 0 / 170 | 0.65 / 0.74 | 97 / 106 | NA | 0.74 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940302 | 08 | 32 | 8" | CVA | 940302 | CHX4.5A1104 | N | 0 | 32-E-9002 | 32-S-9010 | -0.5 / 1.03 | 0 / 110 | 0.58 / 0.68 | 50 | NA | 0.68 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940303 | 08 | 32 | 7" | CVA | 940303 | CHX4.5A1104 | N | 0 | 32-S-9010 | SP-06-19400-01 | -0.5 / 1.03 | 0 / 110 | 0.5 / 0.59 | 50 | NA | 0.59 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940303 | 08 | 32 | 8" | CVA | 940303 | CHX4.5A1104 | N | 0 | 32-S-9010 | SP-06-19400-01 | -0.5 / 1.03 | 0 / 110 | 0.5 / 0.59 | 50 | NA | 0.59 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG940304 | 08 | 32 | 20" | VG | 940304 | CHX1.0A1104 | N | 0 | 32-D-9003 | 32-S-9012 | -0.5 / 0.2 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG940304 | 08 | 32 | 16" | VG | 940304 | CHX1.0A1104 | N | 0 | 32-D-9003 | 32-S-9012 | -0.5 / 0.2 | 0 / 110 | 0.05 / 0.1 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VG940305 | 08 | 32 | 2-1/2" | VG | 940305 | CHX4.5A1104 | P | 50 | 32-V-9003 | 940313 | -0.5 / 0.2 | 0 / 100 | 0.1 / 0.15 | 60 / 80 | NA | NA | NA | V | Process Vent | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP940306 | 08 | 32 | 16" | PP | 940306 | CHX1.0A1004 | P | 100 | 32-D-9003 | 32-V-9003 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940307 | 08 | 32 | 16" | P | 940307 | CHX4.5A4500 | P | 100 | 32-V-9003 | 32-XV-9404 | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940307 | 08 | 32 | 12" | P | 940307 | CHX4.5A4500 | P | 100 | 32-V-9003 | 53-H3201W | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940308 | 08 | 32 | 12" | P | 940308 | CHX4.5A4500 | P | 100 | 32-XV-9404 | SP-06-19400-01 | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP940309 | 08 | 32 | 12" | PP | 940309 | CHX1.0A1004 | P | 100 | 32-S-9012 | 32-V-9002 | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
PP940310 | 08 | 32 | 12" | PP | 940310 | CHX1.0A1004 | P | 100 | 32-V-9002 | Collecting Box | -0.5 / 0.2 | 0 / 110 | 0 / 0.1 | 60 / 80 | NA | NA | NA | V | Polymer | S | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VA940311 | 08 | 32 | 20" | VA | 940311 | CHX1.0A1104 | N | 0 | 32-S-9012 | ATM | -0.5 / 0.1 | 0 / 110 | 0.01 / 0.02 | 60 / 80 | NA | NA | NA | V | Vent to ATM | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940312 | 08 | 32 | 20" | CVA | 940312 | CHX4.5A1104 | N | 0 | 32-S-9100 | 32-C-9100 | -0.5 / 0.1 | 0 / 110 | -0.01 / -0.05 | 0 / 31 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940312 | 08 | 32 | 10" | CVA | 940312 | CHX4.5A1104 | N | 0 | 32-S-9100 | 32-C-9100 | -0.5 / 0.1 | 0 / 110 | -0.01 / -0.05 | 0 / 31 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940313 | 08 | 32 | 12" | CVA | 940313 | CHX4.5A1104 | N | 0 | 32-C-9100 | 32-D-9003 | -0.5 / 0,2 | 0 / 110 | 0.1 / 0.106 | 12 / 43 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940313 | 08 | 32 | 10" | CVA | 940313 | CHX4.5A1104 | N | 0 | 32-C-9100 | 32-D-9003 | -0.5 / 0,2 | 0 / 110 | 0.1 / 0.106 | 12 / 43 | NA | NA | NA | V | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | NA | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940315 | 08 | 32 | 7" | P | 940315 | CHX4.5A4500 | P | 75 | SP-06-19400-01 | 53-H3201E | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940317 | 08 | 32 | 7" | P | 940317 | CHX4.5A4500 | P | 75 | 32-XV-9406 | 53-H3201S | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940318 | 08 | 32 | 7" | P | 940318 | CHX4.5A4500 | P | 75 | 32-XV-9408 | 53-H3201O | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940319 | 08 | 32 | 7" | P | 940319 | CHX4.5A4500 | P | 75 | 32-XV-9410 | 53-H3201J | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940320 | 08 | 32 | 7" | P | 940320 | CHX4.5A4500 | P | 75 | 32-XV-9413 | 53-H3001E | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940320 | 08 | 32 | 8" | P | 940320 | CHX4.5A4500 | P | 75 | 32-XV-9413 | 53-H3001E | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940321 | 08 | 32 | 8" | P | 940321 | CHX4.5A4500 | P | 75 | 32-XV-9412 | 53-H3201V | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940322 | 08 | 32 | 8" | P | 940322 | CHX4.5A4500 | P | 75 | 32-XV-9414 | 53-H3201R | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940323 | 08 | 32 | 8" | P | 940323 | CHX4.5A4500 | P | 75 | 32-XV-9419 | 53-H3001D | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940324 | 08 | 32 | 8" | P | 940324 | CHX4.5A4500 | P | 75 | 32-XV-9418 | 53-H3201U | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940325 | 08 | 32 | 8" | P | 940325 | CHX4.5A4500 | P | 75 | 32-XV-9420 | 53-H3201Q | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940326 | 08 | 32 | 8" | P | 940326 | CHX4.5A4500 | P | 75 | 32-XV-9425 | 53-H3001C | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940327 | 08 | 32 | 8" | P | 940327 | CHX4.5A4500 | P | 75 | 32-XV-9424 | 53-H3201T | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940328 | 08 | 32 | 8" | P | 940328 | CHX4.5A4500 | P | 75 | 32-XV-9426 | 53-H3201P | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940329 | 08 | 32 | 8" | P | 940329 | CHX4.5A4500 | P | 75 | 32-XV-9430 | 53-H3001B | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940330 | 08 | 32 | 7" | P | 940330 | CHX4.5A4500 | P | 75 | 32-XV-9407 | 53-H3201K | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940330 | 08 | 32 | 8" | P | 940330 | CHX4.5A4500 | P | 75 | 32-XV-9407 | 53-H3201K | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940331 | 08 | 32 | 8" | P | 940331 | CHX4.5A4500 | PP | 75 | 32-XV-9415 | 53-H3201N | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940332 | 08 | 32 | 8" | P | 940332 | CHX4.5A4500 | PP | 75 | 32-XV-9421 | 53-H3201M | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940333 | 08 | 32 | 8" | P | 940333 | CHX4.5A4500 | PP | 75 | 32-XV-9427 | 53-H3201L | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940334 | 08 | 32 | 7" | P | 940334 | CHX4.5A4500 | PP | 75 | 32-XV-9409 | 53-H3201F | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940334 | 08 | 32 | 8" | P | 940334 | CHX4.5A4500 | PP | 75 | 32-XV-9409 | 53-H3201F | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940335 | 08 | 32 | 8" | P | 940335 | CHX4.5A4500 | PP | 75 | 32-XV-9416 | 53-H3201I | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940336 | 08 | 32 | 8" | P | 940336 | CHX4.5A4500 | PP | 75 | 32-XV-9422 | 53-H3201H | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940337 | 08 | 32 | 8" | P | 940337 | CHX4.5A4500 | PP | 75 | 32-XV-9428 | 53-H3201G | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940338 | 08 | 32 | 7" | P | 940338 | CHX4.5A4500 | PP | 75 | 32-XV-9411 | 53-H3201A | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940338 | 08 | 32 | 8" | P | 940338 | CHX4.5A4500 | PP | 75 | 32-XV-9411 | 53-H3201A | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940339 | 08 | 32 | 8" | P | 940339 | CHX4.5A4500 | PP | 75 | 32-XV-9417 | 53-H3201D | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940340 | 08 | 32 | 8" | P | 940340 | CHX4.5A4500 | PP | 75 | 32-XV-9423 | 53-H3201C | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
P940341 | 08 | 32 | 8" | P | 940341 | CHX4.5A4500 | PP | 75 | 32-XV-9429 | 53-H3201B | -0.5 / 1.03 | 0 / 100 | 0.5 / 0.59 | 60 / 80 | NA | 0.59 | NA | N | Polymer + Gas | GS | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-02 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
CVA940345 | 08 | 32 | 8" | CVA | 940345 | CHX4.5A1104 | N | 0 | 940302 | 940303 | -0.5 / 1.03 | 0 / 110 | 0.58 / 0.68 | 50 | NA | 0.68 | NA | N | Conveying Air | G | N | - | >1.5 | 0 | sh.74 | 2 | Art.4.3 | NA | N | 5 | N | 32-P-090-01 |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
N800147 | 08 | 32 | 1/2" | N | 800147 | CHX1.0A1104 | N | 0 | 32-E-8000 | SP-33-180B0-02 | -0.5 / 0.2 | 0 / 110 | 0 / 0.04 | 50 | NA | NA | NA | V | Low Pressure Nitrogen | G | N | - | >1.5 | 0 | sh.57 | 2 | NA | NA | N | 5 | N | 32-P-060-01_A |  | VT | N | N | N | - | REV03_PKG 32-PK-8001 to 9004
VA870101 | 08 | 32 | 4" | VA | 870101 | GSBI2 | N | 0 | 32-S-8700 | 3"-VA-870102-GSBI1 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870102 | 08 | 32 | 3" | VA | 870102 | GSBI1 | N | 0 | 4"-VA-870101-GSBI2 | 2-1/2"-VA-870103-GSBI1 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870103 | 08 | 32 | 2-1/2" | VA | 870103 | GSBI1 | N | 0 | 3"-VA-870102-GSBI1 | 2-1/2"-VA-870121-GSBI10 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870104 | 08 | 32 | 2-1/2" | VA | 870104 | GSBI1 | N | 0 | 2-1/2"-VA-870103-GSBI1 | SUCTION POINT 3A | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870105 | 08 | 32 | 2-1/2" | VA | 870105 | GSBI1 | N | 0 | 2-1/2"-VA-870103-GSBI1 | SUCTION POINT 6A | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870106 | 08 | 32 | 2-1/2" | VA | 870106 | GSBI1 | N | 0 | 2-1/2"-VA-870103-GSBI1 | SUCTION POINT 8A | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870107 | 08 | 32 | 2-1/2" | VA | 870107 | GSBI1 | N | 0 | 3"-VA-870102-GSBI1 | 2-1/2"-VA-870121-GSBI10 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870108 | 08 | 32 | 2-1/2" | VA | 870108 | GSBI1 | N | 0 | 2-1/2"-VA-870107-GSBI1 | SUCTION POINT 3B | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870109 | 08 | 32 | 2-1/2" | VA | 870109 | GSBI1 | N | 0 | 2-1/2"-VA-870107-GSBI1 | SUCTION POINT 4B | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870110 | 08 | 32 | 2-1/2" | VA | 870110 | GSBI1 | N | 0 | 2-1/2"-VA-870107-GSBI1 | SUCTION POINT 7B | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870111 | 08 | 32 | 2-1/2" | VA | 870111 | GSBI1 | N | 0 | 2-1/2"-VA-870107-GSBI1 | SUCTION POINT 10B | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870112 | 08 | 32 | 4" | VA | 870112 | GSBI3 | N | 0 | 32-S-8700 | 32-S-8701 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870113 | 08 | 32 | 6" | VA | 870113 | GSBI3 | N | 0 | 32-S-8701 | 32-C-8700 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870115 | 08 | 32 | 2-1/2" | VA | 870115 | GSBI1 | N | 0 | 2-1/2"-VA-870103-GSBI1 | SUCTION POINT 4A | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870120 | 08 | 32 | 8" | VA | 870120 | GSBI3 | N | 0 | 32-C-8700 | ATM | -0,5/0 | 0/60 | 0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | >1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870121 | 08 | 32 | 2-1/2" | VA | 870121 | GSBI10 | N | 0 | 2-1/2"-VA-870103-GSBI1 | 32-XV-8712 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA870122 | 08 | 32 | 2-1/2" | VA | 870122 | GSBI10 | N | 0 | 2-1/2"-VA-870107-GSBI1 | 32-XV-8713 | -0,5/0 | 0/60 | -0,3/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | GS | N | - | <1.5 | 0 | Sh.66 | 2 | Art.4.3 | NA | N | NA | N | 32-P-070-12 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810100 | 08 | 32 | 2-1/2" | VA | 810100 | GSBI10 | N | 0 | 2-1/2"-VA-810109-GSBI10 | 3"-VA-810102-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.64 | 2 | Art.4.3 | NA | N | NA | N | 32-P-062-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810101 | 08 | 32 | 4" | VA | 810101 | GSBI10 | N | 0 | 3"-VA-810102-GSBI10 | 6"-VA-810103-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.60A | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810102 | 08 | 32 | 3" | VA | 810102 | GSBI10 | N | 0 | 2-1/2"-VA-810100-GSBI10 | 4"-VA-810101-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.60A | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810103 | 08 | 32 | 6" | VA | 810103 | GSBI10 | N | 0 | 4"-VA-810101-GSBI10 | 32-C-8100 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.62 | 2 | Art.4.3 | NA | N | NA | N | 32-P-063-01 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810104 | 08 | 32 | 2-1/2" | VA | 810104 | GSBI10 | N | 0 | TP 075 | 6"-VA-810103-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.59 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-01 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810106 | 08 | 32 | 2-1/2" | VA | 810106 | GSBI10 | N | 0 | TP 085 | 2-1/2"-VA-810100-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.64 | 2 | Art.4.3 | NA | N | NA | N | 32-P-062-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810108 | 08 | 32 | 2-1/2" | VA | 810108 | GSBI10 | N | 0 | TP 065 | 6"-VA-810103-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.61 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810109 | 08 | 32 | 2-1/2" | VA | 810109 | GSBI10 | N | 0 | TP 055 | 2-1/2"-VA-810100-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.61 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810110 | 08 | 32 | 2-1/2" | VA | 810110 | GSBI10 | N | 0 | TP 071 | 6"-VA-810103-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.61 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810111 | 08 | 32 | 2-1/2" | VA | 810111 | GSBI10 | N | 0 | TP 025 | 4"-VA-810101-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.60A | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810112 | 08 | 32 | 2-1/2" | VA | 810112 | GSBI10 | N | 0 | TP 035 | 3"-VA-810102-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.60 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810113 | 08 | 32 | 2-1/2" | VA | 810113 | GSBI10 | N | 0 | TP 045 | 4"-VA-810101-GSBI10 | -0,05/0 | 0/60 | -0,045/0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.60 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
VA810114 | 08 | 32 | 8" | VA | 810114 | GSBI10 | N | 0 | 32-C-8100 | TO SAFE LOCATION | -0,05/0 | 0/60 | 0 | 0-31 | - | NA | NA | NA | VENT TO ATMOSPHERE | G | N | - | <1.5 | 0 | Sh.60 | 2 | Art.4.3 | NA | N | NA | N | 32-P-061-02 |  | NA | N | H280 | N | - | REV2_PKG 32-PK-8100 32-PK-8700
PP810304 | 08 | 32 | 14" | PP | 810304 | CHX1.0A6844 | N | 0 | Outlet of 32-ZF-8100A | 14"-PP-810305-CHX1.0A6844 | (-)0.05/(+)0.2 | 100 | 0.1/0.15 | 70/80 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | Sh.59 | 2 | NA | NA | NA | NA | N | 32-P-061-01 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 110 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
PP810305 | 08 | 32 | 14" | PP | 810305 | CHX1.0A6844 | N | 0 | Outlet of 32-ZF-8100B | Inlet of 32-Z-8110 | (-)0.05/(+)0.2 | 100 | 0.1/0.15 | 70/80 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.59 | 2 | NA | NA | NA | NA | N | 32-P-061-01 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 110 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810300 | 08 | 32 | 2" | N | 810300 | 1CS2 | N | 0 | 32-TP-001 | 32-TP-005 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.58 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-060-01 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810301 | 08 | 32 | 2" | N | 810301 | 1CS2 | N | 0 | 32-TP-003 | 32-TP-004 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.58 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-060-01 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VA810101 | 08 | 32 | 8" | VA | 810101 | CHX1.0A6844 | N | 0 | Vent Nozzle B of 32-S-8120 | Inlet of 32-C-8120 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 0-31 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.60A | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VG810102 | 08 | 32 | 6" | VG | 810102 | CHX1.0A6844 | N | 0 | Vent Outlet Nozzle V2 of 32-Z-8120 | Inlet Nozzle A of 32-S-8120 | (-)0.03/(+)0.1 | 40 | 1.006 | 40 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.60A | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810104 | 08 | 32 | 12" | SA | 810104 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8161 | Inlet Nozzle P1 of 32-D-8101 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810345 | 08 | 32 | 6" | SA | 810345 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8150 | Inlet of 32-VM-8155 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810334 | 08 | 32 | 6" | SA | 810334 | CHX1.0A6844 | N | 0 | Outlet Nozzle N3 of 32-VM-8155 | 32-TP-024 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810308 | 08 | 32 | 6" | SA | 810308 | CHX1.0A6844 | N | 0 | Outlet Nozzle N2 of 32-VM-8155 | Inlet Nozzle A of 32-Z-8101 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810339 | 08 | 32 | 6" | SA | 810339 | CHX1.0A6844 | N | 0 | Outlet of 32-Z-8101 | 32-TP-028 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.60A | 2 | NA | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
IA810103 | 08 | 32 | 3/4" | IA | 810103 | 1CS2 | N | 0 | 32-TP-021 | Massager of 32-Z-8111 | 10 | 60 | 6.8 | 40 | 8.92 | 1 | 15.7 | H | Instrument Air | G | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-070-09 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810105 | 08 | 32 | 3/4" | N | 810105 | 1CS2 | N | 0 | 32-TP-023 | Bin Aeration of 32-D-8101 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810310 | 08 | 32 | 1/2" | N | 810310 | 1CS2 | N | 0 | 32-TP-027 | Blanketing/Fluidizing 32-Z-8101 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.60A | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VA810107 | 08 | 32 | 8" | VA | 810107 | CHX1.0A6844 | N | 0 | Vent Nozzle B of 32-S-8121 | Inlet of 32-C-8121 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 0-31 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.60 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VG810108 | 08 | 32 | 6" | VG | 810108 | CHX1.0A6844 | N | 0 | Vent Outlet Nozzle V2 of 32-Z-8121 | Inlet Nozzle A of 32-S-8121 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 40 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.60 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810110 | 08 | 32 | 12" | SA | 810110 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8162 | Inlet Nozzle P1 of 32-D-8102 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810346 | 08 | 32 | 6" | SA | 810346 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8151 | Inlet of 32-VM-8156 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810335 | 08 | 32 | 6" | SA | 810335 | CHX1.0A6844 | N | 0 | Outlet Nozzle N3 of 32-VM-8156 | 32-TP-034 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810311 | 08 | 32 | 6" | SA | 810311 | CHX1.0A6844 | N | 0 | Outlet Nozzle N2 of 32-VM-8156 | Inlet Nozzle A of 32-Z-8102 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810340 | 08 | 32 | 6" | SA | 810340 | CHX1.0A6844 | N | 0 | Outlet of 32-Z-8102 | 32-TP-038 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | NA | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
IA810109 | 08 | 32 | 3/4" | IA | 810109 | 1CS2 | N | 0 | 32-TP-031 | Massager of 32-Z-8112 | 10 | 60 | 6.8 | 40 | 8.92 | 1 | 15.7 | H | Instrument Air | G | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-070-09 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810111 | 08 | 32 | 3/4" | N | 810111 | 1CS2 | N | 0 | 32-TP-033 | Bin Aeration of 32-D-8102 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810313 | 08 | 32 | 1/2" | N | 810313 | 1CS2 | N | 0 | 32-TP-037 | Blanketing/Fluidizing 32-Z-8102 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VA810113 | 08 | 32 | 8" | VA | 810113 | CHX1.0A6844 | N | 0 | Vent Nozzle B of 32-S-8122 | Inlet of 32-C-8122 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 0-31 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.60 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VG810114 | 08 | 32 | 6" | VG | 810114 | CHX1.0A6844 | N | 0 | Vent Outlet Nozzle V2 of 32-Z-8122 | Inlet Nozzle A of 32-S-8122 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 40 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.60 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810116 | 08 | 32 | 12" | SA | 810116 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8163 | Inlet Nozzle P1 of 32-D-8103 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810347 | 08 | 32 | 6" | SA | 810347 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8152 | Inlet of 32-VM-8157 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810336 | 08 | 32 | 6" | SA | 810336 | CHX1.0A6844 | N | 0 | Outlet Nozzle N3 of 32-VM-8157 | 32-TP-044 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810314 | 08 | 32 | 6" | SA | 810314 | CHX1.0A6844 | N | 0 | Outlet Nozzle N2 of 32-VM-8157 | Inlet Nozzle A of 32-Z-8103 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810341 | 08 | 32 | 6" | SA | 810341 | CHX1.0A6844 | N | 0 | Outlet of 32-Z-8103 | 32-TP-048 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.60 | 2 | NA | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
IA810115 | 08 | 32 | 3/4" | IA | 810115 | 1CS2 | N | 0 | 32-TP-041 | Massager of 32-Z-8113 | 10 | 60 | 6.8 | 40 | 8.92 | 1 | 15.7 | H | Instrument Air | G | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-070-09 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810117 | 08 | 32 | 3/4" | N | 810117 | 1CS2 | N | 0 | 32-TP-043 | Bin Aeration of 32-D-8103 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810316 | 08 | 32 | 1/2" | N | 810316 | 1CS2 | N | 0 | 32-TP-047 | Blanketing/Fluidizing 32-Z-8103 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.60 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VA810119 | 08 | 32 | 8" | VA | 810119 | CHX1.0A6844 | N | 0 | Vent Nozzle B of 32-S-8123 | Inlet of 32-C-8123 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 0-31 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VG810120 | 08 | 32 | 6" | VG | 810120 | CHX1.0A6844 | N | 0 | Vent Outlet Nozzle V2 of 32-Z-8123 | Inlet Nozzle A of 32-S-8123 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 40 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810122 | 08 | 32 | 12" | SA | 810122 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8164 | Inlet Nozzle P1 of 32-D-8104 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810348 | 08 | 32 | 6" | SA | 810348 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8153 | Inlet of 32-VM-8158 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810337 | 08 | 32 | 6" | SA | 810337 | CHX1.0A6844 | N | 0 | Outlet Nozzle N3 of 32-VM-8158 | 32-TP-054 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810317 | 08 | 32 | 6" | SA | 810317 | CHX1.0A6844 | N | 0 | Outlet Nozzle N2 of 32-VM-8158 | Inlet Nozzle A of 32-Z-8104 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810342 | 08 | 32 | 6" | SA | 810342 | CHX1.0A6844 | N | 0 | Outlet of 32-Z-8104 | 32-TP-058 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
IA810121 | 08 | 32 | 3/4" | IA | 810121 | 1CS2 | N | 0 | 32-TP-051 | Massager of 32-Z-8114 | 10 | 60 | 6.8 | 40 | 8.92 | 1 | 15.7 | H | Instrument Air | G | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-070-09 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810123 | 08 | 32 | 3/4" | N | 810123 | 1CS2 | N | 0 | 32-TP-053 | Bin Aeration of 32-D-8104 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810319 | 08 | 32 | 1/2" | N | 810319 | 1CS2 | N | 0 | 32-TP-057 | Blanketing/Fluidizing 32-Z-8104 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VA810125 | 08 | 32 | 8" | VA | 810125 | CHX1.0A6844 | N | 0 | Vent Nozzle B of 32-S-8124 | Inlet of 32-C-8124 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 0-31 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
VG810126 | 08 | 32 | 6" | VG | 810126 | CHX1.0A6844 | N | 0 | Vent Outlet Nozzle V2 of 32-Z-8124 | Inlet Nozzle A of 32-S-8124 | (-)0.03/(+)0.1 | 40 | (-)0.03 | 40 | 225-920 | 0 | 8 | N | PP dust with Nitrogen | GS | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810128 | 08 | 32 | 12" | SA | 810128 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8165 | Inlet Nozzle P1 of 32-D-8105 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810349 | 08 | 32 | 6" | SA | 810349 | CHX1.0A6844 | N | 0 | Outlet of 32-VM-8154 | Inlet of 32-VM-8159 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810338 | 08 | 32 | 6" | SA | 810338 | CHX1.0A6844 | N | 0 | Outlet Nozzle N3 of 32-VM-8159 | 32-TP-064 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810320 | 08 | 32 | 6" | SA | 810320 | CHX1.0A6844 | N | 0 | Outlet Nozzle N2 of 32-VM-8159 | Inlet Nozzle A of 32-Z-8105 | 1.5 | 60 | 1.006 | 0-40 | 225-920 | 0 | 8 | H | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810323 | 08 | 32 | 6" | SA | 810323 | CHX1.0A6844 | N | 0 | Outlet of 32-Z-8105 | Inlet of 6"x8" Expander Below 32-Z-8105 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
SA810324 | 08 | 32 | 8" | SA | 810324 | CHX1.0A6844 | N | 0 | Outlet of 32-V-8105 | To TP-069 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 225-920 | 0 | 8 | N | PP Additives | S | NA | NA | <1.5 | - | sh.61 | 2 | NA | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 200 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
IA810127 | 08 | 32 | 3/4" | IA | 810127 | 1CS2 | N | 0 | 32-TP-061 | Massager of 32-Z-8115 | 10 | 60 | 6.8 | 40 | 8.92 | 1 | 15.7 | H | Instrument Air | G | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-070-09 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810129 | 08 | 32 | 3/4" | N | 810129 | 1CS2 | N | 0 | 32-TP-063 | Bin Aeration of 32-D-8105 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-02 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810322 | 08 | 32 | 1/2" | N | 810322 | 1CS2 | N | 0 | 32-TP-067 | Blanketing/Fluidizing 32-Z-8105 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.61 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-03 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
T810325 | 08 | 32 | 8" | T | 810325 | CHX1.0A6844 | N | 0 | Oulet of 32-XV-8117 | Inlet of 32-Z-8106 | 1.5 | 60 | 1.006 | 0-40 | 128-320 | 0 | 8 | H | Talc | S | NA | NA | <1.5 | - | sh.62 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-04 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
T810329 | 08 | 32 | 8" | T | 810329 | CHX1.0A6844 | N | 0 | Outlet of 32-Z-8106 | Inlet of Expander 8"x10" | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 128-320 | 0 | 8 | N | Talc | S | NA | NA | <1.5 | - | sh.62 | 2 | NA | NA | NA | NA | N | 32-P-061-04 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
T810330 | 08 | 32 | 10" | T | 810330 | CHX1.0A6844 | N | 0 | Outlet of 32-V-8106 | To TP-075 | (-)0.005/(+)0.05 | 60 | 0.03 | 0-31 | 128-320 | 0 | 8 | N | Talc | S | NA | NA | <1.5 | - | sh.62 | 2 | NA | NA | NA | NA | N | 32-P-061-04 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
N810328 | 08 | 32 | 1/2" | N | 810328 | 1CS2 | N | 0 | 32-TP-073 | Blanketing/Fluidizing 32-Z-8106 | 12 | 80 | 6.1 | 0-31 | 8.09 | 1 | 15.7 | H | Nitrogen | G | NA | NA | <1.5 | - | sh.62 | 2 | Art.4.3 | NA | NA | NA | N | 32-P-061-04 | - | See doc. 4274-FY-VD-FW10070000000GEN001 | N | 000 | N | - | REV04_PKG 32-PK-8101 32-PK-8102
IA890001 | 08 | 32 | 1/2" | IA | 890001 | HA150A01 | N | 0 | CL-8900 | CL-8900 | 10 | 60 | 6.80 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
IA890002 | 08 | 32 | 1/2" | IA | 890002 | HA150A01 | N | 0 | CL-8900 | CL-8900 | 10 | 60 | 6.80 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
DW890613 | 08 | 32 | 1/2" | DW | 890613 | HB150A01 | N | 0 | CPN-A105 | CPN-A105 | 9 | 50 | 6.50 | 35 | 997 | 0 | 10 | H | Deminaralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
N890001 | 08 | 32 | 1/2" | N | 890001 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890002 | 08 | 32 | 1/2" | N | 890002 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68R | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890003 | 08 | 32 | 1/2" | N | 890003 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890004 | 08 | 32 | 1/2" | N | 890004 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890005 | 08 | 32 | 1/2" | N | 890005 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68R | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890006 | 08 | 32 | 1/2" | N | 890006 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68R | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890007 | 08 | 32 | 1/2" | N | 890007 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890009 | 08 | 32 | 1/2" | N | 890009 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
N890010 | 08 | 32 | 1/2" | N | 890010 | HC150A01 | N | 0 | CPN-A203A | CPN-A203A | 12 | 80 | 6.00 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | <1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
LO890001 | 08 | 32 | 5" | LO | 890001 | HC150A01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 2.5 | 46 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890002 | 08 | 32 | 1/2" | LO | 890002 | HC010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890003 | 08 | 32 | 6" | LO | 890003 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890004 | 08 | 32 | 3" | LO | 890004 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890005 | 08 | 32 | 6" | LO | 890005 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 2.5 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890006 | 08 | 32 | 4" | LO | 890006 | BA010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 2.5 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890007 | 08 | 32 | 3" | LO | 890007 | BA010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890008 | 08 | 32 | 6" | LO | 890008 | BA010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWR890009 | 08 | 32 | 4" | CWR | 890009 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 7.5 | 120 | 3.5 | 37 | 997 | 0 | 12 | H | Cooling water return | L | N | - | >1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-03 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890010 | 08 | 32 | 6" | LO | 890010 | BA010DA01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890011 | 08 | 32 | 6" | LO | 890011 | BA010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890012 | 08 | 32 | 4" | LO | 890012 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 2.5 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890013 | 08 | 32 | 4" | CWS | 890013 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 7.5 | 120 | 5.50 | 26 | 997 | 0 | 12 | H | Cooling water supply | L | N | - | >1.5 | 10 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-02 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890014 | 08 | 32 | 4" | LO | 890014 | BA150A01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 2.5 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890100 | 08 | 32 | 1-1/2" | LO | 890100 | BA010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890101 | 08 | 32 | 1-1/2" | LO | 890101 | BA010D01 | N | 0 | CPN-A204 | CPN-A204 | 10 | 80 | 0 | 68.9 | 852 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890001 | 08 | 32 | 1" | LO | 890001 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 85 | 7.7 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890002 | 08 | 32 | 2" | LO | 890002 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 85 | 7.7 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890003 | 08 | 32 | 1" | LO | 890003 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 85 | 7.7 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890004 | 08 | 32 | 2" | LO | 890004 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 85 | 7.7 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890005 | 08 | 32 | 3" | LO | 890005 | BA150A01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 0.65 | 65 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890006 | 08 | 32 | 3" | LO | 890006 | BA150A01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 0.65 | 65 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890007 | 08 | 32 | 1" | LO | 890007 | BA150A01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890008 | 08 | 32 | 1" | LO | 890008 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890009 | 08 | 32 | 1" | LO | 890009 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890010 | 08 | 32 | 1" | LO | 890010 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890011 | 08 | 32 | 1" | LO | 890011 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 85 | 7.7 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890012 | 08 | 32 | 1" | LO | 890012 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890013 | 08 | 32 | 1" | LO | 890013 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890014 | 08 | 32 | 1" | LO | 890014 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890015 | 08 | 32 | 1" | LO | 890015 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 85 | 7.7 | 59.4 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWR890016 | 08 | 32 | 1" | CWR | 890016 | BA150A01 | N | 0 | CPN-A211 | CPN-A211 | 7.5 | 120 | 3.50 | 37 | 997 | 0 | 12 | H | Cooling water return | L | N | - | >1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-03 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890017 | 08 | 32 | 1" | CWS | 890017 | BA150A01 | N | 0 | CPN-A211 | CPN-A211 | 7.5 | 120 | 5.5 | 26 | 997 | 0 | 12 | H | Cooling water supply | L | N | - | >1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-02 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWR890001 | 08 | 32 | 3" | BCWR | 890001 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890001 | 08 | 32 | 3" | BCWS | 890001 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890001 | 08 | 32 | 1/2" | IA | 890001 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890002 | 08 | 32 | 1" | BCWR | 890002 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890002 | 08 | 32 | 1" | BCWS | 890002 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890002 | 08 | 32 | 1/2" | IA | 890002 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890003 | 08 | 32 | 1" | BCWR | 890003 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890003 | 08 | 32 | 1" | BCWS | 890003 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890003 | 08 | 32 | 1/2" | IA | 890003 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890004 | 08 | 32 | 1" | BCWR | 890004 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890004 | 08 | 32 | 1" | BCWS | 890004 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890004 | 08 | 32 | 1/2" | IA | 890004 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890005 | 08 | 32 | 1" | BCWR | 890005 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890005 | 08 | 32 | 1" | BCWS | 890005 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890005 | 08 | 32 | 1/2" | IA | 890005 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890006 | 08 | 32 | 1" | BCWR | 890006 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890006 | 08 | 32 | 1" | BCWS | 890006 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890006 | 08 | 32 | 1/2" | IA | 890006 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890007 | 08 | 32 | 1" | BCWR | 890007 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890007 | 08 | 32 | 1" | BCWS | 890007 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890007 | 08 | 32 | 1/2" | IA | 890007 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890008 | 08 | 32 | 1" | BCWR | 890008 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890008 | 08 | 32 | 1" | BCWS | 890008 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IA890008 | 08 | 32 | 1/2" | IA | 890008 | HD150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 60 | 6 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
BCWR890009 | 08 | 32 | 1" | BCWR | 890009 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890009 | 08 | 32 | 1" | BCWS | 890009 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890010 | 08 | 32 | 1" | BCWS | 890010 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 6.8 | 50 | 997 | 0 | 20 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWR890102 | 08 | 32 | 1" | BCWR | 890102 | HB150A01 | N | 0 | CPN-A306 | CPN-A306 | 10 | 100 | 4.2 | 90 | 997 | 0 | 20 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68F | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HOR890005 | 08 | 32 | 3" | HOR | 890005 | CA040D01 | C | 40 | CPN-A425 | CPN-A425 | 10 | 315 | 5 | 300 | 880 | 0 | 25 | IO | Heat transfer oil | L | N | - | >1.5 | 0 | sh.84G | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890006 | 08 | 32 | 2" | HOR | 890006 | CA040D01 | C | 40 | CPN-A425 | CPN-A425 | 10 | 315 | 5 | 300 | 880 | 0 | 25 | IO | Heat transfer oil | L | N | - | >1.5 | 0 | sh.84G | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890008 | 08 | 32 | 2" | HOS | 890008 | CA040D01 | C | 50 | CPN-A425 | CPN-A425 | 10 | 315 | 5 | 300 | 880 | 0 | 25 | IO | Heat transfer oil | L | N | - | >1.5 | 0 | sh.84G | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890007 | 08 | 32 | 3" | HOS | 890007 | CA040D01 | C | 50 | CPN-A425 | CPN-A425 | 10 | 315 | 5 | 300 | 880 | 0 | 25 | IO | Heat transfer oil | L | N | - | >1.5 | 0 | sh.84G | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890301 | 08 | 32 | 3" | HOS | 890301 | CA040D01 | C | 50 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890302 | 08 | 32 | 1" | HOS | 890302 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 7.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890303 | 08 | 32 | 1/2" | HOS | 890303 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890304 | 08 | 32 | 1" | HOS | 890304 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890305 | 08 | 32 | 1" | HOS | 890305 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890306 | 08 | 32 | 2" | HOS | 890306 | CA040D01 | C | 50 | CPN-A429 | CPN-A429 | 10 | 315 | 7.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890307 | 08 | 32 | 1" | HOS | 890307 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890308 | 08 | 32 | 1-1/2" | HOS | 890308 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOS890309 | 08 | 32 | 1" | HOS | 890309 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 5.6 | 300 | 880 | 0 | 25 | IO | Heat transfer oil supply | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890401 | 08 | 32 | 3" | HOR | 890401 | CA040D01 | C | 50 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890402 | 08 | 32 | 1/2" | HOR | 890402 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68P | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890403 | 08 | 32 | 1" | HOR | 890403 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890404 | 08 | 32 | 1" | HOR | 890404 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890405 | 08 | 32 | 1" | HOR | 890405 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68H | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890407 | 08 | 32 | 1" | HOR | 890407 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HOR890408 | 08 | 32 | 1" | HOR | 890408 | CA040D01 | C | 40 | CPN-A429 | CPN-A429 | 10 | 315 | 1.2 | 300 | 880 | 0 | 25 | IO | Heat transfer oil return | L | N | - | >1.5 | 0 | sh.68I | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
IA890010 | 08 | 32 | 1/2" | IA | 890010 | HD150A01 | N | 0 | CPN-A517 | CPN-A517 | 10 | 60 | 6.8 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
IA890011 | 08 | 32 | 1/2" | IA | 890011 | HD150A01 | N | 0 | CPN-A517 | CPN-A517 | 10 | 60 | 6.8 | 40 | NA | 0 | 12 | P | Instrument Air | G | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-09 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
PW890011 | 08 | 32 | 12" | PW | 890011 | HC150A01 | N | 0 | CPN-A517 | CPN-A517 | 10 | 120 | 4.1 | 61 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890012 | 08 | 32 | 12" | PW | 890012 | HC150A01 | N | 0 | CPN-A517 | CPN-A517 | 10 | 120 | 4.1 | 61 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWR890001 | 08 | 32 | 3" | CWR | 890001 | BA150A01 | N | 0 | CPN-A601 | CPN-A601 | 7.5 | 120 | 3.5 | 37 | 997 | 0 | 12 | H | Cooling water Return | L | N | - | >1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-03 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890002 | 08 | 32 | 3" | CWS | 890002 | BA150A01 | N | 0 | CPN-A601 | CPN-A601 | 7.5 | 120 | 5.5 | 26 | 997 | 0 | 12 | H | Cooling water supply | L | N | - | >1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-02 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890003 | 08 | 32 | 3" | BCW | 890003 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890004 | 08 | 32 | 3" | BCW | 890004 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890005 | 08 | 32 | 3" | BCW | 890005 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890006 | 08 | 32 | 3" | BCW | 890006 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890007 | 08 | 32 | 3" | BCW | 890007 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890008 | 08 | 32 | 3" | BCW | 890008 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890009 | 08 | 32 | 3" | BCW | 890009 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890010 | 08 | 32 | 1" | BCW | 890010 | HC150A01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PCW890011 | 08 | 32 | 1/2" | PCW | 890011 | HC150A01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 120 | 6.00 | 65 | 997 | 0 | 15 | H | Pellet cooling water | L | N | - | >1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PCW890012 | 08 | 32 | 1/2" | PCW | 890012 | HC150A01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 120 | 6.00 | 65 | 997 | 0 | 15 | H | Pellet cooling water | L | N | - | >1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PCW890013 | 08 | 32 | 1/2" | PCW | 890013 | HC150A01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 120 | 6.00 | 65 | 997 | 0 | 15 | H | Pellet cooling water | L | N | - | >1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890014 | 08 | 32 | 3" | BCW | 890014 | BA150A01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 4.2 | 64.3 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890015 | 08 | 32 | 3" | BCW | 890015 | BA150A01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 50 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890121 | 08 | 32 | 3" | BCW | 890121 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 4.2 | 64.3 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCW890122 | 08 | 32 | 3" | BCW | 890122 | BA010D01 | N | 0 | CPN-A601 | CPN-A601 | 10 | 100 | 6.8 | 46 | 997 | 0 | 15 | H | Barrel cooling water | L | N | - | <1.5 | 10 | sh.68Q | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HO890001 | 08 | 32 | 3" | HO | 890001 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 1.2 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
N890001 | 08 | 32 | 1/4" | N | 890001 | HC010D01 | N | 0 | CPN-A602 | CPN-A602 | 12 | 80 | 6 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | >1.5 | 10 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
HO890002 | 08 | 32 | 3" | HO | 890002 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 1.2 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
N890002 | 08 | 32 | 1" | N | 890002 | CA010D01 | N | 0 | CPN-A602 | CPN-A602 | 12 | 80 | 6 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | >1.5 | 10 | sh.68R | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
HO890003 | 08 | 32 | 3" | HO | 890003 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 1.2 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
N890003 | 08 | 32 | 1/4" | N | 890003 | HC010D01 | N | 0 | CPN-A602 | CPN-A602 | 12 | 80 | 6 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | >1.5 | 10 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
HO890004 | 08 | 32 | 3" | HO | 890004 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
N890004 | 08 | 32 | 1/4" | N | 890004 | HC010D01 | N | 0 | CPN-A602 | CPN-A602 | 12 | 80 | 6 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | >1.5 | 10 | sh.68B | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-10 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
HO890005 | 08 | 32 | 3" | HO | 890005 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
N890005 | 08 | 32 | 2" | N | 890005 | CA10D01 | N | 0 | CPN-A602 | CPN-A602 | 12 | 80 | 6 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | >1.5 | 10 | sh.68R | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
HO890006 | 08 | 32 | 2-1/2" | HO | 890006 | CA010D01 | H | 90 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
N890006 | 08 | 32 | 1" | N | 890006 | CA010D01 | N | 0 | CPN-A602 | CPN-A602 | 12 | 80 | 6 | 20 | NA | 0 | 15 | N | Nitrogen | G | N | - | >1.5 | 10 | sh.68R | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H280 | N | - | REV03_PKG 32-PK-8900
HO890007 | 08 | 32 | 1" | HO | 890007 | CA010D01 | H | 80 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890008 | 08 | 32 | 2" | HO | 890008 | CA010D01 | H | 80 | CPN-A602 | CPN-A602 | 10 | 315 | 1.2 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890009 | 08 | 32 | 1" | HO | 890009 | CA010D01 | H | 80 | CPN-A602 | CPN-A602 | 10 | 315 | 5.6 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890010 | 08 | 32 | 3" | HO | 890010 | CA011D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 1.4 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890012 | 08 | 32 | 3" | HO | 890012 | CA011D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 1.4 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890013 | 08 | 32 | 3" | HO | 890013 | CA011D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 1.4 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890014 | 08 | 32 | 3" | HO | 890014 | CA011D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890015 | 08 | 32 | 2-1/2" | HO | 890015 | CA011D01 | H | 90 | CPN-A602 | CPN-A602 | 10 | 315 | 1.4 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890016 | 08 | 32 | 1" | HO | 890016 | CA011D01 | H | 80 | CPN-A602 | CPN-A602 | 10 | 315 | 5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890017 | 08 | 32 | 2" | HO | 890017 | CA011D01 | H | 80 | CPN-A602 | CPN-A602 | 10 | 315 | 8.5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890018 | 08 | 32 | 2" | HO | 890018 | CA100D01 | H | 50 | CPN-A602 | CPN-A602 | 10 | 315 | 7.6 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890021 | 08 | 32 | 1" | HO | 890021 | CA011D01 | H | 80 | CPN-A602 | CPN-A602 | 10 | 315 | 5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890123 | 08 | 32 | 1" | HO | 890123 | CA011D01 | H | 50 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890124 | 08 | 32 | 1" | HO | 890124 | CA011D01 | H | 50 | CPN-A602 | CPN-A602 | 10 | 315 | 5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890130 | 08 | 32 | 3" | HO | 890130 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890131 | 08 | 32 | 3" | HO | 890131 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5.1 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890132 | 08 | 32 | 3" | HO | 890132 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890133 | 08 | 32 | 3" | HO | 890133 | CA010D01 | H | 100 | CPN-A602 | CPN-A602 | 10 | 315 | 5 | 300 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890019 | 08 | 32 | 3/4" | HO | 890019 | CA011D01 | H | 40 | CPN-A602 | CPN-A602 | 25 | 120 | 3 | 80 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HO890020 | 08 | 32 | 3/4" | HO | 890020 | CA011D01 | H | 40 | CPN-A602 | CPN-A602 | 25 | 120 | 3 | 80 | 880 | 0 | 22.9 | IO | Heat transfer oil | L | N | - | >1.5 | 10 | sh.68R | 1 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | H360FD H304 H410 | N | - | REV03_PKG 32-PK-8900
HF890001 | 08 | 32 | 1" | HF | 890001 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890002 | 08 | 32 | 3/4" | HF | 890002 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 58 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890003 | 08 | 32 | 3/4" | HF | 890003 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890004 | 08 | 32 | 3/4" | HF | 890004 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890005 | 08 | 32 | 2" | HF | 890005 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890006 | 08 | 32 | 2" | HF | 890006 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 58 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890007 | 08 | 32 | 0.87" | HF | 890007 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890008 | 08 | 32 | 0.39" | HF | 890008 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890009 | 08 | 32 | 0.39" | HF | 890009 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890010 | 08 | 32 | 1.18" | HF | 890010 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 58 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890011 | 08 | 32 | 0.87" | HF | 890011 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 58 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890013 | 08 | 32 | 1.18" | HF | 890013 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890014 | 08 | 32 | 0.39" | HF | 890014 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890015 | 08 | 32 | 0.39" | HF | 890015 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 |  | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890016 | 08 | 32 | 2" | HF | 890016 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 58 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890017 | 08 | 32 | 0.73" | HF | 890017 | BB350A01 | N | 0 | CPN-A606 | CPN-A606 | 300 | 80 | 280 | 58 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HFR890602 | 08 | 32 | 3" | HFR | 890602 | CA040D02 | N | 0 | CPN-A609 | CPN-A609 | 300 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil return | L | N | - | <1.5 | 0 | sh.68I | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HFS890601 | 08 | 32 | 2" | HFS | 890601 | CA250D01 | N | 0 | CPN-A609 | CPN-A609 | 330 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic unit supply | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890603 | 08 | 32 | 1 1/4" | HF | 890603 | BB320D01 | N | 0 | CPN-A609 | CPN-A609 | 330 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68H | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890604 | 08 | 32 | 1 1/4" | HF | 890604 | BB320D01 | N | 0 | CPN-A609 | CPN-A609 | 330 | 80 | 280 | 40 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68H | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-05 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890002 | 08 | 32 | 2" | PW | 890002 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890110 | 08 | 32 | 8" | PW | 890110 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 2.5 | 55 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890111 | 08 | 32 | 8" | PW | 890111 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 2.5 | 55 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890112 | 08 | 32 | 8" | PW | 890112 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 2.5 | 55 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890113 | 08 | 32 | 8" | PW | 890113 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 2.5 | 55 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890114 | 08 | 32 | 14" | PW | 890114 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 0,1 | 48.5 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890115 | 08 | 32 | 14" | PW | 890115 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 0,1 | 48.5 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890116 | 08 | 32 | 14" | PW | 890116 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 0,1 | 48.5 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890117 | 08 | 32 | 14" | PW | 890117 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 0,1 | 48.5 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890118 | 08 | 32 | 1" | PW | 890118 | HC150A01 | N | 0 | D-8909 | D-8909 | 10 | 120 | 0.1 | 60 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890012 | 08 | 32 | 14" | CWS | 890012 | HA150A01 | N | 0 | E-8900A/B | E-8900A/B | 7.5 | 120 | 5.5 | 26 | 997 | 0 | 14.3 | H | Cooling water supply | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-02 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890012 | 08 | 32 | 12" | PW | 890012 | HC150A01 | N | 0 | E-8900A/B | E-8900A/B | 10 | 120 | 4.1 | 61 | 997 | 0 | 14.3 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890013 | 08 | 32 | 14" | CWS | 890013 | HA150A01 | N | 0 | E-8900A/B | E-8900A/B | 7.5 | 120 | 5.5 | 26 | 997 | 0 | 14.3 | H | Cooling water supply | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-02 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890013 | 08 | 32 | 12" | PW | 890013 | HC150A01 | N | 0 | E-8900A/B | E-8900A/B | 10 | 120 | 4.1 | 61 | 997 | 0 | 14.3 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890014 | 08 | 32 | 14" | CWS | 890014 | HA150A01 | N | 0 | E-8900A/B | E-8900A/B | 7.5 | 120 | 5.5 | 26 | 997 | 0 | 14.3 | H | Cooling water supply | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-02 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890014 | 08 | 32 | 12" | PW | 890014 | HC150A01 | N | 0 | E-8900A/B | E-8900A/B | 10 | 120 | 4.3 | 60 | 997 | 0 | 14.3 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWR890015 | 08 | 32 | 14" | CWR | 890015 | HA150A01 | N | 0 | E-8900A/B | E-8900A/B | 7.5 | 120 | 3.5 | 37 | 997 | 0 | 14.3 | H | Cooling water return | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-03 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890015 | 08 | 32 | 12" | PW | 890015 | HC150A01 | N | 0 | E-8900A/B | E-8900A/B | 10 | 120 | 4.1 | 56 | 997 | 0 | 14.3 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWS890016 | 08 | 32 | 14" | CWS | 890016 | HA150A01 | N | 0 | E-8900A/B | E-8900A/B | 7.5 | 120 | 5.5 | 26 | 997 | 0 | 14.3 | H | Cooling water supply | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-03 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
CWR890017 | 08 | 32 | 14" | CWR | 890017 | HA150A01 | N | 0 | E-8900A/B | E-8900A/B | 7.5 | 120 | 3.5 | 37 | 997 | 0 | 14.3 | H | Cooling water return | L | N | - | >1.5 | 0 | sh.68O | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-U-021-03 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890607 | 08 | 32 | 1" | LO | 890607 | HB150A01 | N | 0 | ME-8900 | ME-8900 | 10 | 80 | 1 | 43 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 0 | sh.68C | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890609 | 08 | 32 | 1" | LO | 890609 | HB150A01 | N | 0 | ME-8900 | ME-8900 | 10 | 80 | 1 | 43 | 861 | 0 | 15 | H | Lube oil | L | N | - | <1.5 | 0 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890001 | 08 | 32 | 12" | PW | 890001 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890003 | 08 | 32 | 12" | PW | 890003 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890004 | 08 | 32 | 12" | PW | 890004 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890005 | 08 | 32 | 10" | PW | 890005 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890006 | 08 | 32 | 10" | PW | 890006 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890007 | 08 | 32 | 12" | PW | 890007 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 0.1 | 60 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890008 | 08 | 32 | 12" | PW | 890008 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 0.1 | 60 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890009 | 08 | 32 | 16" | PW | 890009 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 0.1 | 60 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890010 | 08 | 32 | 16" | PW | 890010 | HC150A01 | N | 0 | P-8900A/B | P-8900A/B | 10 | 120 | 0.1 | 60 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWS890605 | 08 | 32 | 1" | BCWS | 890605 | HB150A01 | N | 0 | S-8900A/B | S-8900A/B | 10 | 100 | 6.8 | 46 | 997 | 0 | 14.3 | H | Barrel cooling water supply | L | N | - | <1.5 | 0 | sh.68G | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
BCWR890606 | 08 | 32 | 1" | BCWR | 890606 | HB150A01 | N | 0 | S-8900A/B | S-8900A/B | 10 | 100 | 4.2 | 90 | 997 | 0 | 14.3 | H | Barrel cooling water return | L | N | - | <1.5 | 0 | sh.68I | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-04 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890119 | 08 | 32 | 10" | PW | 890119 | HC150A01 | N | 0 | S-8910A/B | S-8910A/B | 10 | 90 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
PW890120 | 08 | 32 | 10" | PW | 890120 | HC150A01 | N | 0 | S-8910A/B | S-8910A/B | 10 | 90 120 | 4.5 | 65 | 997 | 0 | 15 | H | Pellet water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890001 | 08 | 32 | 0.47" | HF | 890001 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 230 | 80 | 70 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890002 | 08 | 32 | 1.38" | HF | 890002 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890003 | 08 | 32 | 0.71" | HF | 890003 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890005 | 08 | 32 | 0.47" | HF | 890005 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890006 | 08 | 32 | 0.39" | HF | 890006 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 270 | 80 | 100 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890007 | 08 | 32 | 0.39" | HF | 890007 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 270 | 80 | 100 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890008 | 08 | 32 | 0.47" | HF | 890008 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 270 | 80 | 100 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68D | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890009 | 08 | 32 | 3/8" | HF | 890009 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 0.1 | 80 | 0 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890010 | 08 | 32 | 1,1" | HF | 890010 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 0.1 | 80 | 0 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890011 | 08 | 32 | 0.47 " | HF | 890011 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 0.1 | 80 | 0 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890012 | 08 | 32 | 0.39" | HF | 890012 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890013 | 08 | 32 | 0.39" | HF | 890013 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 230 | 80 | 70 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890014 | 08 | 32 | 0.39" | HF | 890014 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 230 | 80 | 70 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890015 | 08 | 32 | 0.59" | HF | 890015 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68S | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890016 | 08 | 32 | 0.59" | HF | 890016 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890017 | 08 | 32 | 0.71" | HF | 890017 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68L | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
HF890018 | 08 | 32 | 0,71" | HF | 890018 | BB350A01 | N | 0 | Z-8906 | Z-8906 | 250 | 80 | 180 | 29 | 920 | 0 | 330 | H | Hydraulic oil | L | N | - | <1.5 | 0 | sh.68K | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-06 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890620 | 08 | 32 | 2" | DW | 890620 | HB150A01 | N | 0 | D-8909 | D-8909 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | <1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LSS890001 | 08 | 32 | 3" | LSS | 890001 | CA150A01 | H | 100 | J-8909 | J-8909 | 6.5 | 250 | 4 | 200 | 997 | 0 | 10 | P | Low pressure steam | G | N | - | >1.5 | - | sh.68N |  | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-11 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890101 | 08 | 32 | 1/2" | LO | 890101 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 43 | 861 | 0 | 15 | H | Lube oil | L | N | - | >1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
LO890102 | 08 | 32 | 1/2" | LO | 890102 | BA010D01 | N | 0 | CPN-A211 | CPN-A211 | 10 | 80 | 1 | 43 | 861 | 0 | 15 | H | Lube oil | L | N | - | >1.5 | 10 | sh.68E | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-08 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890623 | 08 | 32 | 1" | DW | 890623 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890622 | 08 | 32 | 1" | DW | 890622 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890624 | 08 | 32 | 1" | DW | 890624 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890625 | 08 | 32 | 1" | DW | 890625 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890626 | 08 | 32 | 1" | DW | 890626 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890627 | 08 | 32 | 1" | DW | 890627 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
DW890621 | 08 | 32 | 1" | DW | 890621 | HB150A01 | N | 0 | CPN-A506 | CPN-A506 | 9 | 50 | 6.5 | 35 | 997 | 0 | 10 | H | Demineralized water | L | N | - | >1.5 | 0 | sh.68N | 2 | Art.4.3 | NA | N | as per 4274-GP-VD-FP10010032PK8900034 | N | 32-P-070-07 |  | NA | N | N/A | N | - | REV03_PKG 32-PK-8900
IG55695700 | 08 | 45 | 3/4" | IG55 | 695700 | CA2 | N | 0 | CYLINDER BATTERY - SYS. E.1 | CYLINDER RACK - BATTERY LIMIT | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.8 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55695701 | 08 | 45 | 1/2" | IG55 | 695701 | CA2 | N | 0 | CYLINDER RACK - BATTERY LIMIT | PROTECTED AREA | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.8 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55695900 | 08 | 45 | 3/4" | IG55 | 695900 | CA2 | N | 0 | CYLINDER BATTERY - SYS. E.2A | CYLINDER RACK - BATTERY LIMIT | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.8 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55695901 | 08 | 45 | 3/4" | IG55 | 695901 | CA2 | N | 0 | CYLINDER RACK - BATTERY LIMIT | PROTECTED AREA | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.8 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55695902 | 08 | 45 | 3/4" | IG55 | 695902 | CA2 | N | 0 | CYLINDER BATTERY - SYS. E.2B | CYLINDER RACK - BATTERY LIMIT | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.8 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55695903 | 08 | 45 | 1/2" | IG55 | 695903 | CA2 | N | 0 | CYLINDER RACK - BATTERY LIMIT | PROTECTED AREA | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.8 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696100 | 08 | 45 | 1-1/2" | IG55 | 696100 | CA1 | N | 0 | CYLINDERS BATTERY MANIFOLD SYS. E.3 | CYLINDERS BATTERY MANIFOLD SYS. E.3 BATTERY LIMIT | 140 | -18 / +50 | 60 | +20 / +50 | - | NA | 165 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | I | MOD.A | Y | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696101 | 08 | 45 | 1-1/2" | IG55 | 696101 | CA1 | N | 0 | CYLINDERS BATTERY MANIFOLD SYS. E.3 BATTERY LIMIT | SELECTOR VALVE MANIFOLD | 140 | -18 / +50 | 60 | +20 / +50 | - | NA | 165 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | I | MOD.A | Y | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696102 | 08 | 45 | 1-1/2" | IG55 | 696102 | CA1 | N | 0 | SELECTOR VALVE MANIFOLD | SELECTOR VALVE | 140 | -18 / +50 | 60 | +20 / +50 | - | NA | 165 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | I | MOD.A | Y | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696103 | 08 | 45 | 1" | IG55 | 696103 | CA2 | N | 0 | SELECTOR VALVE | RACK ROOM LINE BATTERY LIMIT (UNION) | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696104 | 08 | 45 | 1" | IG55 | 696104 | CA2 | N | 0 | RACK ROOM LINE BATTERY LIMIT (UNION) | DISCHARGE NOZZLES | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696105 | 08 | 45 | 1-1/2" | IG55 | 696105 | CA1 | N | 0 | SELECTOR VALVE MANIFOLD | SELECTOR VALVE | 140 | -18 / +50 | 60 | +20 / +50 | - | NA | 165 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | I | MOD.A | Y | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696106 | 08 | 45 | 1-1/2" | IG55 | 696106 | CA2 | N | 0 | SELECTOR VALVE | UPS ROOM LINE BATTERY LIMIT (UNION) | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | I | MOD.A | Y | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696107 | 08 | 45 | 1-1/2" | IG55 | 696107 | CA2 | N | 0 | UPS ROOM LINE BATTERY LIMIT (UNION) | DISCHARGE NOZZLES | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | I | MOD.A | Y | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696300 | 08 | 45 | 3/4" | IG55 | 696300 | CA2 | N | 0 | CYLINDER BATTERY - SYS. F.1A | CYLINDER RACK - BATTERY LIMIT | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696301 | 08 | 45 | 1/2" | IG55 | 696301 | CA2 | N | 0 | CYLINDER RACK - BATTERY LIMIT | PROTECTED AREA | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696302 | 08 | 45 | 3/4" | IG55 | 696302 | CA2 | N | 0 | CYLINDER BATTERY - SYS. F.1B | CYLINDER RACK - BATTERY LIMIT | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
IG55696303 | 08 | 45 | 1/2" | IG55 | 696303 | CA2 | N | 0 | CYLINDER RACK - BATTERY LIMIT | PROTECTED AREA | 60 | -18 / +50 | 60 | +20 / +50 | - | NA | 3 | H | 50% Ar + 50% N2 | G | N | NA | NA | - | sh.9 | 2 | Art.4.3 | NA | N | 4 | Y | 45-U-043-08 |  | NA | N | H280 | N | - | REV2_PKG CA-001-002-003
DEP690100 | 08 | 45 | 4" | DEP | 690100 | VB-13 | N | 0 | DCP-01 | DISCHARGE NOZZLE RISK 2 | 16 | -10 +60 | 8 | 20 | NA | 16 | 24 | H / V | DRY CHEMICAL POWDER (BC) | GS | N | NA | <1.5 | - | sh.10 | 2 | Art.4.3 | NA | N | HDG | N | 32-U-043-19 |  | NA | N | 0 0 0 | N | - | REV4_PKG DCP-01
DEP690101 | 08 | 45 | 3" | DEP | 690101 | VB-13 | N | 0 | DCP-01 | DISCHARGE NOZZLE RISK 1 | 16 | -10 +60 | 8 | 20 | NA | 16 | 24 | H / V | DRY CHEMICAL POWDER (BC) | GS | N | NA | <1.5 | - | sh.10 | 2 | Art.4.3 | NA | N | HDG | N | 32-U-043-19 |  | NA | N | 0 0 0 | N | - | REV4_PKG DCP-01
N690102 | 08 | 45 | 1" | N | 690102 | VB-13 | N | 0 | NITROGEN BOTTLE | 32-PCV-6886 | 200 | -10 +60 | 200 | 20 | NA | 16 | 205 | H / V | NITROGEN | G | N | NA | <1.5 | - | sh.10 | 2 | Art.4.3 | NA | N | HDG PAINTED | N | 32-U-043-19 |  | NA | N | 0 0 0 | N | - | REV4_PKG DCP-01
AI690103 | 08 | 45 | 1/2" | AI | 690103 | SS304 | N | 0 | AMD (AIR MAINTENANCE DEVICE) | AIR DETECTION LINE RISK 1 & 2 | 4 | -10 +60 | 4 | 20 | NA | 2.5 | 16 | H / V | AIR | G | N | NA | <1.5 | - | sh.10 | 2 | Art.4.3 | NA | N | NATURAL FINISH | N | 32-U-043-19 |  | NA | N | 0 0 0 | N | - | REV4_PKG DCP-01
O14013 | 08 | 32 | 1/2" | O | 14013 | 1CS2 | ET | 30 | O14011 | - | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.8 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-02 |  | M | N | 110 | N | 236 | 23,25
O14012 | 08 | 32 | 1/2" | O | 14012 | 1CS2 | ET | 30 | O14010 | - | 6.0/1.0 | 80.0/150.0 | 3.0/0.1 | 30.0/30.0 |  | 9 | 28.5 | IO | OIL | L | - | - | <1.5 | 30 | sh.7 | 2 | Art 4.3 | NA | N | NR | N | 32-P-026-01 |  | M | N | 110 | N | 236 | 23,25
O15026 | 08 | 32 | 3/4" | O | 15026 | B4S2 | ET | 30 | O14003 | - | 5.0 | 150.0 | 2.0 | 30.0 |  | 7.5 | 29.4 | IO | OIL | L | - | - | <1.5 | 30 | sh.9 | 2 | Art 4.3 | NA | N | 20 | N | 32-P-026-05 |  | E | N | 110 | N | 226 | 23,25
JWS64085 | 08 | 32 | 4" | JWS | 64085 | B-1 | N | 0 | JWS64047 | JWS80B04 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS80B04 | 08 | 32 | 4" | JWS | 80B04 | B-1 | N | 0 | JWS80B04 | 32-PK-2500 | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS80B04 | 08 | 32 | 3/4" | JWS | 80B04 | B-1 | N | 0 | JWS80B04 | - | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWS80B04 | 08 | 32 | 1-1/2" | JWS | 80B04 | B-1 | N | 0 | JWS80B04 | - | 9.0 | 100.0 | 5.0 | 30.0 |  | 13.5 | 29.4 | H | JACKET WATER SUPPLY | L | - | - | <1.5 | 30 | sh.82 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-01 |  | E | N | 000 | N | 10
JWR80B13 | 08 | 32 | 4" | JWR | 80B13 | B-1 | N | 0 | JWR23002 | JWR80B12 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR80B12 | 08 | 32 | 4" | JWR | 80B12 | B-1 | N | 0 | JWR80B13 | 32-PK-2500 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR80B12 | 08 | 32 | 3/4" | JWR | 80B12 | B-1 | N | 0 | JWR80B12 | - | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR80B12 | 08 | 32 | 1-1/2" | JWR | 80B12 | B-1 | N | 0 | JWR80B12 | - | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR80B12 | 08 | 32 | 3/4" | JWR | 80B12 | B-1 | N | 0 | JWR80B12 | JWR80B14 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
JWR80B14 | 08 | 32 | 3/4" | JWR | 80B14 | B-1 | N | 0 | JWR80B12 | VA80B05 | 9.0 | 100.0 | 3.5 | 42.0 |  | 13.5 | 29.4 | H | JACKET WATER RETURN | L | - | - | <1.5 | 42 | sh.16 | 2 | Art 4.3 | NA | N | 1 | N | 32-U-022-02 |  | E | N | 000 | N | 11
VA80B05 | 08 | 32 | 1" | VA | 80B05 | 1C2 | N | 0 | JWR80B14 | TO ATM | 3.5 | 82.0 | 0.0 | 30.0 |  | 0 | 26.46 | V | VENT TO ATMOSPHERE | V | - | - | >1.5 | 30 | sh.10 | 2 | Art 4.3 | NA | N | 1 | N | 19-U-010-02 |  | E | N | 000 | N | 3400
Note on H7879: [Commento in thread] La versione di Excel in uso consente di leggere questo commento in thread, ma tutte le modifiche a esso apportate verranno rimosse se il file viene aperto in una versione più recente di Excel. Ulteriori informazioni: https://go.microsoft.com/fwlink/?linkid=870924 Commento: Please check insulation code. In P&ID it is indicated as "C". Comment applicable for all hot oil lines. Rispondi: "C" (contact protection) confirmed